## Sheet1
AHU # | 90.1 EER | Tons | BTU/hr | Fan cfm | Pressure drop credit | A | Fan bhp | # of Poles | Fan Motor Efficiency | Fan W | Fan kW/cfm | Cooling W (compressor + condenser) | Cooling EER (compressor + condenser) | Cooling EIR (compressor + condenser)
1 | 9.5 | 128 | 1536000 | 21017 | 3 | 15.2629 | 42.585 | 2 | 91.7% | 34643.8417 | 0.0016484 | 127040.3689 | 12.0906 | 0.2822
2 | 9.5 | 81 | 972000 | 13403 | 3 | 9.7335 | 20.4239 | 2 | 90.2% | 16891.6069 | 0.0012603 | 85424.1826 | 11.3785 | 0.29986
3 | 9.5 | 117 | 1404000 | 19327 | 3 | 14.0356 | 28.1251 | 2 | 91% | 23056.4007 | 0.001193 | 124733.073 | 11.256 | 0.30313
4 | 9.5 | 176 | 2112000 | 29018 | 3 | 21.0733 | 40.7234 | 2 | 91.7% | 33129.3963 | 0.0011417 | 189186.3932 | 11.1636 | 0.30564
5 | 9.5 | 79 | 948000 | 31826 | 3 | 23.1126 | 44.3738 | 2 | 91.7% | 36099.0783 | 0.0011343 | 63690.3954 | 14.8845 | 0.22923
[15 empty] | Return and/or exhaust airflow control devices | 0.5
|  |  | Enclosed Motors | [11 empty] | Exhaust filters, scrubbers, or other exhaust treatment | The pressure drop of device calculated at fan system design condition
| 2 | Number of Poles ⇒ | 2 | 4 | 6 | [9 empty] | Particulate Filtration Credit: MERV 9 through 12 | 0.5
|  | Synchronous Speed (RPM)⇒ | 3600 | 1800 | 1200 | [9 empty] | Particulate Filtration Credit: MERV 13 through 15 | 0.9
|  | Motor Horsepower | [12 empty] | Particulate Filtration Credit: MERV 16 and greater and electronically enhanced filters | Pressure drop calculated at 2× clean filter pressure drop at fan system design condition
|  | 1 | 75.5 | 82.5 | 80 | [9 empty] | Carbon and other gas-phase air cleaners | Clean filter pressure drop at fan system design condition
|  | 1.5 | 82.5 | 84 | 85.5 | [9 empty] | Heat recovery device | Pressure drop of device at fan system design condition
|  | 2 | 84 | 84 | 86.5 | [9 empty] | Evaporative humidifier/cooler in series with another cooling coil | Pressure drop of device at fan system design condition
|  | 3 | 85.5 | 87.5 | 87.5 | [9 empty] | Sound Attenuation Section | 0.15 in. w.c.
|  | 5 | 87.5 | 87.5 | 87.5
|  | 7.5 | 88.5 | 89.5 | 89.5
|  | 10 | 89.5 | 89.5 | 89.5
|  | 15 | 90.2 | 91 | 90.2
|  | 20 | 90.2 | 91 | 90.2
|  | 25 | 91 | 92.4 | 91.7
|  | 30 | 91 | 92.4 | 91.7
|  | 40 | 91.7 | 93 | 93
|  | 50 | 92.4 | 93 | 93
|  | 60 | 93 | 93.6 | 93.6
|  | 75 | 93 | 94.1 | 93.6
|  | 100 | 93.6 | 94.5 | 94.1
|  | 125 | 94.5 | 94.5 | 94.1
|  | 150 | 94.5 | 95 | 95
|  | 200 | 95 | 95 | 95