## Hi-Rise-Multiuse
[7 empty] | 600 |  |  | Top of Cooling Towers = 600 feet | [31 empty] | 600
[5 empty] | RF | 30 | 570 | [9 empty] | RF-L52 | [7 empty] | Cooling Towers | [5 empty] | Roof : 160 x 120 : (80,50,570) | [10 empty] | 570 | RF | RF
[5 empty] | 45 | 20 | 550 | [9 empty] | MER-L45 |  |  |  | H&V |  |  | Mechanical Equipment Room : 160 x 120 x 20 : (80,50,550) | [17 empty] | 550 | 20 | 45
[5 empty] | 44 | 15 | 535 | [9 empty] | RST-L44 |  |  |  | VAVS |  |  | Restaurant : 160 x 100 x 15 : (80,50,535) | [17 empty] | 535 | 15 | 44
[5 empty] | 43 | 10 | 525 |  | Pressure | [32 empty] | 525 | 10 | 43
[5 empty] | 42 | 10 | 515 |  | Feet x 0.433 = psi | [16 empty] | with partially inset balconies | [15 empty] | 515 | 10 | 42
[5 empty] | 41 | 10 | 505 | [10 empty] | 5 floors | [23 empty] | 505 | 10 | 41
[5 empty] | 40 | 10 | 495 |  | Pipe Height from | [8 empty] | PTAC | [18 empty] | Balcony |  |  |  |  | 495 | 10 | 40
[5 empty] | 39 | 10 | 485 |  | B3 (-40') to the Top | [7 empty] | Apartments-L34-L48 | [9 empty] | 160 x 120 x 10 : (80,50,485) | [14 empty] | 485 | 10 | 39
[5 empty] | 38 | 10 | 475 |  | of Cooling Towers = | [32 empty] | 475 | 10 | 38
[5 empty] | 37 | 10 | 465 |  | 640 feet (277 psi) | [25 empty] | OPERABLE | [6 empty] | 465 | 10 | 37
[5 empty] | 36 | 10 | 455 | [27 empty] | WINDOWS | [6 empty] | 455 | 10 | 36
[5 empty] | 35 | 10 | 445 | [34 empty] | 445 | 10 | 35
[5 empty] | 34 | 10 | 435 | [34 empty] | 435 | 10 | 34
[5 empty] | 33 | 10 | 425 | [34 empty] | 425 | 10 | 33
[5 empty] | 32 | 10 | 415 | [34 empty] | 415 | 10 | 32
[5 empty] | 31 | 10 | 405 | [34 empty] | 405 | 10 | 31
[5 empty] | 30 | 10 | 395 | [10 empty] | 4-Pipe FCU | [23 empty] | 395 | 10 | 30
[5 empty] | 29 | 10 | 385 | [9 empty] | HTL-Rms-L29-L38 | [7 empty] | 10 floors |  |  |  | 160 x 120 x 10 : (80,50,385) | [12 empty] | 385 | 10 | 29
[5 empty] | 28 | 15 | 370 | [7 empty] | Reception - Lobby | [6 empty] | Gymnasium |  |  |  |  | Health Spa |  |  |  | Swimming Pool | [10 empty] | 370 | 15 | 28
[5 empty] | 27 | 15 | 355 | [7 empty] | Laundry Dry Cleaners | [6 empty] | Dance Club / Disc |  |  |  |  | Coctail Bar |  |  |  | Wedding Hall | [10 empty] | 355 | 15 | 27
[5 empty] | 26 | 15 | 340 | [7 empty] | Housekeeping - Storage | [6 empty] | Meeting Rooms |  |  |  |  | Conference Centers | [14 empty] | 340 | 15 | 26
[5 empty] | 25 | 15 | 325 | [6 empty] | HTL-Fns-L25-L28 | [6 empty] | 4 floors |  |  |  | 220 x 120 x 15 : (50,40,325) | [16 empty] | 325 | 15 | 25
[5 empty] | 24 | 20 | 305 | [6 empty] | MER-L24 |  |  |  | H&V |  |  | Mechanical Equipment Room : 220 x 120 x 20 : (50,40,305) | [20 empty] | 305 | 20 | 24
|  | ADJACENT BUILDING |  |  | 23 | 13 | 292 | [13 empty] | Toilets, M-E Closets, Shafts | [20 empty] | 292 | 13 | 23 |  | ADJACENT BUILDING
[5 empty] | 22 | 13 | 279 | [13 empty] | Elevators, Stairs, Lobby, Storage | [11 empty] | ATR-SE | [8 empty] | 279 | 13 | 22
[5 empty] | 21 | 13 | 266 |  | ATRIUMS | [11 empty] | CORE B3-L52 | [11 empty] | Level 19 |  |  |  | SOUTH |  |  |  |  | 266 | 13 | 21
[5 empty] | 20 | 13 | 253 |  | 30' x 30' x | [11 empty] | 80 x 60 (120,70,Z) | [15 empty] | ELEVATION |  |  |  |  | 253 | 13 | 20
[5 empty] | 19 | 13 | 240 |  | 5 levels high | [32 empty] | 240 | 13 | 19
[5 empty] | 18 | 13 | 227 |  | located on the | [28 empty] | OFFICE |  |  |  | 227 | 13 | 18
[5 empty] | 17 | 13 | 214 |  | SE and NW | [23 empty] | ATR-SE |  |  |  |  | ATRIUMS |  |  |  | 214 | 13 | 17
[5 empty] | 16 | 13 | 201 |  | corners of | [23 empty] | Level 14 |  |  |  |  | 5 Flrs High |  |  |  | 201 | 13 | 16
[5 empty] | 15 | 13 | 188 |  | Office Floors | [28 empty] | FIXED |  |  |  | 188 | 13 | 15
[5 empty] | 14 | 13 | 175 |  | (See Plan View) | [28 empty] | WINDOWS |  |  |  | 175 | 13 | 14
[5 empty] | 13 | 13 | 162 | [34 empty] | 162 | 13 | 13
[5 empty] | 12 | 13 | 149 | [25 empty] | ATR-SE | [8 empty] | 149 | 13 | 12
[5 empty] | 11 | 13 | 136 | [25 empty] | Level 9 | [8 empty] | 136 | 13 | 11
[5 empty] | 10 | 13 | 123 | [7 empty] | VAVS-PIU | [26 empty] | 123 | 13 | 10
[5 empty] | 9 | 13 | 110 | [6 empty] | OFC-L9-L23 | [5 empty] | 20 floors |  |  |  | Office : 220 x 120 x 13 : (50,40,110) | [17 empty] | 110 | 13 | 9
[5 empty] | 8 | 20 | 90 |  |  |  | MER-L8 |  |  |  |  | Mechanical Equipment Room : 280 x 160 x 20 : (20,20,90) | [25 empty] | 90 | 20 | 8
[5 empty] | 7 | 10 | 80 | [30 empty] | SHAFTS |  |  |  | 80 | 10 | 7
[5 empty] | 6 | 10 | 70 |  | OPEN | [32 empty] | 70 | 10 | 6
[5 empty] | 5 | 10 | 60 |  | NO WALLS | [32 empty] | 60 | 10 | 5
[5 empty] | 4 | 10 | 50 |  |  |  | PKG-L4-L7 | [5 empty] | Parking : 280 x 160 x 10 : (20,20,50) | [20 empty] | SHAFTS |  |  |  | 50 | 10 | 4
[5 empty] | 3 | 15 | 35 | [26 empty] | Auditorium | [7 empty] | 35 | 15 | 3
[5 empty] | 2 | 15 | 20 |  |  |  | RTL: L2-L3 | [5 empty] | Retail : 280 x 160 x 20 : (20,20,20) | [16 empty] | Theatre |  |  |  |  | Service |  |  | 20 | 15 | 2
[5 empty] | 1 | 20 | 0 |  |  |  | LBY: L1 | [5 empty] | Lobby : 280 x 160 x 20 : (20,20,0) | [21 empty] | Alley |  |  | 0 | 20 | 1
[5 empty] | B1 | 10 | -10 | [30 empty] | Emergency |  |  |  | -10 | 10 | B1
| Z |  |  |  | B2 | 10 | -20 |  | PKG-B1-B2 | [5 empty] | Underground Parking : 320 x 200 x 10 : (0,0,-20) | [15 empty] | Ventil only | [6 empty] | Generators |  |  |  | -20 | 10 | B2
[5 empty] | B3 | 20 | -40 |  | MER-B3 |  |  |  | Mechanical Equipment Room : 320 x 200 x 20 : (0,0,-40) | [17 empty] | H&V | [10 empty] | -40 | 20 | B3
| X | [6 empty] | 0 | 10 | 20 | 30 | 40 | 50 | 60 | 70 | 80 | 90 | 100 | 110 | 120 | 130 | 140 | 150 | 160 | 170 | 180 | 190 | 200 | 210 | 220 | 230 | 240 | 250 | 260 | 270 | 280 | 290 | 300 | 310 | 320
0 | 10 | 20 | 30 | 40 | 50 | 60 | 70 | 80 | 90 | 100 | 110 | 120 | 130 | 140 | 150 | 160 | 170 | 180 | 190 | 200 | 210 | 220 | 230 | 240 | 250 | 260 | 270 | 280 | 290 | 300 | 310 | 320 | 330 | 340 | 350 | 360 | 370 | 380 | 390 | 400 | 410 | 420 | 430 | 440 | 450 | 460 | 470 | 480

## Input-Output
2 | 6 | 6 | 2 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 2 | 5.5 | 5.5 | 5.5 | 5.5 | 2 | 2 | 8 | 8 | 8 | 8.6 | 8.6 | 8.6 | 8.6 | 8.6 | 8.6 | 8.6 | 8.6 | 2 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 2 | 2 | 5 | 5 | 5 | 5 | 2 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 2 | 2 | 5 | 5 | 5 | 5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 2 | 2 | 5 | 5 | 5 | 5 | 2 | 6 | 6 | 6 | 6 | 6 | 7.5 | 7.5 | 2 | 6 | 6 | 6 | 6 | 6 | 7.5 | 7.5 | 7.5
| Infltr | Pi-Po= |  |  | Pi-Po | Inside to Outside Pressure Difference for Building Pressurization = | [6 empty] | 0.02 |  |  | Calc | EX-1 | EX-2 | EX-3 |  |  | Bldg Pressurization - Stack Effect & Wind Press Infltr | [6 empty] | USER INPUT |  | descriptions |  |  | Calc | Sctn | Bldg | Flr-H + Sea-Lvl |  |  |  | Calc | Floor | Floor | Flr |  | From Sheet 'SMMR-Calcs' |  |  |  | SUMMER |  | Annual | [8 empty] | Calc | Floor | Floor | Flr | From Sheet 'WNTR-Calcs' |  |  |  | WINTER |  | Annual | [8 empty] | Calc | Floor | Floor | Flr |  | From Sheet 'SMMR-Calcs' |  |  |  |  | Infltr | Cooling |  | From Sheet 'WNTR-Calcs' |  |  |  |  | Infltr | Heating
| cfm/ft2 | 0.02 |  | Q = Cd * A * ( 2 * ∆P/d )0.5 |  |  | A = Q / ( Cd * ( 2 * ∆P/d )0.5 ) |  |  | Cd = | 0.65 | dens = | 0.071 |  |  | ID # | S-Flr | S-Flr | S-Flr | [11 empty] | CALCULATED |  |  | ID # | Flr # | Flr-# | feet | meters |  |  | ID # | Lvl # | Hgt | Lk-A | [7 empty] | Tons | [8 empty] | ID # | Lvl # | Hgt | Lk-A | [6 empty] | KWH | [8 empty] | ID # | Lvl # | Hgt | Lk-A | [6 empty] | SHG | Energy/Yr | [6 empty] | SHL | Energy/Yr
| Envlp | Infl-A |  | INPUT DATA Preparation Sheet |  |  |  | Prepare your Input Data offline here (up to 3 examples) | [43 empty] | Cooling | [18 empty] | Heating
| Area | ft2 | [7 empty] | and Copy and Paste into next sheet >> | [13 empty] | P R O J E C T D A T A | Description |  |  |  |  | DESIGN (INPUT) | SMMR | WNTR |  | Section >> |  | 8 | # flrs >> | 3 |  |  | Section >> |  | 8 | 25.2 |  | Alt psi | Wnd-V | OA-DB | OA-d | Q cfm | Q/Env-A | Tons | [8 empty] | Section >> |  | 8 | 25.2 | Alt psi | Wnd-V | OA-DB | OA-d | Q cfm | Q/Env-A | KWH | [10 empty] | 8 | 25.2 |  | OA-DB | Vo ft3/lb | Ho bu/lb | Q ft3/min | Q lbs/hr | btuh | K-btu/yr |  | OA-DB | Vo ft3/lb | Ho bu/lb | Q ft3/min | Q lbs/hr | btuh | K-btuh/yr
|  |  |  | EX-1 |  | SECTION No. | 1 | 2-A | 3 | 4-k | 5 | 6 (x) | 7 | 8 |  | 24 | 2 | 2 | 2 |  |  |  |  | Project Name | Very Tall Mixed-Use Building (Description) |  |  |  |  | Wnd (mph) Grnd | 5 | 15 |  | 24 | 2 | 101 | 1789 | 545.2872 |  |  | 24 | 101 | 1289 |  |  | 13.7705 | 9.9236 | 90.4112 | 0.066421 | 722.0424 | 0.085957 | 174.1566 | [8 empty] | 24 | 101 | 1289 |  | 13.7705 | 19.9236 | -20.5888 | 0.084829 | -2093.1136 | -0.24918 | -18041.5511 | [8 empty] | 24 | 101 | 1289 |  |  | 90.4112 | 15.0554 | 35.4142 | 722.0424 | 2877.5404 | 12017.7119 | 2089.8795 |  | -20.5888 | 11.7885 | -4.5618 | -2093.1136 | -10653.3699 | 209302.8804 | -18041.5511
| 0 | 0 |  |  |  | Flr Type (Retl, Offc, ) | Lobby | Retail | Tradg | Office | Htl-Srvc | Hotel | Condos | Dining |  | 23 | 1 | 1 | 1 |  |  |  |  | Project Analyst | VCT (Description) |  |  |  |  | Wnd (mph) Roof | 10 | 20 |  | 23 | 1 | 100 | 1774 | 540.7152 |  |  | 23 | 100 | 1274 |  |  | 13.778 | 9.8663 | 90.4646 | 0.066449 | 712.5913 | 0.084832 | 171.877 | [8 empty] | 23 | 100 | 1274 |  | 13.778 | 19.8663 | -20.5354 | 0.084865 | -2068.5318 | -0.24625 | -17829.6686 | [8 empty] | 23 | 100 | 1274 |  |  | 90.4646 | 15.0491 | 35.4515 | 712.5913 | 2841.0595 | 11901.5041 | 2308.7959 |  | -20.5354 | 11.7834 | -4.5481 | -2068.5318 | -10532.7396 | 206725.5015 | -6702.0431
| 0.02 | 0.040994 |  |  |  | Typical Floor Length (ft) | 320 | 280 | 240 | 220 | 200 | 180 | 180 | 180 | [9 empty] | Bldg Type (Office, Hotel) | Mixed Use High Rise (Description) |  |  |  |  | Outdoor DB (F) | 95 | -16 |  | Section >> |  | 7 | # flrs >> | 16 |  |  | Section >> |  | 7 | 22.4 |  | Alt psi | Wnd-V | OA-DB | OA-d | Q cfm | Q/Env-A | Tons | [8 empty] | Section >> |  | 7 | 22.4 | Alt psi | Wnd-V | OA-DB | OA-d | Q cfm | Q/Env-A | KWH | [10 empty] | 7 | 22.4 |  | OA-DB | Vo ft3/lb | Ho bu/lb | Q ft3/min | Q lbs/hr | btuh | K-btu/yr |  | OA-DB | Vo ft3/lb | Ho bu/lb | Q ft3/min | Q lbs/hr | btuh | K-btu/yr
| 0.04 | 0.081987 |  |  |  | Typical Floor Width (ft) | 240 | 200 | 160 | 140 | 120 | 100 | 100 | 100 |  | 22 | 0 | 3 | 15 |  |  |  |  | Location (City, State) | Minneapolis, MN, USA (Description) |  |  |  |  | Outdoor WB (F) | 75 | -16 |  | 22 | 0 | XX | XX | XX |  |  | 22 | XX | XX |  |  | XX | XX | XX | XX | XX | XX | XX | [8 empty] | 22 | XX | XX |  | XX | XX | F | XX | XX | XX | XX | [8 empty] | 22 | XX | XX |  |  | XX | XX | XX | XX | XX | XX | XX |  | XX | XX | XX | XX | XX | XX | XX
| 0.06 | 0.12298 |  |  |  | Floor-Floor Height (ft) | 20 | 18 | 15 | 13.5 | 15 | 10 | 10 | 15 |  | 21 | 10 | 2 | 10 | [10 empty] | Degree-Days | 2680 | 7981 |  | 21 | 10 | 93 | 1689 | 514.8072 |  |  | 21 | 93 | 1189 |  |  | 13.8209 | 9.5416 | 90.7672 | 0.066606 | 582.0918 | 0.069297 | 140.4006 | [8 empty] | 21 | 93 | 1189 |  | XX | XX | -20.5888 | XX | -1710.0982 | -0.20358 | -14740.157 | [8 empty] | 21 | 93 | 1189 |  |  | 90.7672 | 15.0136 | 35.6638 | 582.0918 | 2326.252 | 9912.1699 | 1885.9775 |  | -20.2328 | 15.0136 | -4.4706 | -1710.0982 | -6834.1782 | 170345.3876 | -5540.7181
| 0.08 | 0.16397 |  |  |  | Number of Typical Floors | 2 | 3 | 6 | 40 | 5 | 25 | 15 | 2 |  | 20 | 5 | 1 | 5 |  |  |  |  | Site Altit. (ft) ref Sea Level | 500 |  | Mech/Grd Flr-Flr-H | 20 |  | Indoor DB (F) | 75 | 72 |  | 20 | 5 | 88 | 1639 | 499.5672 |  |  | 20 | 88 | 1139 |  |  | 13.8462 | 9.3506 | 90.9452 | 0.066699 | 548.4567 | 0.065292 | 132.2878 | [8 empty] | 20 | 88 | 1139 |  | 13.8209 | 19.5416 | -20.5354 | 0.08507 | -1630.1279 | -0.19406 | -14050.8544 | [8 empty] | 20 | 88 | 1139 |  |  | 90.9452 | 14.9928 | 35.789 | 548.4567 | 2194.8774 | 9444.8485 | 1776.9998 |  | -20.0548 | 14.9928 | -4.425 | -1630.1279 | -6523.6339 | 162066.0511 | -5281.6142
| 0.1 | 0.20497 |  |  |  | Mech Flr above Sctn (Y/N) | N | Y | N | Y | N | N | Y | Y | [9 empty] | Mech/Grd % Envel Leakg | 0.6 |  | Mech/Grd Flow C | 0.6 |  | Indoor WB (F) | 62 | 55 |  | Section >> |  | 6 (x) | # flrs >> | 25 |  |  | Section >> |  | 6 (x) | 19.6 |  | Alt psi | Wnd-V | OA-DB | OA-d | Q cfm | Q/Env-A | Tons | [8 empty] | Section >> |  | 6 (x) | 19.6 | Alt psi | Wnd-V | OA-DB | OA-d | Q cfm | Q/Env-A | KWH | [10 empty] | 6 (x) | 19.6 |  | OA-DB | Vo ft3/lb | Ho bu/lb | Q ft3/min | Q lbs/hr | btuh | K-btu/yr |  | OA-DB | Vo ft3/lb | Ho bu/lb | Q ft3/min | Q lbs/hr | btuh | K-btu/yr
| 0.12 | 0.24596 |  |  |  | Leakage Area as % of Envel | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 |  | 19 | 0 | 4 | 20 | [14 empty] | 19 | 0 | XX | XX | XX |  |  | 19 | XX | XX |  |  | XX | XX | XX | XX | XX | XX | XX | [8 empty] | 19 | XX | XX |  | XX | XX | XX | XX | XX | XX | XX | [8 empty] | 19 | XX | XX |  |  | XX | XX | XX | XX | XX | XX | XX |  | XX | XX | XX | XX | XX | XX | XX
| 0.14 | 0.28696 |  |  |  | Envel Leakage Flow Coeff | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 |  | 18 | 25 | 3 | 15 |  |  | # Flrs | Bldg-H | Ntrl-H | Site-Alt |  | Total Bldg-Area |  | Total Envel-Area |  | Total Leakg-Area | % Avg Lkg |  | 18 | 25 | 83 | 1589 | 484.3272 |  |  | 18 | 83 | 1089 |  |  | 13.8715 | 9.1597 | 91.1232 | 0.066791 | 447.7002 | 0.053298 | 107.9853 | [8 empty] | 18 | 83 | 1089 |  | XX | XX | XX | XX | -1353.052 | -0.16108 | -11662.6042 | [8 empty] | 18 | 83 | 1089 |  |  | 91.1232 | 14.972 | 35.9146 | 447.7002 | 1794.1447 | 7795.8096 | 1450.5487 |  | -19.8768 | 11.7218 | -4.3794 | -1353.052 | -6925.8484 | 134259.2686 | -4383.8883
| 0.16 | 0.32795 |  |  |  | In-Out PD (in.wg) PI - PO | 0 | 0.005 | 0.005 | 0.005 | 0.005 | 0.005 | 0.005 | 0.005 |  | 17 | 15 | 2 | 10 |  |  | 102 | 1309 | 654.5 | 500 | 2782800 |  | 584440 |  | 1633.42 |  | 0.27948 |  | 17 | 15 | 73 | 1489 | 453.8472 |  |  | 17 | 73 | 989 |  |  | 13.9223 | 8.7777 | 91.4792 | 0.066976 | 372.0698 | 0.044294 | 89.7432 | [8 empty] | 17 | 73 | 989 |  | 13.8715 | 19.1597 | -19.8768 | 0.085311 | -1193.9411 | -0.14214 | -10291.1515 | [8 empty] | 17 | 73 | 989 |  |  | 91.4792 | 14.9306 | 36.1666 | 372.0698 | 1495.195 | 6621.909 | 1205.506 |  | -19.5208 | 11.6886 | -4.2881 | -1193.9411 | -6128.7551 | 118012.133 | -3868.3692
| 0.18 | 0.36894 | [13 empty] | 16 | 5 | 1 | 5 | [14 empty] | 16 | 5 | 63 | 1389 | 423.3672 |  |  | 16 | 63 | 889 |  |  | 13.9732 | 8.3957 | 91.8352 | 0.067162 | 270.9588 | 0.032257 | 65.3553 | [8 empty] | 16 | 63 | 889 |  | 13.9223 | 18.7777 | -19.5208 | 0.085554 | -1011.5624 | -0.12042 | -8719.142 | [8 empty] | 16 | 63 | 889 |  |  | 91.8352 | 14.8894 | 36.4198 | 270.9588 | 1091.8889 | 4926.5663 | 877.9066 |  | -19.1648 | 11.6555 | -4.1967 | -1011.5624 | -5207.2932 | 99596.4395 | -3277.4622
| 0.2 | 0.40994 |  | EX-2 |  | SECTION No. | A | B | C | D | E | F | G | H | [9 empty] | SECTION (max = 5 chars) >> | 1 | 2-A | 3 | 4-k | 5 | 6 (x) | 7 | 8 |  | Section >> |  | 5 | # flrs >> | 5 |  |  | Section >> |  | 5 | 28.8 |  | Alt psi | Wnd-V | OA-DB | OA-d | Q cfm | Q/Env-A | Tons | [8 empty] | Section >> |  | 5 | 28.8 | Alt psi | Wnd-V | OA-DB | OA-d | Q cfm | Q/Env-A | KWH | [10 empty] | 5 | 28.8 |  | OA-DB | Vo ft3/lb | Ho bu/lb | Q ft3/min | Q lbs/hr | btuh | K-btu/yr |  | OA-DB | Vo ft3/lb | Ho bu/lb | Q ft3/min | Q lbs/hr | btuh | K-btu/yr
| 0.22 | 0.45093 |  |  |  | Flr Type (Retl, Offc, ) | Office | Office | Office | Office | Office | Office | Office | Office |  | 15 | 5 | 3 | 5 |  |  |  |  | Flr Type (Retl, Offc, ) | Lobby | Retail | Tradg | Office | Htl-Srvc | Hotel | Condos | Dining |  | 15 | 5 | 58 | 1339 | 408.1272 |  |  | 15 | 58 | 839 |  |  | 13.9987 | 8.2047 | 92.0132 | 0.067255 | 293.0626 | 0.034888 | 70.6867 | [8 empty] | 15 | 58 | 839 |  | 13.9987 | 18.2047 | -18.9868 | 0.085918 | -1333.2389 | -0.15872 | -11491.8261 | [8 empty] | 15 | 58 | 839 |  |  | 92.0132 | 14.8688 | 36.5469 | 293.0626 | 1182.5944 | 5384.7953 | 949.5229 |  | -18.9868 | 11.639 | -4.151 | -1333.2389 | -6872.9312 | 131011.7705 | -4319.6941
| 0.24 | 0.49192 |  |  |  | Typical Floor Length (ft) | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 |  | 14 | 3 | 2 | 3 |  |  |  |  | Typical Floor Length (ft) | 320 | 280 | 240 | 220 | 200 | 180 | 180 | 180 |  | 14 | 3 | 56 | 1309 | 398.9832 |  |  | 14 | 56 | 809 |  |  | 14.014 | 8.0901 | 92.12 | 0.067311 | 203.7751 | 0.024259 | 49.1506 | [8 empty] | 14 | 56 | 809 |  | 13.9987 | 18.2047 | -18.9868 | 0.085918 | -1232.5716 | -0.14673 | -10624.1258 | [8 empty] | 14 | 56 | 809 |  |  | 92.12 | 14.8565 | 36.6233 | 203.7751 | 822.9746 | 3767.7113 | 660.2313 |  | -18.88 | 11.6292 | -4.1235 | -1232.5716 | -6359.3811 | 120977.4439 | -3993.5318
| 0.26 | 0.53292 |  |  |  | Typical Floor Width (ft) | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 |  | 13 | 1 | 1 | 1 |  |  |  |  | Typical Floor Width (ft) | 240 | 200 | 160 | 140 | 120 | 100 | 100 | 100 |  | 13 | 1 | 54 | 1279 | 389.8392 |  |  | 13 | 54 | 779 |  |  | 14.0293 | 7.9756 | 92.2268 | 0.067366 | -58.5108 | -0.0069656 | -14.1128 | [8 empty] | 13 | 54 | 779 |  | 14.014 | 18.0901 | -18.88 | 0.085991 | -1123.1766 | -0.13371 | -9681.1979 | [8 empty] | 13 | 54 | 779 |  |  | 92.2268 | 14.8442 | 36.6998 | -58.5108 | -236.4999 | -1088.587 | -189.5749 |  | -18.7732 | 11.6193 | -4.0961 | -1123.1766 | -5799.8848 | 110110.7261 | -3639.0921
| 0.28 | 0.57391 |  |  |  | Floor-Floor Height (ft) | 13.5 | 13.5 | 13.5 | 13.5 | 13.5 | 13.5 | 13.5 | 13.5 | [9 empty] | Floor-Floor Height (ft) | 20 | 18 | 15 | 13.5 | 15 | 10 | 10 | 15 |  | Section >> |  | 4-k | # flrs >> | 41 |  |  | Section >> |  | 4-k | 24.3 |  | Alt psi | Wnd-V | OA-DB | OA-d | Q cfm | Q/Env-A | Tons | [8 empty] | Section >> |  | 4-k | 24.3 | Alt psi | Wnd-V | OA-DB | OA-d | Q cfm | Q/Env-A | KWH | [10 empty] | 4-k | 24.3 |  | OA-DB | Vo ft3/lb | Ho bu/lb | Q ft3/min | Q lbs/hr | btuh | K-btu/yr |  | OA-DB | Vo ft3/lb | Ho bu/lb | Q ft3/min | Q lbs/hr | btuh | K-btu/yr
| 0.3 | 0.6149 |  |  |  | Number of Typical Floors | 2 | 3 | 3 | 5 | 3 | 4 | 3 | 2 |  | 12 | 30 | 5 | 30 |  |  |  |  | Number of Typical Floors | 2 | 3 | 6 | 40 | 5 | 25 | 15 | 2 |  | 12 | 30 | 36 | 1109 | 338.0232 |  |  | 12 | 36 | 609 |  |  | 14.1165 | 7.3262 | 92.832 | 0.067683 | -437.7785 | -0.052116 | -105.5922 | [8 empty] | 12 | 36 | 609 |  | 14.1165 | 17.3262 | -18.168 | 0.086478 | -437.7785 | -0.052116 | -3773.423 | [8 empty] | 12 | 36 | 609 |  |  | 92.832 | 14.7747 | 37.1354 | -437.7785 | -1777.8112 | -8430.9645 | -1418.4023 |  | -18.168 | 11.5636 | -3.9404 | -437.7785 | -2271.502 | -35601.4486 | 1184.5034
| 0.32 | 0.6559 |  |  |  | Mech Flr above Sctn (Y/N) | [9 empty] | 11 | 25 | 4 | 25 |  |  |  |  | Mech Flr above Sctn (Y/N) | N | Y | N | Y | N | N | Y | Y |  | 11 | 25 | 31 | 1041.5 | 317.4492 |  |  | 11 | 31 | 541.5 |  |  | 14.1512 | 7.0684 | 93.0723 | 0.067809 | -520.0928 | -0.061916 | -125.4464 | [8 empty] | 11 | 31 | 541.5 |  | 14.1165 | 17.3262 | -18.168 | 0.086478 | -520.0928 | -0.061916 | -4482.9298 | [8 empty] | 11 | 31 | 541.5 |  |  | 93.0723 | 73.0723 | 37.3093 | -520.0928 | -427.0508 | -10151.1932 | -1685.1008 |  | -17.9277 | 11.5416 | -3.8785 | -520.0928 | -2703.7572 | -71343.523 | 2380.0283 | bar: A to H
| 0.34 | 0.69689 |  |  |  | Leakage Area as % of Envel | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 |  | 10 | 20 | 3 | 20 |  |  |  |  | Leakage Area as % of Envel | 0.4 | 0.35 | 0.3 | 0.25 | 0.3 | 0.35 | 0.4 | 0.3 |  | 10 | 20 | 26 | 974 | 296.8752 |  |  | 10 | 26 | 474 |  |  | 14.186 | 6.8105 | 93.3126 | 0.067935 | -592.8376 | -0.070576 | -142.9924 | [8 empty] | 10 | 26 | 474 |  | 14.1512 | 17.0684 | -17.9277 | 0.086643 | -592.8376 | -0.070576 | -5109.9522 | [8 empty] | 10 | 26 | 474 |  |  | 93.3126 | 73.3126 | 37.4838 | -592.8376 | -485.1864 | -11724.8848 | -1920.7939 |  | -17.6874 | 11.5196 | -3.8166 | -592.8376 | -3087.8082 | -94083.2149 | 3147.0365
| 0.36 | 0.73788 |  |  |  | Envel Leakage Flow Coeff | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 |  | 9 | 15 | 2 | 15 |  |  |  |  | Envel Leakage Flow Coeff | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 |  | 9 | 15 | 21 | 906.5 | 276.3012 |  |  | 9 | 21 | 406.5 |  |  | 14.2209 | 6.5527 | 93.5529 | 0.068061 | -659.1887 | -0.078475 | -158.9963 | [8 empty] | 9 | 21 | 406.5 |  | 14.186 | 16.8105 | -17.6874 | 0.086809 | -659.1887 | -0.078475 | -5681.8637 | [8 empty] | 9 | 21 | 406.5 |  |  | 93.5529 | 73.5529 | 37.6589 | -659.1887 | -537.7265 | -13208.2223 | -2135.7714 |  | -17.4471 | 11.4977 | -3.7547 | -659.1887 | -3439.9459 | -112041.0847 | 3757.7865
| 0.38 | 0.77888 |  |  |  | In-Out PD (in.wg) PI - PO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 8 | 5 | 1 | 5 |  |  |  |  | In-Out PD (in.wg) PI - PO | 0 | 0.005 | 0.005 | 0.005 | 0.005 | 0.005 | 0.005 | 0.005 |  | 8 | 5 | 17 | 771.5 | 235.1532 |  |  | 8 | 17 | 271.5 |  |  | 14.2908 | 6.0371 | 94.0335 | 0.068314 | -779.1125 | -0.092751 | -187.9219 | [8 empty] | 8 | 17 | 271.5 |  | 14.2209 | 16.5527 | -17.4471 | 0.086974 | -779.1125 | -0.092751 | -6715.5448 | [8 empty] | 8 | 17 | 271.5 |  |  | 94.0335 | 74.0335 | 38.0108 | -779.1125 | -631.4273 | -16015.5436 | -2524.3246 |  | -16.9665 | 11.454 | -3.6306 | -779.1125 | -4081.2719 | -140632.9729 | 4742.2202
| 0.4 | 0.81987 | [31 empty] | Section >> |  | 3 | # flrs >> | 6 |  |  | Section >> |  | 3 | 36 |  | Alt psi | Wnd-V | OA-DB | OA-d | Q cfm | Q/Env-A | Tons | [8 empty] | Section >> |  | 3 | 36 | Alt psi | Wnd-V | OA-DB | OA-d | Q cfm | Q/Env-A | KWH | [10 empty] | 3 | 36 |  | OA-DB | Vo ft3/lb | Ho bu/lb | Q ft3/min | Q lbs/hr | btuh | K-btu/yr |  | OA-DB | Vo ft3/lb | Ho bu/lb | Q ft3/min | Q lbs/hr | btuh | K-btu/yr
| 0.42 | 0.86087 |  | EX-3 |  | SECTION No. | a | b | c | d | e | f | g | h |  | 7 | 0 | 3 | 5 |  |  |  |  | SECTION No. >> | 1 | 2-A | 3 | 4-k | 5 | 6 (x) | 7 | 8 |  | 7 | 0 | XX | XX | XX |  |  | 7 | XX | XX |  |  | XX | XX | XX | XX | XX | XX | XX | [8 empty] | 7 | XX | XX |  | XX | XX | XX | XX | XX | XX | XX | [8 empty] | 7 | XX | XX |  |  | XX | XX | XX | XX | XX | XX | XX |  | XX | XX | XX | XX | XX | XX | XX
| 0.44 | 0.90186 |  |  |  | Flr Type (Retl, Offc, ) | Office | Office | Office | Office | Office | Office | Office | Office |  | 6 | 2 | 2 | 3 |  |  |  |  | No. of Flrs (Incl Mech Flr) | 2 | 4 | 6 | 41 | 5 | 25 | 16 | 3 |  | 6 | 2 | 8 | 644 | 196.2912 |  |  | 6 | 8 | 144 |  |  | 14.3572 | 5.55 | 94.4874 | 0.068553 | -1306.4637 | -0.15553 | -315.119 | [8 empty] | 6 | 8 | 144 |  | 14.3572 | 15.55 | -16.5126 | 0.08762 | 2517.3533 | 0.29968 | 21698.2766 | [8 empty] | 6 | 8 | 144 |  |  | 94.4874 | 14.5873 | 38.3452 | -1306.4637 | -5373.7048 | -27496.2904 | -4232.9423 |  | -16.5126 | 11.4129 | -3.5134 | 2517.3533 | 13234.2611 | -240642.9953 | 8156.2248
| 0.46 | 0.94285 |  |  |  | Typical Floor Length (ft) | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 |  | 5 | 1 | 1 | 1 |  |  |  |  | Area per Flr (ft2) | 76800 | 56000 | 38400 | 30800 | 24000 | 18000 | 18000 | 18000 |  | 5 | 1 | 7 | 629 | 191.7192 |  |  | 5 | 7 | 129 |  |  | 14.365 | 5.4927 | 94.5408 | 0.068581 | -1323.6325 | -0.15758 | -319.2602 | [8 empty] | 5 | 7 | 129 |  | 14.365 | 15.4927 | -16.4592 | 0.087657 | 2555.066 | 0.30417 | 22023.34 | [8 empty] | 5 | 7 | 129 |  |  | 94.5408 | 14.5813 | 38.3847 | -1323.6325 | -5446.5587 | -27933.9685 | -4288.5694 |  | -16.4592 | 11.4081 | -3.4996 | 2555.066 | 13438.1999 | -244100.7294 | 8278.4137
| 0.48 | 0.98385 |  |  |  | Typical Floor Width (ft) | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | [9 empty] | Envelope Length (ft) | 1120 | 960 | 800 | 720 | 640 | 560 | 560 | 560 |  | Section >> |  | 2-A | # flrs >> | 4 |  |  | Section >> |  | 2-A | 60.48 |  | Alt psi | Wnd-V | OA-DB | OA-d | Q cfm | Q/Env-A | Tons | [8 empty] | Section >> |  | 2-A | 60.48 | Alt psi | Wnd-V | OA-DB | OA-d | Q cfm | Q/Env-A | KWH | [10 empty] | 2-A | 60.48 |  | OA-DB | Vo ft3/lb | Ho bu/lb | Q ft3/min | Q lbs/hr | btuh | K-btu/yr |  | OA-DB | Vo ft3/lb | Ho bu/lb | Q ft3/min | Q lbs/hr | btuh | K-btu/yr
| 0.5 | 1.0248 |  |  |  | Floor-Floor Height (ft) | 13.5 | 13.5 | 13.5 | 13.5 | 13.5 | 13.5 | 13.5 | 13.5 |  | 4 | 0 | 3 | 3 |  |  |  |  | Envelope Area per Flr (ft2) | 22400 | 17280 | 12000 | 9720 | 9600 | 5600 | 5600 | 8400 |  | 4 | 0 | XX | XX | XX |  |  | 4 | XX | XX |  |  | XX | XX | XX | XX | XX | XX | XX | [8 empty] | 4 | XX | XX |  | XX | XX | XX | XX | XX | XX | XX | [8 empty] | 4 | XX | XX |  |  | XX | XX | XX | XX | XX | XX | XX |  | XX | XX | XX | XX | XX | XX | XX
| 0.52 | 1.0658 |  |  |  | Number of Typical Floors | 2 | 3 | 6 | 40 | 5 | 25 | 15 | 2 |  | 3 | 2 | 2 | 2 |  |  |  |  | Envel Leakage Area (ft2) | 89.6 | 60.48 | 36 | 24.3 | 28.8 | 19.6 | 22.4 | 25.2 |  | 3 | 2 | 4 | 576 | 175.5648 |  |  | 3 | 4 | 76 |  |  | 14.3926 | 5.2903 | 94.7294 | 0.06868 | -2323.8644 | -0.27665 | -560.5161 | [8 empty] | 3 | 4 | 76 |  | XX | XX | XX | XX | 2683.7352 | 0.31949 | 23132.4018 | [8 empty] | 3 | 4 | 76 |  |  | 94.7294 | 14.5602 | 38.5244 | -2323.8644 | -9576.244 | -49516.4264 | -7529.3206 |  | -16.2706 | 11.3911 | -3.4508 | 2683.7352 | 14136.0054 | -255846.3931 | 8695.302
| 0.54 | 1.1068 |  |  |  | Mech Flr above Sctn (Y/N) | [9 empty] | 2 | 1 | 1 | 1 |  |  |  |  | SECTION-Height (ft) | 40 | 74 | 90 | 560 | 75 | 250 | 170 | 50 |  | 2 | 1 | 3 | 558 | 170.0784 |  |  | 2 | 3 | 58 |  |  | 14.402 | 5.2215 | 94.7935 | 0.068714 | -2357.3029 | -0.28063 | -568.5815 | [8 empty] | 2 | 3 | 58 |  | 14.3926 | 15.2903 | -16.2706 | 0.087788 | 2725.9337 | 0.32452 | 23496.1308 | [8 empty] | 2 | 3 | 58 |  |  | 94.7935 | 14.553 | 38.5719 | -2357.3029 | -9718.8206 | -50392.0687 | -7637.6615 |  | -16.2065 | 11.3853 | -3.4342 | 2725.9337 | 14365.5537 | -259680.6155 | 8832.0251 | bar: a to h
| 0.56 | 1.1478 |  |  |  | Leakage Area as % of Envel | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | [9 empty] | Total Section Flr Area (ft2) | 153600 | 224000 | 230400 | 1262800 | 120000 | 450000 | 288000 | 54000 |  | Section >> |  | 1 | # flrs >> | 2 |  |  | Section >> |  | 1 | 89.6 |  | Alt psi | Wnd-V | OA-DB | OA-d | Q cfm | Q/Env-A | Tons | [8 empty] | Section >> |  | 1 | 89.6 | Alt psi | Wnd-V | OA-DB | OA-d | Q cfm | Q/Env-A | KWH | [10 empty] | 1 | 89.6 |  | OA-DB | Vo ft3/lb | Ho bu/lb | Q ft3/min | Q lbs/hr | btuh | K-btu/yr |  | OA-DB | Vo ft3/lb | Ho bu/lb | Q ft3/min | Q lbs/hr | btuh | K-btu/yr
| 0.58 | 1.1888 |  |  |  | Envel Leakage Flow Coeff | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 |  | 2 | 2 | 2 | 2 |  |  |  |  | Totl Section Envel Area (ft2) | 44800 | 69120 | 72000 | 398520 | 48000 | 140000 | 89600 | 25200 |  | 2 | 2 | 2 | 520 | 158.496 |  |  | 2 | 2 | 20 |  |  | 14.4219 | 5.0764 | 94.9288 | 0.068786 | -3339.6037 | -0.39757 | -805.5124 | [8 empty] | 2 | 2 | 20 |  | 14.4219 | 15.0764 | -16.0712 | 0.087927 | 7099.114 | 0.84513 | 61190.6715 | [8 empty] | 2 | 2 | 20 |  |  | 94.9288 | 14.5379 | 38.6724 | -3339.6037 | -13783.0129 | -71878.6379 | -10820.316 |  | -16.0712 | 11.3731 | -3.3992 | 7099.114 | 37452.0571 | -675245.6917 | 23001.1295
| 0.6 | 1.2298 |  |  |  | In-Out PD (in.wg) PI - PO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1 | 1 | 1 | 1 |  |  |  |  | Totl Section Leakg Area (ft2) | 179.2 | 241.92 | 216 | 996.3 | 144 | 490 | 358.4 | 75.6 |  | 1 | 1 | 1 | 500 | 152.4 |  |  | 1 | 1 | 0 |  |  | 14.4324 | 5 | 95 | 0.068823 | -3397.4752 | -0.40446 | -819.471 | [8 empty] | 1 | 1 | 0 |  | 14.4219 | 15.0764 | -16.0712 | 0.087927 | 7208.3748 | 0.85814 | 62132.4423 | [8 empty] | 1 | 1 | 0 |  |  | 95 | 14.53 | 38.7254 | -3397.4752 | -14029.5205 | -73385.4638 | -11007.8196 |  | -16 | 11.3667 | -3.3808 | 7208.3748 | 38049.8785 | -685083.9396 | 23355.1343

## SMMR-Calcs
Bldg Pressurization - Stack Effect & Wind Press Infltr-Exfiltr | [9 empty] | Summer Calcs
[20 empty] | Convert K-Pa to |  |  | In.Hg | 0.29611 | In.H2O | 4.0186 | PSI | 0.14504 | ∆PS = C1*ρO* [ (TO - TI) / TI ] * g * (HNPL - H) |  |  |  |  | C1 = | 0.000598 | g = | 32.17 | C2 = | 0.013
Site Altit |  | 500 | Bldg-H | 1309 | NPL-H | 654.5 |  | Total Bldg Area | 2782800 |  | Total Envel Area |  | 584440 |  | Leakg-A | 1633.42 | Wnd-Vel Diff |  | 5 | Convert in.H20 to |  |  | In.Hg | 0.073684 | K-Pa | 0.24885 | PSI | 0.036092 | ∆PW = C2 * s2 * CP * ρO * (UH)2 / 2 |  |  |  |  | s = | 0.4 | CF = | 0.65 | CP = | 0.065
|  |  | Alt ref Sea-Lvl |  | Outdoor Std. Atm. Press. @ Altit |  |  |  | Wnd Vel | DB | WB | DP | W | RH | V | d | H | Tdb | Twb | Location |  | Psychrometric Calculations for DP, RH, V, W, H, TR | [6 empty] | Q = Cd * A * ( 2 * ∆P/d )0.5 |  |  | Coolg-DD |  | 2680 | TO (OR) | Ti (OR) | ρO = OA dens |  | A = Leakg-A
|  |  | feet | meters | K-Pa | in.Hg | in.H2O | psi | mph | F | F | F | lbs/b | % | ft3/lb | lbs/ft3 | btu/lb | R | R | Description |  | PWSwb | WSwb | PWSdb | VPs | VPa | a | WSdb | ∆PS = | Stack Effect Press Diff (in.wg) |  |  |  | UH = mph |  | Sp.Ht of Air = |  | 0.24
Sea-Level Conditions |  |  | 0 | 0 | 101.325 | 29.9213 | 406.0345 | 14.6546 | 7.5 | 75 | 62 | 53.2919 | 0.0089201 | 48.1285 | 13.6728 | 0.073138 | 27.7612 | 534.7 | 521.7 | Out | Sea-Lvl | 0.27548 | 0.011916 | 0.43051 | 0.87899 | 0.42305 | -1.5741 | 0.018825 | ∆PW = | Wind Press (in.wg) |  |  | Iniltr SHG/hr = CFM * 1.08 (To-Ti)) |  |  |  | Cooling/ year = CFM * 1.08 * CDD
Indoor Conditions |  |  | 500 | 152.4 | 99.5077 | 29.3846 | 398.752 | 14.3917 | 5 | 75 | 62 | 66.0781 | 0.014436 | 40.0699 | 14.53 | 0.068823 | 38.7254 | 554.7 | 534.7 | In | Room | 0.43051 | 0.019179 | 0.817 | 1.6681 | 0.66653 | -1.1195 | 0.037434 | Q = | Airflow Rate (ft3/sec) |  |  | PI - PO | Bldg Pressurization (Inside Press - Outside Press)
8 |  |  | No. of Flrs |  | 2 | Envel-Area per Flr (ft2) |  |  | 8400 | [10 empty] | 8 |  | % Envel-Leakg |  | 0.3 | Leakg Flow Cf |  | 0.6 |  | Inside-Outside (PI-PO) |  |  | 0.005 | Envel Leakg A |  | 25.2 | Section Infltr (tons/yr) |  |  | 366.5563
Level | Sctn | Bldg | Alt ref Sea-Lvl |  | Outdoor Std. Atm. Press. @ Altit |  |  |  | Wnd Vel | DB | WB | DP | W | RH | V | d | H | Tdb | Twb | Level | Bldg | Psychrometric Calculations for DP, RH, V, W, H, TR | [6 empty] | Floor | ∆PS | ∆PW | ∆P = | ∆P + | Leakg Q | Exfl - | Leakage | Q / | SHG | SHG/yr
ID No. | Flr No. | Flr No. | feet | meters | K-Pa | in.Hg | in.H2O | psi | mph | F | F | F | lbs/b | % | ft3/lb | lbs/ft3 | btu/lb | R | R | ID No. | Flr No. | PWSwb | WSwb | PWSdb | VPs | VPa | a | WSdb | Hght | in.H2O | in.H2O | ∆PW+∆PS | PI - PO | ft3/min | Infl + | ft3/min | Envel-A | btuh | tons
24 | 2 | 101 | 1789 | 545.2872 | 94.944 | 28.1134 | 381.5388 | 13.7705 | 9.9236 | 90.4112 | 70.4112 | 60.6391 | 0.012456 | 38.152 | 15.0554 | 0.066421 | 35.4142 | 550.1112 | 530.1112 | 24 | 101 | 0.36878 | 0.017115 | 0.70862 | 1.4468 | 0.55194 | -1.3081 | 0.033743 | 1289 | -0.023368 | 0.00044217 | -0.022926 | -0.017926 | 722.0424 | Exfl | 722.0424 | 0.085957 | 12017.7119 | 2089.8795
23 | 1 | 100 | 1774 | 540.7152 | 94.9961 | 28.1288 | 381.7482 | 13.778 | 9.8663 | 90.4646 | 70.4646 | 60.7032 | 0.012478 | 38.1752 | 15.0491 | 0.066449 | 35.4515 | 550.1646 | 530.1646 | 23 | 100 | 0.36945 | 0.017138 | 0.7098 | 1.4493 | 0.5532 | -1.3058 | 0.033783 | 1274 | -0.022904 | 0.00043727 | -0.022467 | -0.017467 | 712.5913 | Exfl | 712.5913 | 0.084832 | 11901.5041 | 2308.7959
7 |  |  | No. of Flrs |  | 15 | Envel-Area per Flr (ft2) |  |  | 5600 | % Envel-Leakg |  | 0.4 | Leakg Flow Cf |  | 0.6 | Inside-Outside (PI-PO) |  |  | 0.005 | 7 |  | % Envel-Leakg |  | 0.4 | Leakg Flow Cf |  | 0.6 |  | Inside-Outside (PI-PO) |  |  | 0.005 | Envel Leakg A |  | 22.4 | Section Infltr (tons/yr) |  |  | 305.2481
Level | Sctn | Bldg | Alt ref Sea-Lvl |  | Outdoor Std. Atm. Press. @ Altit |  |  |  | Wnd Vel | DB | WB | DP | W | RH | V | d | H | Tdb | Twb | Level | Bldg | Psychrometric Calculations for DP, RH, V, W, H, TR | [6 empty] | Floor | ∆PS | ∆PW | ∆P = | ∆P + | Leakg Q | Exfl - | Leakage | Q / | SHG | SHG/yr
ID No. | Flr No. | Flr No. | feet | meters | K-Pa | in.Hg | in.H2O | psi | mph | F | F | F | lbs/b | % | ft3/lb | lbs/ft3 | btu/lb | R | R | ID No. | Flr No. | PWSwb | WSwb | PWSdb | VPs | VPa | a | WSdb | Hght | in.H2O | in.H2O | ∆PW+∆PS | PI - PO | ft3/min | Infl + | ft3/min | Envel-A | btuh | tons
22 | 0 | XX | XX | XX | XX | XX | XX | XX | XX | [10 empty] | 22 | XX | XX | XX | XX | XX | XX | XX | XX | XX | XX | XX | XX | XX | XX | XX | XX | XX | XX | XX | bar: DB to Twb
21 | 10 | 93 | 1689 | 514.8072 | 95.2919 | 28.2164 | 382.9367 | 13.8209 | 9.5416 | 90.7672 | 70.7672 | 61.0657 | 0.012603 | 38.3065 | 15.0136 | 0.066606 | 35.6638 | 550.4672 | 530.4672 | 21 | 93 | 0.37328 | 0.017265 | 0.71655 | 1.463 | 0.56038 | -1.293 | 0.03401 | 1189 | -0.020196 | 0.00040993 | -0.019786 | -0.014786 | 582.0918 | Exfl | 582.0918 | 0.069297 | 9912.1699 | 1885.9775
20 | 5 | 88 | 1639 | 499.5672 | 95.4662 | 28.268 | 383.6372 | 13.8462 | 9.3506 | 90.9452 | 70.9452 | 61.2787 | 0.012677 | 38.3834 | 14.9928 | 0.066699 | 35.789 | 550.6452 | 530.6452 | 20 | 88 | 0.37554 | 0.01734 | 0.72055 | 1.4712 | 0.56464 | -1.2854 | 0.034144 | 1139 | -0.018539 | 0.00039423 | -0.018145 | -0.013145 | 548.4567 | Exfl | 548.4567 | 0.065292 | 9444.8485 | 1776.9998
6 (x) |  |  | No. of Flrs |  | 25 | Envel-Area per Flr (ft2) |  |  | 5600 | [10 empty] | 6 (x) |  | % Envel-Leakg |  | 0.35 | Leakg Flow Cf |  | -0.6 |  | Inside-Outside (PI-PO) |  |  | 0.005 | Envel Leakg A |  | 19.6 | Section Infltr (tons/yr) |  |  | 294.4968
Level | Sctn | Bldg | Alt ref Sea-Lvl |  | Outdoor Std. Atm. Press. @ Altit |  |  |  | Wnd Vel | DB | WB | DP | W | RH | V | d | H | Tdb | Twb | Level | Bldg | Psychrometric Calculations for DP, RH, V, W, H, TR | [6 empty] | Floor | ∆PS | ∆PW | ∆P = | ∆P + | Leakg Q | Exfl - | Leakage | Q / | SHG | SHG/yr
ID No. | Flr No. | Flr No. | feet | meters | K-Pa | in.Hg | in.H2O | psi | mph | F | F | F | lbs/b | % | ft3/lb | lbs/ft3 | btu/lb | R | R | ID No. | Flr No. | PWSwb | WSwb | PWSdb | VPs | VPa | a | WSdb | Hght | in.H2O | in.H2O | ∆PW+∆PS | PI - PO | ft3/min | Infl + | ft3/min | Envel-A | btuh | tons
19 | 0 | XX | XX | XX | XX | XX | XX | XX | XX | [10 empty] | 19 | XX | XX | XX | XX | XX | XX | XX | XX | XX | XX | XX | XX | XX | XX | XX | XX | XX | XX | XX | bar: DB to Twb
18 | 25 | 83 | 1589 | 484.3272 | 95.6408 | 28.3197 | 384.3388 | 13.8715 | 9.1597 | 91.1232 | 71.1232 | 61.4915 | 0.012751 | 38.46 | 14.972 | 0.066791 | 35.9146 | 550.8232 | 530.8232 | 18 | 83 | 0.37782 | 0.017415 | 0.72457 | 1.4794 | 0.56892 | -1.2778 | 0.034279 | 1089 | -0.016835 | 0.00037881 | -0.016456 | -0.011456 | 447.7002 | Exfl | 447.7002 | 0.053298 | 7795.8096 | 1450.5487
17 | 15 | 73 | 1489 | 453.8472 | 95.9907 | 28.4233 | 385.745 | 13.9223 | 8.7777 | 91.4792 | 71.4792 | 61.9164 | 0.012901 | 38.6126 | 14.9306 | 0.066976 | 36.1666 | 551.1792 | 531.1792 | 17 | 73 | 0.38241 | 0.017567 | 0.73266 | 1.4959 | 0.57756 | -1.2628 | 0.03455 | 989 | -0.013283 | 0.00034884 | -0.012934 | -0.0079341 | 372.0698 | Exfl | 372.0698 | 0.044294 | 6621.909 | 1205.506
16 | 5 | 63 | 1389 | 423.3672 | 96.3417 | 28.5273 | 387.1553 | 13.9732 | 8.3957 | 91.8352 | 71.8352 | 62.3405 | 0.013051 | 38.7642 | 14.8894 | 0.067162 | 36.4198 | 551.5352 | 531.5352 | 16 | 63 | 0.38705 | 0.017719 | 0.74083 | 1.5126 | 0.58629 | -1.2478 | 0.034822 | 889 | -0.0095395 | 0.00032003 | -0.0092195 | -0.0042195 | 270.9588 | Exfl | 270.9588 | 0.032257 | 4926.5663 | 877.9066
5 |  |  | No. of Flrs |  | 5 | Envel-Area per Flr (ft2) |  |  | 9600 | [10 empty] | 5 |  | % Envel-Leakg |  | 0.3 | Leakg Flow Cf |  | 0.6 |  | Inside-Outside (PI-PO) |  |  | 0.005 | Envel Leakg A |  | 28.8 | Section Infltr (tons/yr) |  |  | 118.3483
Level | Sctn | Bldg | Alt ref Sea-Lvl |  | Outdoor Std. Atm. Press. @ Altit |  |  |  | Wnd Vel | DB | WB | DP | W | RH | V | d | H | Tdb | Twb | Level | Bldg | Psychrometric Calculations for DP, RH, V, W, H, TR | [6 empty] | Floor | ∆PS | ∆PW | ∆P = | ∆P + | Leakg Q | Exfl - | Leakage | Q / | SHG | SHG/yr
ID No. | Flr No. | Flr No. | feet | meters | K-Pa | in.Hg | in.H2O | psi | mph | F | F | F | lbs/b | % | ft3/lb | lbs/ft3 | btu/lb | R | R | ID No. | Flr No. | PWSwb | WSwb | PWSdb | VPs | VPa | a | WSdb | Hght | in.H2O | in.H2O | ∆PW+∆PS | PI - PO | ft3/min | Infl + | ft3/min | Envel-A | btuh | tons
15 | 5 | 58 | 1339 | 408.1272 | 96.5175 | 28.5793 | 387.8621 | 13.9987 | 8.2047 | 92.0132 | 72.0132 | 62.5522 | 0.013127 | 38.8396 | 14.8688 | 0.067255 | 36.5469 | 551.7132 | 531.7132 | 15 | 58 | 0.38939 | 0.017796 | 0.74494 | 1.521 | 0.59069 | -1.2403 | 0.034959 | 839 | -0.0075953 | 0.00030606 | -0.0072893 | -0.0022893 | 293.0626 | Exfl | 293.0626 | 0.034888 | 5384.7953 | 949.5229
14 | 3 | 56 | 1309 | 398.9832 | 96.6232 | 28.6106 | 388.2866 | 14.014 | 8.0901 | 92.12 | 72.12 | 62.6792 | 0.013172 | 38.8847 | 14.8565 | 0.067311 | 36.6233 | 551.82 | 531.82 | 14 | 56 | 0.3908 | 0.017842 | 0.74742 | 1.5261 | 0.59335 | -1.2358 | 0.035041 | 809 | -0.0064056 | 0.00029781 | -0.0061078 | -0.0011078 | 203.7751 | Exfl | 203.7751 | 0.024259 | 3767.7113 | 660.2313
13 | 1 | 54 | 1279 | 389.8392 | 96.7289 | 28.6419 | 388.7116 | 14.0293 | 7.9756 | 92.2268 | 72.2268 | 62.8061 | 0.013218 | 38.9297 | 14.8442 | 0.067366 | 36.6998 | 551.9268 | 531.9268 | 13 | 54 | 0.39221 | 0.017888 | 0.74991 | 1.5311 | 0.59601 | -1.2313 | 0.035124 | 779 | -0.0051983 | 0.00028968 | -0.0049086 | 9.1405e-05 | 58.5108 | Infl | -58.5108 | -0.0069656 | -1088.587 | -189.5749
4-k |  |  | No. of Flrs |  | 40 | Envel-Area per Flr (ft2) |  |  | 9720 | [10 empty] | 4-k |  | % Envel-Leakg |  | 0.25 | Leakg Flow Cf |  | 0.6 |  | Inside-Outside (PI-PO) |  |  | 0.005 | Envel Leakg A |  | 24.3 | Section Infltr (tons/yr) |  |  | -807.0327
Level | Sctn | Bldg | Alt ref Sea-Lvl |  | Outdoor Std. Atm. Press. @ Altit |  |  |  | Wnd Vel | DB | WB | DP | W | RH | V | d | H | Tdb | Twb | Level | Bldg | Psychrometric Calculations for DP, RH, V, W, H, TR | [6 empty] | Floor | ∆PS | ∆PW | ∆P = | ∆P + | Leakg Q | Exfl - | Leakage | Q / | SHG | SHG/yr
ID No. | Flr No. | Flr No. | feet | meters | K-Pa | in.Hg | in.H2O | psi | mph | F | F | F | lbs/b | % | ft3/lb | lbs/ft3 | btu/lb | R | R | ID No. | Flr No. | PWSwb | WSwb | PWSdb | VPs | VPa | a | WSdb | Hght | in.H2O | in.H2O | ∆PW+∆PS | PI - PO | ft3/min | Infl + | ft3/min | Envel-A | btuh | tons
12 | 30 | 36 | 1109 | 338.0232 | 97.3299 | 28.8199 | 391.1266 | 14.1165 | 7.3262 | 92.832 | 72.832 | 63.5239 | 0.013478 | 39.1834 | 14.7747 | 0.067683 | 37.1354 | 552.532 | 532.532 | 12 | 36 | 0.4003 | 0.018152 | 0.76412 | 1.5602 | 0.61127 | -1.206 | 0.035594 | 609 | 0.0019758 | 0.00024558 | 0.0022213 | 0.0072213 | 437.7785 | Infl | -437.7785 | -0.052116 | -8430.9645 | -1418.4023
11 | 25 | 31 | 1041.5 | 317.4492 | 97.5694 | 28.8908 | 392.0889 | 14.1512 | 7.0684 | 93.0723 | 73.0723 | 63.8082 | 0.013582 | 39.2833 | 14.7473 | 0.067809 | 37.3093 | 552.7723 | 532.7723 | 11 | 31 | 0.40356 | 0.018258 | 0.76984 | 1.5718 | 0.61741 | -1.196 | 0.035783 | 541.5 | 0.0049822 | 0.00022902 | 0.0052112 | 0.010211 | 520.0928 | Infl | -520.0928 | -0.061916 | -10151.1932 | -1685.1008
10 | 20 | 26 | 974 | 296.8752 | 97.8093 | 28.9618 | 393.0531 | 14.186 | 6.8105 | 93.3126 | 73.3126 | 64.0923 | 0.013687 | 39.3829 | 14.72 | 0.067935 | 37.4838 | 553.0126 | 533.0126 | 10 | 26 | 0.40683 | 0.018364 | 0.77558 | 1.5836 | 0.62359 | -1.1861 | 0.035972 | 474 | 0.0080791 | 0.00021301 | 0.0082921 | 0.013292 | 592.8376 | Infl | -592.8376 | -0.070576 | -11724.8848 | -1920.7939
9 | 15 | 21 | 906.5 | 276.3012 | 98.0497 | 29.033 | 394.0192 | 14.2209 | 6.5527 | 93.5529 | 73.5529 | 64.376 | 0.013792 | 39.482 | 14.6927 | 0.068061 | 37.6589 | 553.2529 | 533.2529 | 9 | 21 | 0.41013 | 0.018471 | 0.78137 | 1.5954 | 0.62982 | -1.1761 | 0.036162 | 406.5 | 0.011267 | 0.00019755 | 0.011464 | 0.016464 | 659.1887 | Infl | -659.1887 | -0.078475 | -13208.2223 | -2135.7714
8 | 5 | 17 | 771.5 | 235.1532 | 98.532 | 29.1758 | 395.9572 | 14.2908 | 6.0371 | 94.0335 | 74.0335 | 64.9425 | 0.014004 | 39.6789 | 14.6383 | 0.068314 | 38.0108 | 553.7335 | 533.7335 | 8 | 17 | 0.4168 | 0.018686 | 0.79305 | 1.6192 | 0.64243 | -1.1563 | 0.036544 | 271.5 | 0.017917 | 0.00016831 | 0.018085 | 0.023085 | 779.1125 | Infl | -779.1125 | -0.092751 | -16015.5436 | -2524.3246
3 |  |  | No. of Flrs |  | 6 | Envel-Area per Flr (ft2) |  |  | 12000 | [10 empty] | 3 |  | % Envel-Leakg |  | 0.3 | Leakg Flow Cf |  | 0.6 |  | Inside-Outside (PI-PO) |  |  | 0.005 | Envel Leakg A |  | 36 | Section Infltr (tons/yr) |  |  | -710.126
Level | Sctn | Bldg | Alt ref Sea-Lvl |  | Outdoor Std. Atm. Press. @ Altit |  |  |  | Wnd Vel | DB | WB | DP | W | RH | V | d | H | Tdb | Twb | Level | Bldg | Psychrometric Calculations for DP, RH, V, W, H, TR | [6 empty] | Floor | ∆PS | ∆PW | ∆P = | ∆P + | Leakg Q | Exfl - | Leakage | Q / | SHG | SHG/yr
ID No. | Flr No. | Flr No. | feet | meters | K-Pa | in.Hg | in.H2O | psi | mph | F | F | F | lbs/b | % | ft3/lb | lbs/ft3 | btu/lb | R | R | ID No. | Flr No. | PWSwb | WSwb | PWSdb | VPs | VPa | a | WSdb | Hght | in.H2O | in.H2O | ∆PW+∆PS | PI - PO | ft3/min | Infl + | ft3/min | Envel-A | btuh | tons
7 | 0 | XX | XX | XX | XX | XX | XX | XX | XX | [10 empty] | 7 | XX | XX | XX | XX | XX | XX | XX | XX | XX | XX | XX | XX | XX | XX | XX | XX | XX | XX | XX | bar: DB to Twb
6 | 2 | 8 | 644 | 196.2912 | 98.9892 | 29.3112 | 397.7946 | 14.3572 | 5.55 | 94.4874 | 74.4874 | 65.4764 | 0.014206 | 39.8634 | 14.5873 | 0.068553 | 38.3452 | 554.1874 | 534.1874 | 6 | 8 | 0.42319 | 0.01889 | 0.80422 | 1.642 | 0.6545 | -1.1377 | 0.036908 | 144 | 0.024537 | 0.00014275 | 0.024679 | 0.029679 | 1306.4637 | Infl | -1306.4637 | -0.15553 | -27496.2904 | -4232.9423
5 | 1 | 7 | 629 | 191.7192 | 99.0431 | 29.3272 | 398.0112 | 14.365 | 5.4927 | 94.5408 | 74.5408 | 65.5391 | 0.01423 | 39.885 | 14.5813 | 0.068581 | 38.3847 | 554.2408 | 534.2408 | 5 | 7 | 0.42395 | 0.018914 | 0.80554 | 1.6447 | 0.65594 | -1.1355 | 0.036951 | 129 | 0.025337 | 0.00013987 | 0.025477 | 0.030477 | 1323.6325 | Infl | -1323.6325 | -0.15758 | -27933.9685 | -4288.5694
2-A |  |  | No. of Flrs |  | 3 | Envel-Area per Flr (ft2) |  |  | 17280 | [10 empty] | 2-A |  | % Envel-Leakg |  | 0.35 | Leakg Flow Cf |  | 0.6 |  | Inside-Outside (PI-PO) |  |  | 0.005 | Envel Leakg A |  | 60.48 | Section Infltr (tons/yr) |  |  | -1263.9152
Level | Sctn | Bldg | Alt ref Sea-Lvl |  | Outdoor Std. Atm. Press. @ Altit |  |  |  | Wnd Vel | DB | WB | DP | W | RH | V | d | H | Tdb | Twb | Level | Bldg | Psychrometric Calculations for DP, RH, V, W, H, TR | [6 empty] | Floor | ∆PS | ∆PW | ∆P = | ∆P + | Leakg Q | Exfl - | Leakage | Q / | SHG | SHG/yr
ID No. | Flr No. | Flr No. | feet | meters | K-Pa | in.Hg | in.H2O | psi | mph | F | F | F | lbs/b | % | ft3/lb | lbs/ft3 | btu/lb | R | R | ID No. | Flr No. | PWSwb | WSwb | PWSdb | VPs | VPa | a | WSdb | Hght | in.H2O | in.H2O | ∆PW+∆PS | PI - PO | ft3/min | Infl + | ft3/min | Envel-A | btuh | tons
4 | 0 | XX | XX | XX | XX | XX | XX | XX | XX | [10 empty] | 4 | XX | XX | XX | XX | XX | XX | XX | XX | XX | XX | XX | XX | XX | XX | XX | XX | XX | XX | XX | bar: DB to Twb
3 | 2 | 4 | 576 | 175.5648 | 99.2338 | 29.3836 | 398.7774 | 14.3926 | 5.2903 | 94.7294 | 74.7294 | 65.7607 | 0.014314 | 39.9611 | 14.5602 | 0.06868 | 38.5244 | 554.4294 | 534.4294 | 3 | 4 | 0.42663 | 0.019 | 0.81023 | 1.6543 | 0.66102 | -1.1278 | 0.037103 | 76 | 0.028203 | 0.00012994 | 0.028333 | 0.033333 | 2323.8644 | Infl | -2323.8644 | -0.27665 | -49516.4264 | -7529.3206
2 | 1 | 3 | 558 | 170.0784 | 99.2986 | 29.4028 | 399.0379 | 14.402 | 5.2215 | 94.7935 | 74.7935 | 65.8359 | 0.014343 | 39.987 | 14.553 | 0.068714 | 38.5719 | 554.4935 | 534.4935 | 2 | 3 | 0.42755 | 0.019029 | 0.81183 | 1.6576 | 0.66275 | -1.1252 | 0.037155 | 58 | 0.029189 | 0.00012665 | 0.029316 | 0.034316 | 2357.3029 | Infl | -2357.3029 | -0.28063 | -50392.0687 | -7637.6615
1 |  |  | No. of Flrs |  | 2 | Envel-Area per Flr (ft2) |  |  | 22400 | [10 empty] | 1 |  | % Envel-Leakg |  | 0.4 | Leakg Flow Cf |  | 0.6 |  | Inside-Outside (PI-PO) |  |  | 0 | Envel Leakg A |  | 89.6 | Section Infltr (tons/yr) |  |  | -1819.0113
Level | Sctn | Bldg | Alt ref Sea-Lvl |  | Outdoor Std. Atm. Press. @ Altit |  |  |  | Wnd Vel | DB | WB | DP | W | RH | V | d | H | Tdb | Twb | Level | Bldg | Psychrometric Calculations for DP, RH, V, W, H, TR | [6 empty] | Floor | ∆PS | ∆PW | ∆P = | ∆P + | Leakg Q | Exfl - | Leakage | Q / | SHG | SHG/yr
ID No. | Flr No. | Flr No. | feet | meters | K-Pa | in.Hg | in.H2O | psi | mph | F | F | F | lbs/b | % | ft3/lb | lbs/ft3 | btu/lb | R | R | ID No. | Flr No. | PWSwb | WSwb | PWSdb | VPs | VPa | a | WSdb | Hght | in.H2O | in.H2O | ∆PW+∆PS | PI - PO | ft3/min | Infl + | ft3/min | Envel-A | btuh | tons
2 | 2 | 2 | 520 | 158.496 | 99.4355 | 29.4434 | 399.5882 | 14.4219 | 5.0764 | 94.9288 | 74.9288 | 65.9946 | 0.014404 | 40.0414 | 14.5379 | 0.068786 | 38.6724 | 554.6288 | 534.6288 | 2 | 2 | 0.42948 | 0.019091 | 0.81521 | 1.6645 | 0.66642 | -1.1197 | 0.037264 | 20 | 0.031293 | 0.00011983 | 0.031413 | 0.031413 | 3339.6037 | Infl | -3339.6037 | -0.39757 | -71878.6379 | -10820.316
1 | 1 | 1 | 500 | 152.4 | 99.5077 | 29.4647 | 399.8781 | 14.4324 | 5 | 95 | 75 | 66.0781 | 0.014436 | 40.0699 | 14.53 | 0.068823 | 38.7254 | 554.7 | 534.7 | 1 | 1 | 0.43051 | 0.019124 | 0.817 | 1.6681 | 0.66835 | -1.1168 | 0.037322 | 0 | 0.032413 | 0.00011631 | 0.032529 | 0.032529 | 3397.4752 | Infl | -3397.4752 | -0.40446 | -73385.4638 | -11007.8196

## WNTR-Calcs
Bldg Pressurization - Stack Effect & Wind Press Infltr-Exfiltr | [9 empty] | Summer Calcs
[20 empty] | Convert K-Pa to |  |  | In.Hg | 0.29611 | In.H2O | 4.0186 | PSI | 0.14504 | ∆PS = C1*ρO* [ (TO - TI) / TI ] * g * (HNPL - H) |  |  |  |  | C1 = | 0.000598 | g = | 32.17 | C2 = | 0.013
Site Altit |  | 500 | Bldg-H | 1309 | NPL-H | 654.5 |  | Total Bldg Area | 2782800 |  | Total Envel Area |  | 584440 |  | Leakg-A | 1633.42 | Wnd-Vel Diff |  | 5 | Convert in.H20 to |  |  | In.Hg | 0.073684 | K-Pa | 0.24885 | PSI | 0.036092 | ∆PW = C2 * s2 * CP * ρO * (UH)2 / 2 |  |  |  |  | s = | 0.4 | CF = | 0.65 | CP = | 0.065
|  |  | Alt ref Sea-Lvl |  | Outdoor Std. Atm. Press. @ Altit |  |  |  | Wnd Vel | DB | WB | DP | W | RH | V | d | H | Tdb | Twb | Location |  | Psychrometric Calculations for DP, RH, V, W, H, TR | [6 empty] | Q = Cd * A * ( 2 * ∆P/d )0.5 |  |  | Coolg-DD |  | 7981 | TO (OR) | Ti (OR) | ρO = OA dens |  | A = Leakg-A
|  |  | feet | meters | K-Pa | in.Hg | in.H2O | psi | mph | F | F | F | lbs/b | % | ft3/lb | lbs/ft3 | btu/lb | R | R | Description |  | PWSwb | WSwb | PWSdb | VPs | VPa | a | WSdb | ∆PS = | Stack Effect Press Diff (in.wg) |  |  |  | UH = mph |  | Sp.Ht of Air = |  | 0.24
Sea-Level Conditions |  |  | 0 | 0 | 101.325 | 29.9213 | 406.0345 | 14.6546 | 7.5 | 75 | 62 | 53.2919 | 0.0089201 | 48.1285 | 13.6728 | 0.073138 | 27.7612 | 534.7 | 521.7 | Out | Sea-Lvl | 0.27548 | 0.011916 | 0.43051 | 0.87899 | 0.42305 | -1.5741 | 0.018825 | ∆PW = | Wind Press (in.wg) |  |  | Iniltr SHG/hr = CFM * 1.08 (To-Ti)) |  |  |  | Cooling/ year = CFM * 1.08 * CDD
Indoor Conditions |  |  | 500 | 152.4 | 99.5077 | 29.3846 | 398.752 | 14.3917 | 15 | 72 | 55 | -19.6727 | 0.00043573 | 100 | 11.3667 | 0.087976 | -3.3808 | 443.7 | 443.7 | In | Room | 0.010104 | 0.00043696 | 0.010104 | 0.020629 | 0.020571 | -4.5977 | 0.00043696 | Q = | Airflow Rate (ft3/sec) |  |  | PI - PO | Bldg Pressurization (Inside Press - Outside Press)
8 |  |  | No. of Flrs |  | 2 | Envel-Area per Flr (ft2) |  |  | 8400 | [10 empty] | 8 |  | % Envel-Leakg |  | 0.3 | Leakg Flow Cf |  | 0.6 |  | Inside-Outside (PI-PO) |  |  | 0.005 | Envel Leakg A |  | 25.2 | Section Infltr (K-btu/yr) |  |  | -24743.5942
Level | Sctn | Bldg | Alt ref Sea-Lvl |  | Outdoor Std. Atm. Press. @ Altit |  |  |  | Wnd Vel | DB | WB | DP | W | RH | V | d | H | Tdb | Twb | Level | Bldg | Psychrometric Calculations for DP, RH, V, W, H, TR | [6 empty] | Floor | ∆PS | ∆PW | ∆P = | ∆P + | Leakg Q | Exfl - | Leakage | Q / | SHL | SHL/yr
ID No. | Flr No. | Flr No. | feet | meters | K-Pa | in.Hg | in.H2O | psi | mph | F | F | F | lbs/b | % | ft3/lb | lbs/ft3 | btu/lb | R | R | ID No. | Flr No. | PWSwb | WSwb | PWSdb | VPs | VPa | a | WSdb | Hght | in.H2O | in.H2O | ∆PW+∆PS | PI - PO | ft3/min | Infl + | ft3/min | Envel-A | btuh | K-btu
24 | 2 | 101 | 1789 | 545.2872 | 94.944 | 28.1134 | 381.5388 | 13.7705 | 19.9236 | -20.5888 | -20.5888 | -25.0224 | 0.0003608 | 100 | 11.7885 | 0.084829 | -4.5618 | 439.1112 | 439.1112 | 24 | 101 | 0.0079834 | 0.0003608 | 0.0079834 | 0.0163 | 0.016299 | -4.8305 | 0.0003608 | 1289 | 0.18511 | 0.0022763 | 0.18738 | 0.19238 | 2093.1136 | Infl | -2093.1136 | -0.24918 | 209302.8804 | -18041.5511
23 | 1 | 100 | 1774 | 540.7152 | 94.9961 | 28.1288 | 381.7482 | 13.778 | 19.8663 | -20.5354 | -20.5354 | -24.9594 | 0.0003616 | 100 | 11.7834 | 0.084865 | -4.5481 | 439.1646 | 439.1646 | 23 | 100 | 0.0080055 | 0.0003616 | 0.0080055 | 0.016345 | 0.016344 | -4.8277 | 0.0003616 | 1274 | 0.18071 | 0.0022642 | 0.18297 | 0.18797 | 2068.5318 | Infl | -2068.5318 | -0.24625 | 206725.5015 | -6702.0431
7 |  |  | No. of Flrs |  | 15 | Envel-Area per Flr (ft2) |  |  | 5600 | % Envel-Leakg |  | 0.4 | Leakg Flow Cf |  | 0.6 | Inside-Outside (PI-PO) |  |  | 0.005 | 7 |  | % Envel-Leakg |  | 0.4 | Leakg Flow Cf |  | 0.6 |  | Inside-Outside (PI-PO) |  |  | 0.005 | Envel Leakg A |  | 22.4 | Section Infltr (K-btu/yr) |  |  | -10822.3323
Level | Sctn | Bldg | Alt ref Sea-Lvl |  | Outdoor Std. Atm. Press. @ Altit |  |  |  | Wnd Vel | DB | WB | DP | W | RH | V | d | H | Tdb | Twb | Level | Bldg | Psychrometric Calculations for DP, RH, V, W, H, TR | [6 empty] | Floor | ∆PS | ∆PW | ∆P = | ∆P + | Leakg Q | Exfl - | Leakage | Q / | SHL | SHL/yr
ID No. | Flr No. | Flr No. | feet | meters | K-Pa | in.Hg | in.H2O | psi | mph | F | F | F | lbs/b | % | ft3/lb | lbs/ft3 | btu/lb | R | R | ID No. | Flr No. | PWSwb | WSwb | PWSdb | VPs | VPa | a | WSdb | Hght | in.H2O | in.H2O | ∆PW+∆PS | PI - PO | ft3/min | Infl + | ft3/min | Envel-A | btuh | K-btu
22 | 0 | XX | XX | XX | XX | XX | XX | XX | XX | [10 empty] | 22 | XX | XX | XX | XX | XX | XX | XX | XX | XX | XX | XX | XX | XX | XX | XX | XX | XX | XX | XX | bar: DB to Twb
21 | 10 | 93 | 1689 | 514.8072 | 95.2919 | 28.2164 | 382.9367 | 13.8209 | 19.5416 | -20.2328 | -20.2328 | -24.6025 | 0.00036619 | 100 | 11.755 | 0.08507 | -4.4706 | 439.4672 | 439.4672 | 21 | 93 | 0.0081322 | 0.00036619 | 0.0081322 | 0.016604 | 0.016602 | -4.812 | 0.00036619 | 1189 | 0.15579 | 0.0021961 | 0.15799 | 0.16299 | 1710.0982 | Infl | -1710.0982 | -0.20358 | 170345.3876 | -5540.7181
20 | 5 | 88 | 1639 | 499.5672 | 95.4662 | 28.268 | 383.6372 | 13.8462 | 19.3506 | -20.0548 | -20.0548 | -24.3929 | 0.0003689 | 100 | 11.7384 | 0.085191 | -4.425 | 439.6452 | 439.6452 | 20 | 88 | 0.0082075 | 0.0003689 | 0.0082075 | 0.016758 | 0.016756 | -4.8028 | 0.0003689 | 1139 | 0.14116 | 0.0021564 | 0.14331 | 0.14831 | 1630.1279 | Infl | -1630.1279 | -0.19406 | 162066.0511 | -5281.6142
6 (x) |  |  | No. of Flrs |  | 25 | Envel-Area per Flr (ft2) |  |  | 5600 | [10 empty] | 6 (x) |  | % Envel-Leakg |  | 0.35 | Leakg Flow Cf |  | -0.6 |  | Inside-Outside (PI-PO) |  |  | 0.005 | Envel Leakg A |  | 19.6 | Section Infltr (K-btu/yr) |  |  | -11529.7197
Level | Sctn | Bldg | Alt ref Sea-Lvl |  | Outdoor Std. Atm. Press. @ Altit |  |  |  | Wnd Vel | DB | WB | DP | W | RH | V | d | H | Tdb | Twb | Level | Bldg | Psychrometric Calculations for DP, RH, V, W, H, TR | [6 empty] | Floor | ∆PS | ∆PW | ∆P = | ∆P + | Leakg Q | Exfl - | Leakage | Q / | SHL | SHL/yr
ID No. | Flr No. | Flr No. | feet | meters | K-Pa | in.Hg | in.H2O | psi | mph | F | F | F | lbs/b | % | ft3/lb | lbs/ft3 | btu/lb | R | R | ID No. | Flr No. | PWSwb | WSwb | PWSdb | VPs | VPa | a | WSdb | Hght | in.H2O | in.H2O | ∆PW+∆PS | PI - PO | ft3/min | Infl + | ft3/min | Envel-A | btuh | K-btu
19 | 0 | XX | XX | XX | XX | XX | XX | XX | XX | [10 empty] | 19 | XX | XX | XX | XX | XX | XX | XX | XX | XX | XX | XX | XX | XX | XX | XX | XX | XX | XX | XX | bar: DB to Twb
18 | 25 | 83 | 1589 | 484.3272 | 95.6408 | 28.3197 | 384.3388 | 13.8715 | 19.1597 | -19.8768 | -19.8768 | -24.1835 | 0.00037164 | 100 | 11.7218 | 0.085311 | -4.3794 | 439.8232 | 439.8232 | 18 | 83 | 0.0082835 | 0.00037164 | 0.0082835 | 0.016913 | 0.016911 | -4.7936 | 0.00037164 | 1089 | 0.12653 | 0.002117 | 0.12865 | 0.13365 | 1353.052 | Infl | -1353.052 | -0.16108 | 134259.2686 | -4383.8883
17 | 15 | 73 | 1489 | 453.8472 | 95.9907 | 28.4233 | 385.745 | 13.9223 | 18.7777 | -19.5208 | -19.5208 | -23.7653 | 0.00037717 | 100 | 11.6886 | 0.085554 | -4.2881 | 440.1792 | 440.1792 | 17 | 73 | 0.0084373 | 0.00037717 | 0.0084373 | 0.017227 | 0.017225 | -4.7752 | 0.00037717 | 989 | 0.09732 | 0.0020392 | 0.09936 | 0.10436 | 1193.9411 | Infl | -1193.9411 | -0.14214 | 118012.133 | -3868.3692
16 | 5 | 63 | 1389 | 423.3672 | 96.3417 | 28.5273 | 387.1553 | 13.9732 | 18.3957 | -19.1648 | -19.1648 | -23.3479 | 0.00038276 | 100 | 11.6555 | 0.085796 | -4.1967 | 440.5352 | 440.5352 | 16 | 63 | 0.0085937 | 0.00038276 | 0.0085937 | 0.017546 | 0.017545 | -4.7568 | 0.00038276 | 889 | 0.068162 | 0.0019627 | 0.070125 | 0.075125 | 1011.5624 | Infl | -1011.5624 | -0.12042 | 99596.4395 | -3277.4622
5 |  |  | No. of Flrs |  | 5 | Envel-Area per Flr (ft2) |  |  | 9600 | [10 empty] | 5 |  | % Envel-Leakg |  | 0.3 | Leakg Flow Cf |  | 0.6 |  | Inside-Outside (PI-PO) |  |  | 0.005 | Envel Leakg A |  | 28.8 | Section Infltr (K-btu/yr) |  |  | -11952.3179
Level | Sctn | Bldg | Alt ref Sea-Lvl |  | Outdoor Std. Atm. Press. @ Altit |  |  |  | Wnd Vel | DB | WB | DP | W | RH | V | d | H | Tdb | Twb | Level | Bldg | Psychrometric Calculations for DP, RH, V, W, H, TR | [6 empty] | Floor | ∆PS | ∆PW | ∆P = | ∆P + | Leakg Q | Exfl - | Leakage | Q / | SHL | SHL/yr
ID No. | Flr No. | Flr No. | feet | meters | K-Pa | in.Hg | in.H2O | psi | mph | F | F | F | lbs/b | % | ft3/lb | lbs/ft3 | btu/lb | R | R | ID No. | Flr No. | PWSwb | WSwb | PWSdb | VPs | VPa | a | WSdb | Hght | in.H2O | in.H2O | ∆PW+∆PS | PI - PO | ft3/min | Infl + | ft3/min | Envel-A | btuh | K-btu
15 | 5 | 58 | 1339 | 408.1272 | 96.5175 | 28.5793 | 387.8621 | 13.9987 | 18.2047 | -18.9868 | -18.9868 | -23.1395 | 0.00038559 | 100 | 11.639 | 0.085918 | -4.151 | 440.7132 | 440.7132 | 15 | 58 | 0.0086729 | 0.00038559 | 0.0086729 | 0.017708 | 0.017706 | -4.7477 | 0.00038559 | 839 | 0.053603 | 0.0019249 | 0.055528 | 0.060528 | 1333.2389 | Infl | -1333.2389 | -0.15872 | 131011.7705 | -4319.6941
14 | 3 | 56 | 1309 | 398.9832 | 96.6232 | 28.6106 | 388.2866 | 14.014 | 18.0901 | -18.88 | -18.88 | -23.0146 | 0.00038729 | 100 | 11.6292 | 0.085991 | -4.1235 | 440.82 | 440.82 | 14 | 56 | 0.0087207 | 0.00038729 | 0.0087207 | 0.017806 | 0.017804 | -4.7422 | 0.00038729 | 809 | 0.044874 | 0.0019023 | 0.046776 | 0.051776 | 1232.5716 | Infl | -1232.5716 | -0.14673 | 120977.4439 | -3993.5318
13 | 1 | 54 | 1279 | 389.8392 | 96.7289 | 28.6419 | 388.7116 | 14.0293 | 17.9756 | -18.7732 | -18.7732 | -22.8898 | 0.000389 | 100 | 11.6193 | 0.086064 | -4.0961 | 440.9268 | 440.9268 | 13 | 54 | 0.0087688 | 0.000389 | 0.0087688 | 0.017904 | 0.017902 | -4.7367 | 0.000389 | 779 | 0.03615 | 0.0018799 | 0.03803 | 0.04303 | 1123.1766 | Infl | -1123.1766 | -0.13371 | 110110.7261 | -3639.0921
4-k |  |  | No. of Flrs |  | 40 | Envel-Area per Flr (ft2) |  |  | 9720 | [10 empty] | 4-k |  | % Envel-Leakg |  | 0.25 | Leakg Flow Cf |  | 0.6 |  | Inside-Outside (PI-PO) |  |  | 0.005 | Envel Leakg A |  | 24.3 | Section Infltr (K-btu/yr) |  |  | 15211.5748
Level | Sctn | Bldg | Alt ref Sea-Lvl |  | Outdoor Std. Atm. Press. @ Altit |  |  |  | Wnd Vel | DB | WB | DP | W | RH | V | d | H | Tdb | Twb | Level | Bldg | Psychrometric Calculations for DP, RH, V, W, H, TR | [6 empty] | Floor | ∆PS | ∆PW | ∆P = | ∆P + | Leakg Q | Exfl - | Leakage | Q / | SHL | SHL/yr
ID No. | Flr No. | Flr No. | feet | meters | K-Pa | in.Hg | in.H2O | psi | mph | F | F | F | lbs/b | % | ft3/lb | lbs/ft3 | btu/lb | R | R | ID No. | Flr No. | PWSwb | WSwb | PWSdb | VPs | VPa | a | WSdb | Hght | in.H2O | in.H2O | ∆PW+∆PS | PI - PO | ft3/min | Infl + | ft3/min | Envel-A | btuh | K-btu
12 | 30 | 36 | 1109 | 338.0232 | 97.3299 | 28.8199 | 391.1266 | 14.1165 | 17.3262 | -18.168 | -18.168 | -22.1836 | 0.00039881 | 100 | 11.5636 | 0.086478 | -3.9404 | 441.532 | 441.532 | 12 | 36 | 0.0090456 | 0.00039881 | 0.0090456 | 0.018469 | 0.018467 | -4.7056 | 0.00039881 | 609 | -0.013189 | 0.0017549 | -0.011435 | -0.0064346 | 365.5875 | Exfl | 365.5875 | 0.043522 | -35601.4486 | 1184.5034
11 | 25 | 31 | 1041.5 | 317.4492 | 97.5694 | 28.8908 | 392.0889 | 14.1512 | 17.0684 | -17.9277 | -17.9277 | -21.9039 | 0.00040277 | 100 | 11.5416 | 0.086643 | -3.8785 | 441.7723 | 441.7723 | 11 | 31 | 0.0091578 | 0.00040277 | 0.0091578 | 0.018698 | 0.018696 | -4.6933 | 0.00040277 | 541.5 | -0.032734 | 0.0017063 | -0.031028 | -0.026028 | 734.5766 | Exfl | 734.5766 | 0.08745 | -71343.523 | 2380.0283
10 | 20 | 26 | 974 | 296.8752 | 97.8093 | 28.9618 | 393.0531 | 14.186 | 16.8105 | -17.6874 | -17.6874 | -21.6245 | 0.00040675 | 100 | 11.5196 | 0.086809 | -3.8166 | 442.0126 | 442.0126 | 10 | 26 | 0.0092711 | 0.00040675 | 0.0092711 | 0.01893 | 0.018928 | -4.6809 | 0.00040675 | 474 | -0.052252 | 0.0016583 | -0.050594 | -0.045594 | 971.3076 | Exfl | 971.3076 | 0.11563 | -94083.2149 | 3147.0365
9 | 15 | 21 | 906.5 | 276.3012 | 98.0497 | 29.033 | 394.0192 | 14.2209 | 16.5527 | -17.4471 | -17.4471 | -21.3455 | 0.00041078 | 100 | 11.4977 | 0.086974 | -3.7547 | 442.2529 | 442.2529 | 9 | 21 | 0.0093857 | 0.00041078 | 0.0093857 | 0.019164 | 0.019162 | -4.6687 | 0.00041078 | 406.5 | -0.071743 | 0.0016109 | -0.070132 | -0.065132 | 1159.8106 | Exfl | 1159.8106 | 0.13807 | -112041.0847 | 3757.7865
8 | 5 | 17 | 771.5 | 235.1532 | 98.532 | 29.1758 | 395.9572 | 14.2908 | 16.0371 | -16.9665 | -16.9665 | -20.7886 | 0.00041892 | 100 | 11.454 | 0.087306 | -3.6306 | 442.7335 | 442.7335 | 8 | 17 | 0.0096188 | 0.00041892 | 0.0096188 | 0.019639 | 0.019638 | -4.6441 | 0.00041892 | 271.5 | -0.11064 | 0.0015179 | -0.10912 | -0.10412 | 1463.6482 | Exfl | 1463.6482 | 0.17424 | -140632.9729 | 4742.2202
3 |  |  | No. of Flrs |  | 6 | Envel-Area per Flr (ft2) |  |  | 12000 | [10 empty] | 3 |  | % Envel-Leakg |  | 0.3 | Leakg Flow Cf |  | 0.6 |  | Inside-Outside (PI-PO) |  |  | 0.005 | Envel Leakg A |  | 36 | Section Infltr (K-btu/yr) |  |  | 16434.6385
Level | Sctn | Bldg | Alt ref Sea-Lvl |  | Outdoor Std. Atm. Press. @ Altit |  |  |  | Wnd Vel | DB | WB | DP | W | RH | V | d | H | Tdb | Twb | Level | Bldg | Psychrometric Calculations for DP, RH, V, W, H, TR | [6 empty] | Floor | ∆PS | ∆PW | ∆P = | ∆P + | Leakg Q | Exfl - | Leakage | Q / | SHL | SHL/yr
ID No. | Flr No. | Flr No. | feet | meters | K-Pa | in.Hg | in.H2O | psi | mph | F | F | F | lbs/b | % | ft3/lb | lbs/ft3 | btu/lb | R | R | ID No. | Flr No. | PWSwb | WSwb | PWSdb | VPs | VPa | a | WSdb | Hght | in.H2O | in.H2O | ∆PW+∆PS | PI - PO | ft3/min | Infl + | ft3/min | Envel-A | btuh | K-btu
7 | 0 | XX | XX | XX | XX | XX | XX | XX | XX | [10 empty] | 7 | XX | XX | XX | XX | XX | XX | XX | XX | XX | XX | XX | XX | XX | XX | XX | XX | XX | XX | XX | bar: DB to Twb
6 | 2 | 8 | 644 | 196.2912 | 98.9892 | 29.3112 | 397.7946 | 14.3572 | 15.55 | -16.5126 | -16.5126 | -20.2639 | 0.00042674 | 100 | 11.4129 | 0.08762 | -3.5134 | 443.1874 | 443.1874 | 6 | 8 | 0.0098438 | 0.00042674 | 0.0098438 | 0.020099 | 0.020097 | -4.621 | 0.00042674 | 144 | -0.14727 | 0.0014322 | -0.14584 | -0.14084 | 2517.3533 | Exfl | 2517.3533 | 0.29968 | -240642.9953 | 8156.2248
5 | 1 | 7 | 629 | 191.7192 | 99.0431 | 29.3272 | 398.0112 | 14.365 | 15.4927 | -16.4592 | -16.4592 | -20.2022 | 0.00042767 | 100 | 11.4081 | 0.087657 | -3.4996 | 443.2408 | 443.2408 | 5 | 7 | 0.0098705 | 0.00042767 | 0.0098705 | 0.020153 | 0.020151 | -4.6183 | 0.00042767 | 129 | -0.15158 | 0.0014223 | -0.15015 | -0.14515 | 2555.066 | Exfl | 2555.066 | 0.30417 | -244100.7294 | 8278.4137
2-A |  |  | No. of Flrs |  | 3 | Envel-Area per Flr (ft2) |  |  | 17280 | [10 empty] | 2-A |  | % Envel-Leakg |  | 0.35 | Leakg Flow Cf |  | 0.6 |  | Inside-Outside (PI-PO) |  |  | 0.005 | Envel Leakg A |  | 60.48 | Section Infltr (K-btu/yr) |  |  | 17527.3271
Level | Sctn | Bldg | Alt ref Sea-Lvl |  | Outdoor Std. Atm. Press. @ Altit |  |  |  | Wnd Vel | DB | WB | DP | W | RH | V | d | H | Tdb | Twb | Level | Bldg | Psychrometric Calculations for DP, RH, V, W, H, TR | [6 empty] | Floor | ∆PS | ∆PW | ∆P = | ∆P + | Leakg Q | Exfl - | Leakage | Q / | SHL | SHL/yr
ID No. | Flr No. | Flr No. | feet | meters | K-Pa | in.Hg | in.H2O | psi | mph | F | F | F | lbs/b | % | ft3/lb | lbs/ft3 | btu/lb | R | R | ID No. | Flr No. | PWSwb | WSwb | PWSdb | VPs | VPa | a | WSdb | Hght | in.H2O | in.H2O | ∆PW+∆PS | PI - PO | ft3/min | Infl + | ft3/min | Envel-A | btuh | K-btu
4 | 0 | XX | XX | XX | XX | XX | XX | XX | XX | [10 empty] | 4 | XX | XX | XX | XX | XX | XX | XX | XX | XX | XX | XX | XX | XX | XX | XX | XX | XX | XX | XX | bar: DB to Twb
3 | 2 | 4 | 576 | 175.5648 | 99.2338 | 29.3836 | 398.7774 | 14.3926 | 15.2903 | -16.2706 | -16.2706 | -19.9845 | 0.00043097 | 100 | 11.3911 | 0.087788 | -3.4508 | 443.4294 | 443.4294 | 3 | 4 | 0.0099657 | 0.00043097 | 0.0099657 | 0.020348 | 0.020346 | -4.6087 | 0.00043097 | 76 | -0.16677 | 0.0013874 | -0.16538 | -0.16038 | 2683.7352 | Exfl | 2683.7352 | 0.31949 | -255846.3931 | 8695.302
2 | 1 | 3 | 558 | 170.0784 | 99.2986 | 29.4028 | 399.0379 | 14.402 | 15.2215 | -16.2065 | -16.2065 | -19.9106 | 0.00043209 | 100 | 11.3853 | 0.087833 | -3.4342 | 443.4935 | 443.4935 | 2 | 3 | 0.0099982 | 0.00043209 | 0.0099982 | 0.020414 | 0.020412 | -4.6055 | 0.00043209 | 58 | -0.17192 | 0.0013757 | -0.17055 | -0.16555 | 2725.9337 | Exfl | 2725.9337 | 0.32452 | -259680.6155 | 8832.0251
1 |  |  | No. of Flrs |  | 2 | Envel-Area per Flr (ft2) |  |  | 22400 | [10 empty] | 1 |  | % Envel-Leakg |  | 0.4 | Leakg Flow Cf |  | 0.6 |  | Inside-Outside (PI-PO) |  |  | 0 | Envel Leakg A |  | 89.6 | Section Infltr (K-btu/yr) |  |  | 46356.2638
Level | Sctn | Bldg | Alt ref Sea-Lvl |  | Outdoor Std. Atm. Press. @ Altit |  |  |  | Wnd Vel | DB | WB | DP | W | RH | V | d | H | Tdb | Twb | Level | Bldg | Psychrometric Calculations for DP, RH, V, W, H, TR | [6 empty] | Floor | ∆PS | ∆PW | ∆P = | ∆P + | Leakg Q | Exfl - | Leakage | Q / | SHL | SHL/yr
ID No. | Flr No. | Flr No. | feet | meters | K-Pa | in.Hg | in.H2O | psi | mph | F | F | F | lbs/b | % | ft3/lb | lbs/ft3 | btu/lb | R | R | ID No. | Flr No. | PWSwb | WSwb | PWSdb | VPs | VPa | a | WSdb | Hght | in.H2O | in.H2O | ∆PW+∆PS | PI - PO | ft3/min | Infl + | ft3/min | Envel-A | btuh | K-btu
2 | 2 | 2 | 520 | 158.496 | 99.4355 | 29.4434 | 399.5882 | 14.4219 | 15.0764 | -16.0712 | -16.0712 | -19.7548 | 0.00043447 | 100 | 11.3731 | 0.087927 | -3.3992 | 443.6288 | 443.6288 | 2 | 2 | 0.010067 | 0.00043447 | 0.010067 | 0.020555 | 0.020553 | -4.5986 | 0.00043447 | 20 | -0.1828 | 0.001351 | -0.18145 | -0.18145 | 7099.114 | Exfl | 7099.114 | 0.84513 | -675245.6917 | 23001.1295
1 | 1 | 1 | 500 | 152.4 | 99.5077 | 29.4647 | 399.8781 | 14.4324 | 15 | -16 | -16 | -19.6727 | 0.00043573 | 100 | 11.3667 | 0.087976 | -3.3808 | 443.7 | 443.7 | 1 | 1 | 0.010104 | 0.00043573 | 0.010104 | 0.020629 | 0.020627 | -4.595 | 0.00043573 | 0 | -0.18852 | 0.0013381 | -0.18718 | -0.18718 | 7208.3748 | Exfl | 7208.3748 | 0.85814 | -685083.9396 | 23355.1343

## HRB-Apt-Pressurization Vnt-Exh
High-Rise - Apt-Condo Bldg with operable windows - Ventil-Exhaust - Pressure-Analysis | [26 empty] | Apt Unit Types - Studio, 1, 2, 3 bedrooms | [9 empty] | High-Rise - Apt-Condo Bldg with operable windows - Ventil-Exhaust - Pressure-Analysis | [30 empty] | Apt Unit Types - Studio, 1, 2, 3 bedrooms | [13 empty] | APARTMENT Building: Schedules / Profiles | [9 empty] | DOE2 - 0 to 1 (fraction) |  |  |  | TRACE - 0 to 100 (percent)
# units/flr & unit types vary per section & floor | [11 empty] | Space |  | SF |  |  | Space |  | SF |  |  | Apartment |  |  | cfm/SF |  |  | Diversity/Floor |  |  |  | Core-Exhst fan-cfm/Flr |  |  |  |  | Apt Ktchn & Bthrm Exhaust | [8 empty] | Apt Ktchn & Bthrm Exhaust | [9 empty] | CORE Exhaust & Supply Air | [12 empty] | CORE Exhaust & Supply Air
|  | 2 Bthr per 2-bdrm & 1-bdrm (1-Riser/Apt) | [8 empty] | sfK | Ktchn |  | 200 |  | sf1 | 1-Bdrm |  | 900 |  | oaA | Apt-Ventil |  |  | 0.05 |  | dvA | Apt-Ventil |  | 1 |  | exT | Trash Chute |  |  | 100 | Bldg-Sectn - 1 |  |  |  | Bldg-Sectn - 2 |  |  |  |  | Bldg-Sectn - 3 |  |  |  | Bldg-Sectn - 4 | [6 empty] | Bldg-Sectn - 1 | [5 empty] | Bldg-Sectn - 2 | [6 empty] | Bldg-Sectn - 3 | [5 empty] | Bldg-Sectn - 4 | [5 empty] | Hour No. (DOE2) | Hour No. (TRACE) | Hour From-To | People (Apt-PPL) | Lights (Apt-LGT) | Equipment (Apt-EQP) | Elevators (Apt-ELV) | Domestic Hot Water | Apt Ventil = People Schd | Apt Toilet Exhaust | Apt Kitchen Exhaust | Core General Exhaust | Trash Chute Exhaust | Core Storage Exhaust | Core Laundr Exhaust | System/AHU Operatg Sch | Smmr Inside DB Temp (F) | Heating Unit Operatg Sch | Wntr Inside DB Temp (F)
|  | 1 Bthr per Studio & 1-bdrm (1-Riser/Apt) | [8 empty] | sfB | Bthrm |  | 100 |  | sf2 | 2-Bdrm |  | 1300 |  | exK | Kitchn-Exh |  |  | 0.4 |  | dvK | Kitchn-Exh |  | 1 |  | exS | Storg/Lckrs |  |  | 500 | Flrs/Sectn |  |  | 25 | Flrs/Sectn |  |  | 40 |  | Flrs/Sectn |  |  | 10 | Flrs/Sectn |  |  |  | 3 |  |  | Flrs/Sectn |  |  |  | 25 |  | Flrs/Sectn |  |  |  | 40 |  |  | Flrs/Sectn |  |  |  | 10 |  | Flrs/Sectn |  |  |  | 3
(1) Water Source |  |  |  |  | 1 Ktch per Apt (1-Riser/Apt) | [5 empty] | sfS | Studio |  | 650 |  | sf3 | 3-Bdrm |  | 1600 |  | exB | Bthrm-Exh |  |  | 0.7 |  | dvB | Bthrm-Exh |  | 1 |  | exL | Laundry-Rm |  |  | 900 |  | Kitchen Exh | Bathrm Exh |  |  | Kitchen Exh | Bathrm Exh |  |  |  | Kitchen Exh | Bathrm Exh |  |  | Kitchen Exh |  | Bathrm Exh |  |  |  | Trash Chute | Storage Exh | Laundry Exh | Miscell Exh |  | Supply Air | Trash Chute | Storage Exh | Laundry Exh | Miscell Exh |  | Supply Air |  | Trash Chute | Storage Exh | Laundry Exh | Miscell Exh |  | Supply Air | Trash Chute | Storage Exh | Laundry Exh | Miscell Exh |  | Supply Air
Heat Pumps (WSHP) | [5 empty] | # Bldg-Sctns |  |  | 4 |  | Core-Pressurizition-Ratio (SA/EA) | [7 empty] | 1.5 |  | oaC | Core-Vent |  |  | 0.2 |  | dvC | Core-Exh |  | 1 |  | exM | Miscellan |  |  | 100
Stacked Vertically in Closets | [7 empty] | Ventilation from Corridor | [5 empty] | Windows closed (HVAC System on) when winter dry bulb temp < 65 degF and summer dew point temp > 55 degF
2-Pipe-Risers (WSHP & FCU) | [5 empty] | Plumbing-Pipe-Risers |  |  |  |  | supplied from under Door | [5 empty] | Row |  | Column |  |  | c1 |  | c2 |  | c3 |  | c4 | C O R E Areas |  | Services |  |  | CORE - EA Floor | [20 empty] | ROOF
[18 empty] | Flr-Sections |  |  |  | S1 |  | S2 |  | S3 |  | S4 |  |  | Corridors |  |  | TC | Trash-Chute | [48 empty] | Units | sf/P | W/sf | W/sf | W/Elev | gal/P | cfm/P | cfm/sf | cfm/sf | cfm/sf | cfm/sf | cfm/sf | cfm/sf | MAY - OCT |  | NOV - APR
| NW |  | B |  | N1 |  |  |  | N2 |  |  | B |  | NE |  |  | r1 | # of Studio Apts |  |  |  | 5 |  | 6 |  | 0 |  | 0 |  |  | Flr-Flr-Trvl |  |  | GE | Miscell-Exh | [19 empty] | Flr - N | [26 empty] | Design Basis >> |  |  | 500 | 1 | 0.25 |  |  | 40 | 2 | 2 | 1 | 1 | 1 | 1 | On/Off | Temp | Not | Temp
|  |  | K | OA | [6 empty] | OA | K |  |  |  |  | r2 | # of 1-Bdr Apts |  |  |  | 6 |  | 9 |  | 12 |  | 5 |  |  | Exh Shaft |  |  | LE | Laundr-Exh | [46 empty] | Design Value >> | [14 empty] | 0 / 100 | 75 | Used | 70
[5 empty] | K | B |  |  | B | K |  |  | OA |  |  |  | r3 | # of 2-Bdr Apts |  |  |  | 4 |  | 0 |  | 8 |  | 15 |  | OA | Outdr Air |  |  | EE | Electric-Exh | [46 empty] | 1 | 0 | 0 - 1 | 95 | 5 | 30 | 5 | 5 | 95 | 5 | 5 | 0 | 0 | 0 | 0 | 100 | 75 | 100 | 70
|  |  |  | OA - Corrid to Apts Under Door | [12 empty] | r4 | # of 3-Bdr Apts |  |  |  | 2 |  | 0 |  | 0 |  | 10 | [5 empty] | EA Apartments | [47 empty] | 2 | 1 | 1 - 2 | 95 | 5 | 30 | 5 | 5 | 95 | 5 | 5 | 0 | 0 | 0 | 0 | 100 | 75 | 100 | 70
| W2 |  | K |  | Lockers |  | TC | Washers |  |  |  | K |  | E1 |  |  | r5 | Core-A % of Flr |  |  |  | 15 |  | 15 |  | 15 |  | 15 | Calculations |  |  |  |  | B | Bathrm-Exh | [46 empty] | 3 | 2 | 2 - 3 | 95 | 5 | 30 | 5 | 5 | 95 | 5 | 5 | 0 | 0 | 0 | 0 | 100 | 75 | 100 | 70
|  |  | B | Corridor | Storage |  | GE | Laundry |  |  | Corridor | B |  |  |  |  | r6 | # of Kitch Risers |  |  |  | 17 |  | 15 |  | 20 |  | 30 | r6 = r1 + r2 + r3 + r4 |  |  |  |  | K | Kitchen-Exh | [16 empty] | Intermediate Floors | [29 empty] | 4 | 3 | 3 - 4 | 95 | 5 | 30 | 5 | 5 | 95 | 5 | 5 | 0 | 0 | 0 | 0 | 100 | 75 | 100 | 70
[5 empty] | Lockers |  | LE | Dryers | [8 empty] | r7 | # of Bthr Risers |  |  |  | 23 |  | 15 |  | 28 |  | 55 | r7 = r1 + r2 + 2*r3 + 2*r4 | [52 empty] | 5 | 4 | 4 - 5 | 95 | 5 | 30 | 5 | 5 | 95 | 5 | 5 | 0 | 0 | 0 | 0 | 100 | 75 | 100 | 70
[7 empty] | Corridor | [9 empty] | r8 | Tot-Apart-Area |  |  |  | 17050 |  | 12000 |  | 21200 |  | 40000 | r8 = r1*sfS + r2*sf1 +r3*sf2 + r4*sf3 | [52 empty] | 6 | 5 | 5 - 6 | 95 | 5 | 30 | 5 | 5 | 95 | 50 | 80 | 0 | 0 | 0 | 0 | 100 | 75 | 100 | 70
| W1 |  | B |  | ELEVATORS |  |  |  | STAIRS |  |  | B |  | E2 |  |  | r9 | Tot-Core-A SF |  |  |  | 3008.8235 |  | 2117.6471 |  | 3741.1765 |  | 7058.8235 | r9 = (r8*r5/100) / (1-r5/100) | [52 empty] | 7 | 6 | 6 - 7 | 95 | 25 | 50 | 20 | 30 | 95 | 50 | 80 | 0 | 0 | 0 | 0 | 100 | 75 | 100 | 70
|  |  | K |  | Util-Clo |  | EE | OA |  |  |  | K |  |  |  |  | r10 | Tot-Flr-Area SF |  |  |  | 20058.8235 |  | 14117.6471 |  | 24941.1765 |  | 47058.8235 | r10 = r8 + r9 | [5 empty] | Row-Col #s | [19 empty] | Flr - 3 | [26 empty] | 8 | 7 | 7 - 8 | 80 | 45 | 90 | 40 | 50 | 80 | 50 | 80 | 0 | 0 | 0 | 0 | 100 | 75 | 100 | 70
|  |  |  | OA - Corrid to Apts Under Door | [12 empty] | r11 | Apt Vnt < Corr |  |  |  | 1002.9412 |  | 705.8824 |  | 1247.0588 |  | 2352.9412 | r1 = r10 * oaA * dvA | [52 empty] | 9 | 8 | 8 - 9 | 80 | 45 | 30 | 50 | 40 | 80 | 5 | 5 | 0 | 0 | 0 | 0 | 100 | 75 | 100 | 70
[5 empty] | K | B |  |  | B | K | [6 empty] | r12 | Apt-Kitch-Exh |  |  |  | 1360 |  | 1200 |  | 1600 |  | 2400 | r12 = r6 * exK * dvK * sfK | [25 empty] | Flr - 2 | [26 empty] | 10 | 9 | 9 - 10 | 65 | 35 | 30 | 40 | 30 | 65 | 5 | 5 | 0 | 0 | 0 | 0 | 0 | 95 | 50 | 50
|  |  | K | [8 empty] | K |  |  |  |  | r13 | Apt-Bthrm-Exh |  |  |  | 1610 |  | 1050 |  | 1960 |  | 3850 | r13 = r7 * exB * dvB * sfB | [52 empty] | 11 | 10 | 10 - 11 | 65 | 35 | 30 | 40 | 30 | 65 | 5 | 5 | 0 | 0 | 0 | 0 | 0 | 95 | 50 | 50
| SW |  | B |  |  | S2 |  |  | S1 |  |  | B |  | SE |  |  | r14 | Apt Vnt+Exh |  |  |  | 3972.9412 |  | 2955.8824 |  | 4807.0588 |  | 8602.9412 | r14 = r11 + r12 + r13 | [5 empty] | User Input | [19 empty] | Flr - 1 | [26 empty] | 12 | 11 | 11 - 12 | 65 | 35 | 30 | 35 | 35 | 65 | 50 | 80 | 0 | 0 | 0 | 0 | 0 | 95 | 50 | 50
[17 empty] | r15 | Core-Supp-OA |  |  |  | 5959.4118 |  | 4433.8235 |  | 7210.5882 |  | 12904.4118 | r15 = r14 * SA/EA | [5 empty] | Calculated |  | Bldg-Sectn - 1 |  |  |  | Bldg-Sectn - 2 |  |  |  |  | Bldg-Sectn - 3 |  |  |  | Bldg-Sectn - 4 | [6 empty] | Bldg-Sectn - 1 | [5 empty] | Bldg-Sectn - 2 | [6 empty] | Bldg-Sectn - 3 | [5 empty] | Bldg-Sectn - 4 | [5 empty] | 13 | 12 | 12 - 13 | 65 | 25 | 50 | 35 | 40 | 65 | 50 | 80 | 0 | 0 | 0 | 0 | 0 | 95 | 50 | 50
Alternate HVAC System = (2) Window A-C Units + Electric Baseboard Heat | [16 empty] | r16 | Cor-OA-cfm/SF |  |  |  | 1.9806 |  | 2.0938 |  | 1.9274 |  | 1.8281 | r16 = r15 / r9 | [5 empty] | Aprtmnts |  | Ktch & Bthr Exh |  |  |  | Ktch & Bthr Exh |  |  |  |  | Ktch & Bthr Exh |  |  |  | Ktch & Bthr Exh | [6 empty] | Risers/Section [Exhsts = 1-Trash-Chute, 2-Storage, 3-Laundry, 4-Miscell] 5-Supply-OA | [24 empty] | 14 | 13 | 13 - 14 | 65 | 25 | 90 | 30 | 35 | 65 | 50 | 80 | 0 | 0 | 0 | 0 | 100 | 75 | 100 | 70
|  |  |  | Site Plan |  |  |  |  | or (3a) 2-Pipe (Elctr-Htg) or (3b) 4-Pipe (HW-Htg) Fan-Coil Units (FCU) or (4) Central HVAC System (heating & cooling) | [25 empty] | Ktch-Bthr |  | # Ktc Risers |  |  | 17 | # Ktc Risers |  |  | 15 |  | # Ktc Risers |  |  | 20 | # Ktc Risers |  |  |  | 30 |  |  | 1-Trash |  |  | 2500 |  |  | 1-Trash |  |  | 4000 |  |  |  | 1-Trash |  |  | 4000 |  |  | 1-Trash |  |  | 300 |  |  | 15 | 14 | 14 - 15 | 65 | 25 | 30 | 30 | 35 | 65 | 5 | 5 | 0 | 0 | 0 | 0 | 100 | 75 | 100 | 70
|  |  | N Street | [11 empty] | Bldg-Apt Complex |  |  |  |  | Row |  |  | Column |  |  | c1 |  | c2 | c3 |  | c4 | [5 empty] | Ktch Exh |  | 34000 |  | Ktch Exh |  | 48000 |  |  | Ktch Exh |  | 16000 |  | Ktch Exh |  |  | 7200 |  |  |  | Trash Fan-SP | [5 empty] | Trash Fan-SP | [6 empty] | Trash Fan-SP | [5 empty] | Trash Fan-SP | [5 empty] | 16 | 15 | 15 - 16 | 65 | 25 | 30 | 30 | 30 | 65 | 5 | 5 | 0 | 0 | 0 | 0 | 100 | 75 | 100 | 70
[16 empty] | Elevation |  |  |  |  | Sections |  |  | Divers |  | S1 |  | S2 | S3 |  | S4 | [5 empty] | Ktch Fan-SP |  |  |  | Ktch Fan-SP |  |  |  |  | Ktch Fan-SP |  |  |  | Ktch Fan-SP | [6 empty] | 2-Storage |  |  | 12500 |  |  | 2-Storage |  |  | 20000 |  |  |  | 2-Storage |  |  | 5000 |  |  | 2-Storage |  |  | 1500 |  |  | 17 | 16 | 16 - 17 | 80 | 25 | 30 | 40 | 30 | 80 | 5 | 5 | 0 | 0 | 0 | 0 | 0 | 95 | 50 | 50
| X Avenue | [6 empty] | Z Avenue | [11 empty] | r21 | Flrs/Sectn |  |  |  |  | 25 |  | 40 | 10 |  | 3 |  | Calculations |  |  |  | Bth Risers |  |  | 23 | Bth Risers |  |  | 15 |  | Bth Risers |  |  | 28 | Bth Risers |  |  |  | 55 |  |  | Storg Fan-SP | [5 empty] | Storg Fan-SP | [6 empty] | Storg Fan-SP | [5 empty] | Storg Fan-SP | [5 empty] | 18 | 17 | 17 - 18 | 80 | 35 | 50 | 45 | 50 | 80 | 50 | 80 | 0 | 0 | 0 | 0 | 0 | 95 | 50 | 50
|  |  |  | Court | [15 empty] | r22 | Sctn Flr SF |  |  |  |  | 501470.5882 |  | 564705.8824 | 249411.7647 |  | 141176.4706 |  | Flr-A = r21 * r10 |  |  |  | Bthr Exh |  | 40250 |  | Bthr Exh |  | 42000 |  |  | Bthr Exh |  | 19600 |  | Bthr Exh |  |  | 11550 |  |  |  | 3-Laundry |  |  | 22500 |  |  | 3-Laundry |  |  | 36000 |  |  |  | 3-Laundry |  |  | 9000 |  |  | 3-Laundry |  |  | 2700 |  |  | 19 | 18 | 18 - 19 | 85 | 70 | 90 | 50 | 50 | 85 | 50 | 80 | 0 | 0 | 0 | 0 | 100 | 75 | 100 | 70
|  |  |  | Yard | [15 empty] | r23 | Apt-Vent |  |  | 1 |  | 25073.5294 |  | 28235.2941 | 12470.5882 |  | 7058.8235 |  | Ap-V = r23 * r21 * r11 |  |  |  | Bthr Fan-SP |  |  |  | Bthr Fan-SP |  |  |  |  | Bthr Fan-SP |  |  |  | Bthr Fan-SP | [6 empty] | Lndry Fan-SP | [5 empty] | Lndry Fan-SP | [6 empty] | Lndry Fan-SP | [5 empty] | Lndry Fan-SP | [5 empty] | 20 | 19 | 19 - 20 | 85 | 70 | 30 | 40 | 40 | 85 | 50 | 80 | 0 | 0 | 0 | 0 | 100 | 75 | 100 | 70
[20 empty] | r24 | Kitchn Exh |  |  | 1 |  | 34000 |  | 48000 | 16000 |  | 7200 |  | Kt-Ex = r24 * r21 * r12 |  |  |  | Apt Vnt |  | 148985.2941 |  | Apt Vnt |  | 177352.9412 |  |  | Apt Vnt |  | 72105.8824 |  | Apt Vnt |  |  | 38713.2353 |  |  |  | 4-Miscell |  |  | 2500 |  |  | 4-Miscell |  |  | 4000 |  |  |  | 4-Miscell |  |  | 1000 |  |  | 4-Miscell |  |  | 300 |  |  | 21 | 20 | 20 - 21 | 85 | 70 | 30 | 35 | 35 | 85 | 5 | 5 | 0 | 0 | 0 | 0 | 100 | 75 | 100 | 70
[20 empty] | r25 | Bthrm Exh |  |  | 1 |  | 40250 |  | 42000 | 19600 |  | 11550 |  | Bt-Ex = r25 * r21 * r13 |  |  |  | Apt Exh |  | 74250 |  | Apt Exh |  | 90000 |  |  | Apt Exh |  | 35600 |  | Apt Exh |  |  | 18750 |  |  |  | Miscl Fan-SP | [5 empty] | Miscl Fan-SP | [6 empty] | Miscl Fan-SP | [5 empty] | Miscl Fan-SP | [5 empty] | 22 | 21 | 21 - 22 | 95 | 70 | 30 | 30 | 45 | 95 | 5 | 5 | 0 | 0 | 0 | 0 | 100 | 75 | 100 | 70
|  |  | N+1 Street | [7 empty] | Sctn-1 |  | Sctn-2 |  | Sctn-3 |  | Sctn-4 |  |  | r26 | Core-Exhst |  |  | 1 |  | 99323.5294 |  | 118235.2941 | 48070.5882 |  | 25808.8235 |  | Cr-Ex = r26 * r21 * r14 |  |  |  | Bldg (all sections) Ventil Air (cfm) | [7 empty] | 437157.3529 | [11 empty] | 5-OA |  | 148985.2941 |  |  |  | 5-OA |  | 177352.9412 |  |  |  |  | 5-OA |  | 72105.8824 |  |  |  | 5-OA |  | 38713.2353 |  |  |  | 23 | 22 | 22 - 23 | 95 | 60 | 30 | 10 | 30 | 95 | 5 | 5 | 0 | 0 | 0 | 0 | 100 | 75 | 100 | 70
[11 empty] | Lobby-Services-Offices-Garage | [8 empty] | r27 | Cor-Apt-OA |  |  | 1 |  | 148985.2941 |  | 177352.9412 | 72105.8824 |  | 38713.2353 |  | Ap-SA r27 * r21 * r15 |  |  |  | Bldg (all sections) Exhaust Air (cfm) | [7 empty] | 346400 |  |  | Core-Pressurization | [5 empty] | 1.262 |  |  | S-OA Fan-SP | [5 empty] | S-OA Fan-SP | [6 empty] | S-OA Fan-SP | [5 empty] | S-OA Fan-SP | [5 empty] | 24 | 23 | 23 - 24 | 95 | 5 | 30 | 5 | 5 | 95 | 5 | 5 | 0 | 0 | 0 | 0 | 100 | 75 | 100 | 70

## Bldg-Stck-Eff-Theory
Infltr & Exfltr due to Building Stack Effect, Wind Press | [15 empty] | Basis of Calculations | [7 empty] | Infltr & Exfltr due to Building Stack Effect, Wind Press | [8 empty] | Basis of Calculations
Definitions
ASHRAE def. of Tall Buildings = above 300 ft
CTBUH def. of Super-Tall Bldgs = above 300 meters = above 985 feet
NFPA def. of High Rise Bldg > than 7 stories (> 75 ft approx) fight fire from inside
Def. of Low Rise Bldg varies. Ex. Requires no elevators (up to 3 flrs, less than 35 ft)
Def. of Mid Rise Bldg = between Low Rise and High Rise (4 to 7 flrs, 35 ft to 75 ft)
| Flr to Flr Heights (ft): |  |  |  | Residential = |  |  |  | 10 |  | Office = |  |  | 13.5 |  | Retail = |  |  | 15 |  | Lobby = |  | 18
IP Units |  |  | Grnd Temp = TG F | [5 empty] | SI Units |  |  | Grnd Temp = TG C | [8 empty] | Std. Atm. Press.
| T = TG - 0.00356 * H | [8 empty] | T = TG - 0.00649 * H | [11 empty] | 101.325 | kPa
| D = 2.7 * PSIa / (T + 459.7) | [8 empty] | D = P / ( 0.2869 * ( T + 273.1 ) ) | [11 empty] | 29.92 | in.Hg | Building pressure variations are caused by climatic wind pressure and stack effect (air buoyancy) which results
| P (in.Hg) = .296 * P (K-Pa) | [8 empty] | P = 101325 (1 - 2.25577 10-5 H)5.25588 | [11 empty] | 14.696 | PSI | in an uncontrolled air flow into and out of a high rise building. The quantity of uncontrolled ventilation is
[8 empty] | P = air press. (Pa) |  |  |  |  | H = altitude above sea level (m) | [8 empty] | 407.1828 | in.H2O | influenced by indoor-outdoor temperature difference, wind velocity, wind direction, height of the building, and
Stack Efect Press Difference | [5 empty] | (ASHRAE Handbook of Fundamentals) | [10 empty] | Stack Efect Press Difference | [6 empty] | building construction. In cold climates air infiltrates into the lower half of the high rise building through doors,
| ∆PS = C1 * ρO * [ (TO - TI) / TI ] * g * (HNPL - H) | [20 empty] | (Wikipedia) |  | curtain walls, and other paths and rises to upper floors through shafts and other means due to natural stack
| ∆PS = |  | Difference (Indoor - Outdoor) Stack Press (in.wg) | [12 empty] | ∆PS = C * Atm.Pr. * H * (1/TO-1/TI) | [7 empty] | effect and ex-filtrates from the upper half of the building.
| C1 = |  | Conversion Factor = 0.00598 (in.wg . ft.sec2/lbm) | [8 empty] | 0.00598 | [7 empty] | Var. |  | IP | SI
| ρO = |  | Outdoor Air Density at Outdoor Air Temp, lbm/ft3 | [16 empty] | C |  | 0.0188 | 0.0342 | Wind creates a distribution of static pressure on the building envelope, which is dependent on wind direction
| g = |  | gravitational constant |  |  |  | ft/sec2 |  | 32.2 |  | m/sec2 |  | 9.81 | [6 empty] | ∆PS |  | PSI | Pa | and location on building envelope. The basic wind pressure theory is expressed as (Hong Kong Univ, 2001):
| TI = |  | Indr | (OR=460+OF) |  | (OK=273+OC) | [13 empty] | At.Pr. |  | PSI | Pa | [5 empty] | ρ = | air density, lbm/ft3 (about 0.075)
| TO = |  | Outdr | (OR=460+OF) |  | (OK=273+OC) | [13 empty] | H (ht) |  | Ft | m | [5 empty] | V = | wind speed, mph
| HNPL = |  | Neutral Pr. Plane above Ref Plane, ft (0.5*H appr) | [11 empty] | C2 * ρO* g = |  |  | 0.014057 |  | TO , TI |  | OR | OK | [5 empty] | I & o = |  | inside & outside
| H = |  | Building Height above Reference Plane, (ft) | [20 empty] | ∆PW = |  | wind pressure difference, in of water |  |  | C = | unit conversion, 0.0129
Wind Pressure |  |  |  | Pushes Outdoor Air on Windward side (+ve) - Pulls Indoor Air on Leeward side (-ve) | [19 empty] | CP = | surface (location on building envelope) pressure coefficient, dimensionless
| ∆PW = C2 * s2 * CP * ρO * (UH)2 / 2 | [17 empty] | feet to meters |  |  |  | 0.3048 | Note: Using the above equation, the wind pressure is 0.1 in. of water at 15 mph wind on windward surface
| ∆PW = |  | Wind Surface Pr. above Outdoor Air Press (in.wg) | [15 empty] | lbs/ft3 to kg/m3 |  |  |  | 16.0185 | [9 empty] | (0.4 in. of water at 30 mph)
| C2 = |  | Conv. Factor (in.wg * ft3/lbm * mph2) | [6 empty] | 0.0129 | [8 empty] | m3/hr to ft3/min |  |  |  | 0.58858
| CP = |  | Wind Surface Pr. Coeff ( = 0.5 to 0.8) | [6 empty] | 0.65 | [8 empty] | mph to Km/hr |  |  |  | 1.609 | Air density varies with temperature. In cold weather, low density air infiltrates the building, rises within the high rise
| s = |  | Shelter Factor (0.4 for example) | [5 empty] | 0.4 | [9 empty] | K-Pa to In.wg |  |  |  | 4.0161 | bldg’s vertical shafts as it warms & creates stack effect pressure. The basic stack effect theory is expressed as:
| ρO = |  | OA Density at OA Temp, lbm/ft2 | [15 empty] | K-Pa to In.Hg |  |  |  | 0.2953 | [7 empty] | ∆PS = |  | stack pressure, in of water
| UH = |  | Effective Wind Speed (mph) | [15 empty] | K-Pa to PSI |  |  |  | 0.14504 | [7 empty] | T = | temperature, oR
| (Indoor - Outdor) Press (in. H2O) | [5 empty] | 0.02 |  | to | 0.03 | [8 empty] | Sq.Ft to Sq.M |  |  |  | 0.092903 | [7 empty] | I & o = |  | inside & outside
Airflow (Leakge) thru Envelope | [7 empty] | Air Pressue and the Building Envelope by Rick Quirouette | [15 empty] | C2, ρ, g = |  |  | air density and gravity constant, 0.01444 |  |  |  | h = | height, feet
| Q = Cd * A * ( 2 * ∆P/d )0.5 |  |  |  |  | Cd = |  | 0.6 | [8 empty] | Convert |  | In.Hg |  |  | Convert | in.H2O | hneutral = |  |  | height of neutral pressure level
| or | ∆P = (d/2) * (Q / (Cd * A))2 | [14 empty] | K-Pa |  | 3.3864 |  |  | K-Pa | 0.24885 | Note: Using the above equation, the stack pressure is 1.1 in. of water for a 60 story building with -10oF
| ∆P = |  | PD across Opening, Pa | [13 empty] | In.H2O |  | 13.596 |  |  | In.Hg | 0.073684 | [11 empty] | outside temperature
| Q = |  | Airflow Rate, m3/s | [13 empty] | PSI |  | 0.49115 |  |  | PSI | 0.036092
| Cd = |  | Discharge Coeff. for Opening, dimensionless (0.6) | [13 empty] | Kgf/m2 |  | 0.034532 |  |  | Kgf/m2 | 25.375 | The resultant pressure difference will cause air flow based on the following expression for flow through an orifice:
| A = |  | cross-sectional area of opening, m2 | [13 empty] | mm.Hg |  | 25.4 |  |  | mm.Hg | 186.821 |  |  |  |  | Q = | air flow
| d = |  | density of air, kg/m3 | [24 empty] | ρ = | air density |  |  | Cf = |  | flow coefficient
[6 empty] | Std. Atmos. Press. = | [6 empty] | 14.696 |  | PSI |  | 29.92 |  | in.Hg |  | 407.1828 |  | in.H2O |  |  |  |  | ∆Ptotal = |  | total pressure difference across flow area
[6 empty] | Pressurized Bldg: Indoor Press. - Outdoor Press. = | [15 empty] | 0.035 | in.H2O

## Ref-Psychro-EQNs
| PSYCHROMETRICS |  |  | Temp t | C1 | -10214.165 | t (DB) | Dry Bulb Temperature (F) | 78
|  |  |  | < 32 F | C2 | -4.8932 | t" (WB) | Wet Bulb Temperature (F) | 63.5
Z-sl | Altitude (Sea-Level) ft |  | 0 |  | C3 | -0.0053766 | Z | Altitude | 0
P-sl | Std Atmos Press (in. Hg) |  | 29.92 |  | C4 | 1.9202e-07 | P (in.Hg) | Atmospheric Pressure (in. Hg) | 29.92 | 29.92 * ( 1 - 6.8753*10^-6 * Z )^5.2559
DB-sl | Dry Bulb T at Std.Atm.Pr. |  | 68 |  | C5 | 3.5576e-10 | VPs | Water Vapor Press. at Saturation | 0.97005 | pws * 2.041772658
Z | Site Alitude of Project (ft) |  | 1000 |  | C6 | -9.0345e-14 | P (psi) | Entering Pressure (psi) | 14.6539 | P (in.Hg) * 2.041772658
p | Atm. Pr. at Site Altit (in.Hg) |  | 28.8545 |  | C7 | 4.1635 | pw | Partial Press Water Vapor | 0.43686 | ( P_in.Hg * W ) / (0.62198 + W )
t (DB) | Dry Bulb Temperature (F) |  | 95 | Temp t | C8 | -10440.397 | T" | Absolute Temp (R) | 523.17 | t* + 459.67
t" (WB) | Wet Bulb Temperature (F) |  | 75 | > 32 F | C9 | -11.2946 | pws" | Satur Water Vap Pr. ( t > 32 ) | 0.29011 | LN(pws") = C8/T + C9 + C10*T +
P (psi) | Atmos Pressure (psi) |  | 14.6539 |  | C10 | -0.027022 |  |  |  | C11*T^2 + C12*T^3 + C13*LN(T)
VPs | Water Vapor Press. at Saturation |  | 1.6666 |  | C11 | 1.289e-05 | Ws" | Humidity Ratio ( t > 32 ) | 0.012562 | 0.62198 * ( pws" / (P_psi - pws" )
pw | Partial Press Water Vapor |  | 0.66421 |  | C12 | -2.4781e-09 | T | Absolute Temp (R) | 537.67 | t + 459.67
T" | Absolute WB Temp (R) |  | 534.67 |  | C13 | 6.546 | W | Humidity Ratio | 0.0092161 | ( ( 1093 - 0.556*t" ) * Ws" -
pws" | Satur Water Vap Pr. ( t > 32 ) |  | 0.43007 | Temp t | C14 | 100.45 |  |  |  | 0.24 * (t - t") / ( 1093 + 0.444 * t - t")
Ws" | Humidity Ratio ( t > 32 ) |  | 0.018806 | > 32 F | C15 | 33.193 | pws | Satur Water Vap Pr. ( t > 32 ) | 0.4751 | LN(pws_db) = C8/T + C9 + C10*T +
T | Absolute DB Temp (R) |  | 554.67 |  | C16 | 2.319 |  |  |  | C11*T^2 + C12*T^3 + C13*LN(T)
W | Humidity Ratio |  | 0.014121 |  | C17 | 0.17074 | Ws | Humidity Ratio ( t > 32 ) | 0.020841 | 0.62198 * ( Ws / ( P_psi - Ws) )
pws | Satur Water Vap Pr. ( t > 32 ) |  | 0.81625 |  | C18 | 1.2063 | m | Mole Fraction Water Vapor | 0.44221 | W/Ws
Ws | Humidity Ratio ( t > 32 ) |  | 0.036689 | Temp t | C19 | 90.12 | f | Degree of Saturation | 0.45035 | m / (1- (1-m) * ( pws / P_psi ) )
m | Mole Fraction Water Vapor |  | 0.38489 | < 32 F | C20 | 26.142 | a |  | -1.542 | LN ( pw * 0.4897705)
f (DS) | Degree of Saturation |  | 0.39855 |  | C21 | 0.8927 |  | Relative Humidity ( % ) | 45.035 | 100 * f
a |  | a | -1.123 |  |  |  | td (DP) | Dew Point Temperature ( t > 32 ) | 54.1673 | td = C14 + C15*a + C16*a^2 +
u (RH) | Relative Humidity ( % ) |  | 39.8547 | Z | Altitude (Z) |  |  |  |  | C17*a^3 + C18*pw^0.1984
td (DP) | Dew Point Temp ( t > 32 F ) |  | 65.8994 | p | Atmos. Press. (in. Hg) at Alt Z |  | W | Humidity Ratio (lbs/lb) | 0.0092161 | ( ( 1093 - 0.556*t" ) * Ws" -
W | Humidity Ratio (lbs/lb) |  | 0.014121 |  | Atmos. Press. (psi) at Alt Z |  |  |  |  | 0.24 * (t - t") / ( 1093 + 0.444 * t - t")
| Humidity Ratio (grains/lb) |  | 98.8485 |  | Dry Bulb Temp (F) at Alt Z |  |  | Humidity Ratio (grains/lb) | 64.5125 | 7000 * W
H | Enthalpy (btu/lb) |  | 38.3782 | W | Humidity Ratio at DB/WB lbs/lb |  | H | Enthalpy | 28.8174 | 0.24*t + W * (1061 + 0.444*t)
V | Specific Volume (ft3/lb) |  | 14.301 |  | Vapor Pressure at DB/WB |  | V | Specific Volume | 13.7558 | 0.7543 * ( T * (1 + 1.6078*W ) ) / P
|  |  |  | m | Mole Fraction of Water Vapor |  | t (DB) | Dry Bulb (DB) Temp (F)
Pws | Satur. Water Vap Press ( > 32 F) |  |  |  | Relative Humidity (%) |  | td (DP) | Dew Point Temp ( t > 32 F )
Ws | Humidity Ratio (lbs/lb) ( > 32 F ) | [6 empty] | Enthalpy
t* (WB) | Dry Bulb (DB) Temp (F) | [6 empty] | Specific Volume
Pws* | Satur. Water Vap Press ( > 32 F)
Ws* | Humidity Ratio (lbs/lb) ( > 32 F )