## Input-Output
[5 empty] | Length (L) | [10 empty] | Perimeter Length | [11 empty] | 2.5 | ROOF | [5 empty] | 2.5 | 2 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 3 | 6 | 6 | 6.5 | 7 | 6.5 | 5 | 1 | 6 | 6 | 6.5 | 7 | 6.5 | 6.5 | 5.5 | 5.5 | 5.5 | 7 | 7 | 8 | 8 | 7 | 2 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 2 | 2 | 5.5 | 5.5 | 6 | 7 | 6 | 6.5 | 5.5 | 5.5 | 5.5 | 7 | 7 | 8 | 8 | 7 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5
| Width (W) |  |  | Perimeter Zone (PZ) | [28 empty] | MECHANICAL |  |  |  | Building Pressurization - |  |  | P = 2 * pi * SQRT( W*L / pi) |  |  | 3.1416 | USER INPUT |  | CALCULATED |  |  | Calc | Sctn | Bldg | Flr-H + Sea-Lvl |  | Floor |  | Calc | Sctn | Bldg | Flr-H + Sea-Lvl |  | Outdr-Air from Sheet 'SMMR-Calcs' | [5 empty] | SUMMER |  | Coolg |  | Bldg | Summer - Infiltr-Exfiltr - Q cfm - Design-Day | [6 empty] | Bldg |  |  | Calc | Sctn | Bldg | Flr-H + Sea-Lvl |  | Outdr-Air from Sheet 'WNTR-Calcs' | [5 empty] | WINTER |  | Coolg |  | Bldg | Winter - Infiltr-Exfiltr - Q cfm - Design-Day | [6 empty] | Bldg
[23 empty] | b | [7 empty] | S-8 |  |  | Restaurant |  |  | Stack Effect & Wind Press Infltration | [11 empty] | ID # | Flr # | Flr-# | ft | m | Data |  | ID # | Flr # | Flr-# | ft | m | [8 empty] | Load / |  | Flr-# | Infiltration |  |  |  | Exfiltration |  |  | Flr-# |  |  | ID # | Flr # | Flr-# | ft | m | [8 empty] | Load / |  | Flr-# | Infiltration |  |  |  | Exfiltration |  |  | Flr-#
|  |  |  | Interior Zone (IZ) | [33 empty] | PROJECT Data | Description | [5 empty] | DESIGN Data | SMMR | WNTR | [21 empty] | Year | [25 empty] | Year
[6 empty] | Core | [31 empty] | Project Name | Tall Mixed-Use Building (Description) | [5 empty] | Wnd (mph) Grnd | 5 | 10 |  | Section >> |  | 8-din | # flrs >> | 3 | 2 |  | Section >> |  | 8-din | # flrs >> | 3 | in.Hg | Wnd-V | Tdb | Twb | Enth | Dens | Q cfm | Q/ EnA | Tons |  | 1 | [7 empty] | 1 |  |  | Section >> |  | 8-din | # flrs >> | 3 | in.Hg | Wnd-V | Tdb | Twb | Enth | Dens | Q cfm | Q/ EnA | Tons |  | 1 | [7 empty] | 1
[6 empty] | Zone | [31 empty] | Project Analyst | VCT (Description) | [5 empty] | Wnd (mph) Roof | 15 | 25 |  | 61 | 0 | XX | XX | XX | 0 |  | 61 | 0 | XX | XX | XX | XX | XX | XX | XX | XX | XX | 0 | XX | 0 |  | 2 | [7 empty] | 2 |  |  | 61 | 0 | XX | XX | XX | XX | XX | XX | XX | XX | XX | 0 | XX | 0 |  | 2 | [7 empty] | 2
[38 empty] | Building Type | Mixed Use High Rise (Description) | [5 empty] | Wnd Dir (0-360) | 180 | 315 |  | 60 | 2 | 101 | 1789 | 545.2872 | 1 |  | 60 | 2 | 101 | 1789 | 545.2872 | 28.1134 | 14.8472 | 90.4112 | 71.9837 | 36.8657 | 0.066284 | 850.5892 | 0.11923 | 2461.9453 |  | 1-Grd | [7 empty] | 1-Grd |  |  | 60 | 2 | 101 | 1789 | 545.2872 | 28.1134 | 24.7708 | -24.5888 | -23.0163 | -5.2088 | 0.085567 | -4035.9389 | -0.56573 | -34787.6949 |  | 1-Grd | [7 empty] | 1-Grd
[31 empty] | S-7 |  |  | Apartments |  |  |  | Location | Minneapolis, MN, USA (Description) | [5 empty] | Outdoor DB (F) | 95 | -20 |  | 59 | 1 | 100 | 1774 | 540.7152 | 1 |  | 59 | 1 | 100 | 1774 | 540.7152 | 28.1288 | 14.7326 | 90.4646 | 72.0188 | 36.8871 | 0.066313 | 824.0355 | 0.11551 | 2385.0884 |  | 3 | [7 empty] | 3 |  |  | 59 | 1 | 100 | 1774 | 540.7152 | 28.1288 | 24.5989 | -24.5354 | -22.9812 | -5.1997 | 0.085604 | -3990.6408 | -0.55938 | -34397.2488 |  | 3 | [7 empty] | 3
[39 empty] | Site Altit (ft) ref Sea Level | 500 |  | Mechan Flr-Flr-H | 20 |  | Outdoor WB (F) | 75 | -20 |  | Section >> |  | 7-Apt | # flrs >> | 19 | 11 |  | Section >> |  | 7-Apt | # flrs >> | 19 | in.Hg | Wnd-V | Tdb | Twb | Enth | Dens | Q cfm | Q/ EnA | Tons |  | 4 | [7 empty] | 4 |  |  | Section >> |  | 7-Apt | # flrs >> | 19 | in.Hg | Wnd-V | Tdb | Twb | Enth | Dens | Q cfm | Q/ EnA | Tons |  | 4 | [7 empty] | 4
[20 empty] | a | [18 empty] | Leakage Air Flow Coeff. Cd | 0.65 |  | Core Area (%) | 10 |  | Degree-Days | 2680 | 7981 |  | 58 | 0 | XX | XX | XX | 0 |  | 58 | 0 | XX | XX | XX | XX | XX | XX | XX | XX | XX | 0 | XX | 0 |  | 5 | [7 empty] | 5 |  |  | 58 | 0 | XX | XX | XX | XX | XX | XX | XX | XX | XX | 0 | XX | 0 |  | 5 | [7 empty] | 5
| Rectangle | [6 empty] | Circle | [30 empty] | Avg Envelope Leakage (%) | 0.6 |  | Perim-Zone-D | 15 |  | Indoor DB (F) | 75 | 72 |  | 57 | 19 | 102 | 1779 | 542.2392 | 1 |  | 57 | 19 | 102 | 1779 | 542.2392 | 28.1237 | 14.7708 | 90.4468 | 72.0071 | 36.88 | 0.066303 | 1061.637 | 0.22322 | 3439.704 |  | 2-Rtl | [7 empty] | 2-Rtl |  |  | 57 | 19 | 102 | 1779 | 542.2392 | 28.1237 | 24.6562 | -24.5532 | -22.9929 | -5.2027 | 0.085592 | -3856.3273 | -0.81084 | -12494.5005 |  | 2-Rtl | [7 empty] | 2-Rtl
| Area : A = L * W | [6 empty] | Area : A = PI *R^2 | [5 empty] | Oval | [24 empty] | Avg Envl Leakg Area (ft2/ft2) | 0.01 |  | Column Dist (ft) | 31 |  | Indoor WB (F) | 62 | 55 |  | 56 | 17 | 100 | 1759 | 536.1432 | 1 |  | 56 | 17 | 100 | 1759 | 536.1432 | 28.1443 | 14.618 | 90.518 | 72.0539 | 36.9085 | 0.066342 | 1034.4563 | 0.21751 | 3351.6385 |  | 7 | [7 empty] | 7 |  |  | 56 | 17 | 100 | 1759 | 536.1432 | 28.1443 | 24.427 | -24.482 | -22.9461 | -5.1906 | 0.085641 | -3796.2681 | -0.79821 | -12299.9087 |  | 7 | [7 empty] | 7
| Perimeter : P = 2 * (L+W) | [6 empty] | Perimeter: P = 2 * PI * R | [5 empty] | Area (approx) : A = PI * a * b | [34 empty] | 55 | 15 | 98 | 1739 | 530.0472 | 1 |  | 55 | 15 | 98 | 1739 | 530.0472 | 28.1649 | 14.4652 | 90.5892 | 72.1007 | 36.937 | 0.066381 | 1006.2158 | 0.21157 | 3260.1393 |  | 8 | [7 empty] | 8 |  |  | 55 | 15 | 98 | 1739 | 530.0472 | 28.1649 | 24.1979 | -24.4108 | -22.8993 | -5.1784 | 0.085691 | -3735.3345 | -0.7854 | -12102.4836 |  | 8 | [7 empty] | 8
[14 empty] | Perimeter : P = 2*PI * { (a2+b2) / 2 }0.5 | [24 empty] | SCTN (max=5 chars) >> | 1-Grd | 2-Rtl | 3-Fin | 4-Ofc | 5-Srv | 6-Htl | 7-Apt | 8-din |  | 54 | 13 | 96 | 1719 | 523.9512 | 1 |  | 54 | 13 | 96 | 1719 | 523.9512 | 28.1855 | 14.3125 | 90.6604 | 72.1475 | 36.9655 | 0.06642 | 976.8236 | 0.20539 | 3164.9085 |  | 9 | [7 empty] | 9 |  |  | 54 | 13 | 96 | 1719 | 523.9512 | 28.1855 | 23.9687 | -24.3396 | -22.8525 | -5.1663 | 0.08574 | -3673.4828 | -0.77239 | -11902.0844 |  | 9 | [7 empty] | 9
[39 empty] | Floor Type | Lobby | Retail | Tradg | Office | Htl-Srvc | Hotel | Condos | Dining |  | 53 | 11 | 94 | 1699 | 517.8552 | 1 |  | 53 | 11 | 94 | 1699 | 517.8552 | 28.2061 | 14.1597 | 90.7316 | 72.1943 | 36.994 | 0.066459 | 946.1723 | 0.19894 | 3065.5984 |  | 10 | [7 empty] | 10 |  |  | 53 | 11 | 94 | 1699 | 517.8552 | 28.2061 | 23.7395 | -24.2684 | -22.8057 | -5.1542 | 0.085789 | -3610.6661 | -0.75918 | -11698.5581 |  | 10 | [7 empty] | 10
|  | Column Width |  |  |  |  | Floor Depth | [13 empty] | Panel Width | [17 empty] | Typical Floor Length (ft) | 320 | 280 | 240 | 220 | 200 | 180 | 180 | 180 |  | 52 | 9 | 92 | 1679 | 511.7592 | 1 |  | 52 | 9 | 92 | 1679 | 511.7592 | 28.2267 | 14.0069 | 90.8028 | 72.2411 | 37.0226 | 0.066498 | 914.1354 | 0.19221 | 2961.7987 |  | 11 | [7 empty] | 11 |  |  | 52 | 9 | 92 | 1679 | 511.7592 | 28.2267 | 23.5103 | -24.1972 | -22.7589 | -5.1421 | 0.085839 | -3546.8329 | -0.74576 | -11491.7386 |  | 11 | [7 empty] | 11
[39 empty] | Typical Floor Width (ft) | 240 | 200 | 160 | 140 | 120 | 100 | 100 | 100 |  | 51 | 7 | 90 | 1659 | 505.6632 | 1 |  | 51 | 7 | 90 | 1659 | 505.6632 | 28.2474 | 13.8541 | 90.874 | 72.2879 | 37.0511 | 0.066537 | 880.5615 | 0.18515 | 2853.0194 |  | 12 | [7 empty] | 12 |  |  | 51 | 7 | 90 | 1659 | 505.6632 | 28.2474 | 23.2811 | -24.126 | -22.7121 | -5.1299 | 0.085888 | -3481.9274 | -0.73211 | -11281.4447 |  | 12 | [7 empty] | 12
[34 empty] | Hotel |  |  |  |  | OR Non-Rectg Floor-A (ft2) | 76800 | 56000 |  |  |  | 18000 | 18000 | 18000 |  | 50 | 5 | 88 | 1639 | 499.5672 | 1 |  | 50 | 5 | 88 | 1639 | 499.5672 | 28.268 | 13.7013 | 90.9452 | 72.3347 | 37.0797 | 0.066576 | 845.2676 | 0.17773 | 2738.6671 |  | 12 | [7 empty] | 12 |  |  | 50 | 5 | 88 | 1639 | 499.5672 | 28.268 | 23.0519 | -24.0548 | -22.6653 | -5.1178 | 0.085938 | -3415.8884 | -0.71823 | -11067.4785 |  | 12 | [7 empty] | 12
[24 empty] | Prefabricated (manuf.) | [14 empty] | OR Non-Rectg Flr Perm (ft) | 982.3936 | 838.8783 |  |  |  | 475.5993 | 475.5993 | 475.5993 |  | 49 | 3 | 86 | 1619 | 493.4712 | 1 |  | 49 | 3 | 86 | 1619 | 493.4712 | 28.2887 | 13.5485 | 91.0164 | 72.3815 | 37.1083 | 0.066615 | 808.0283 | 0.1699 | 2618.0119 |  | 3-Fin | [7 empty] | 3-Fin |  |  | 49 | 3 | 86 | 1619 | 493.4712 | 28.2887 | 22.8228 | -23.9836 | -22.6185 | -5.1057 | 0.085987 | -3348.649 | -0.70409 | -10849.6227 |  | 3-Fin | [7 empty] | 3-Fin
[13 empty] | Flr-Flr-H |  |  |  | Flr-Celg-H | [6 empty] | Curtain Wall Panel | [14 empty] | Floor-Floor Height (ft) | 20 | 18 | 15 | 13.5 | 15 | 10 | 10 | 15 |  | 48 | 2 | 85 | 1609 | 490.4232 | 1 |  | 48 | 2 | 85 | 1609 | 490.4232 | 28.299 | 13.4721 | 91.052 | 72.4049 | 37.1225 | 0.066634 | 788.5936 | 0.16581 | 2555.0434 |  | 13 | [7 empty] | 13 |  |  | 48 | 2 | 85 | 1609 | 490.4232 | 28.299 | 22.7082 | -23.948 | -22.5951 | -5.0996 | 0.086012 | -3314.5563 | -0.69692 | -10739.1623 |  | 13 | [7 empty] | 13
[29 empty] | S-6 |  |  | MECHANICAL Flr | [6 empty] | Floor-Ceiling Height (ft) | 15 | 14 | 13 | 10 | 11 | 9.5 | 9.5 | 11 |  | 47 | 1 | 84 | 1599 | 487.3752 | 1 |  | 47 | 1 | 84 | 1599 | 487.3752 | 28.3094 | 13.3957 | 91.0876 | 72.4283 | 37.1368 | 0.066654 | 768.5609 | 0.1616 | 2490.1375 |  | 15 | [7 empty] | 15 |  |  | 47 | 1 | 84 | 1599 | 487.3752 | 28.3094 | 22.5936 | -23.9124 | -22.5717 | -5.0936 | 0.086036 | -3280.1352 | -0.68968 | -10627.638 |  | 15 | [7 empty] | 15
[39 empty] | Number of Section Floors | 2 | 3 | 6 | 40 | 5 | 25 | 15 | 2 |  | Section >> |  | 6-Htl | # flrs >> | 25 | 13 |  | Section >> |  | 6-Htl | # flrs >> | 25 | in.Hg | Wnd-V | Tdb | Twb | Enth | Dens | Q cfm | Q/ EnA | Tons |  | 17 | [7 empty] | 17 |  |  | Section >> |  | 6-Htl | # flrs >> | 25 | in.Hg | Wnd-V | Tdb | Twb | Enth | Dens | Q cfm | Q/ EnA | Tons |  | 17 | [7 empty] | 17
|  |  |  | Distance between Columns (Bay) | [6 empty] | Elevation View of Envelope | [27 empty] | Mech Floor in Section (Y/N) | N | Y | N | Y | N | N | Y | Y |  | 46 | 25 | 83 | 1589 | 484.3272 | 1 |  | 46 | 25 | 83 | 1589 | 484.3272 | 28.3197 | 13.3193 | 91.1232 | 72.4517 | 37.1511 | 0.066673 | 669.1578 | 0.1407 | 2168.0713 |  | 19 | [7 empty] | 19 |  |  | 46 | 25 | 83 | 1589 | 484.3272 | 28.3197 | 22.479 | -23.8768 | -22.5483 | -5.0875 | 0.086061 | -2903.7568 | -0.61055 | -9408.1721 |  | 19 | [7 empty] | 19
[19 empty] | Q = Cd * A * ( 2 * ∆P/d ) ^ 0.5 | [19 empty] | No. of Windows per Bay | 5 | 6 | 7 | 7 | 3 | 6 | 6 | 5 |  | 46 | 24 | 82 | 1579 | 481.2792 | 1 |  | 46 | 24 | 82 | 1579 | 481.2792 | 28.3301 | 13.2429 | 91.1588 | 72.4751 | 37.1654 | 0.066693 | 650.0284 | 0.13668 | 2106.0922 |  | 22 | [7 empty] | 22 |  |  | 46 | 24 | 82 | 1579 | 481.2792 | 28.3301 | 22.3644 | -23.8412 | -22.5249 | -5.0814 | 0.086086 | -2872.3428 | -0.60394 | -9306.3907 |  | 22 | [7 empty] | 22
[39 empty] | Window Unit Width (ft) | 5.5 | 4.5 | 4 | 4 | 9 | 5 | 5 | 5.5 |  | 45 | 23 | 81 | 1569 | 478.2312 | 1 |  | 45 | 23 | 81 | 1569 | 478.2312 | 28.3404 | 13.1665 | 91.1944 | 72.4985 | 37.1797 | 0.066712 | 630.2146 | 0.13251 | 2041.8953 |  | 25 | [7 empty] | 25 |  |  | 45 | 23 | 81 | 1569 | 478.2312 | 28.3404 | 22.2498 | -23.8056 | -22.5015 | -5.0754 | 0.086111 | -2840.6054 | -0.59727 | -9203.5614 |  | 25 | [7 empty] | 25
Appendix C: Commercial & Institutional Building Airtightness Data | [18 empty] | A = Q / ( Cd * ( 2 * ∆P/d ) ^ 0.5 ) | [19 empty] | Window Unit Height (ft) | 11 | 10 | 8 | 8 | 10 | 7 | 7 | 8 |  | 44 | 21 | 79 | 1549 | 472.1352 | 1 |  | 44 | 21 | 79 | 1549 | 472.1352 | 28.3611 | 13.0138 | 91.2656 | 72.5453 | 37.2084 | 0.066751 | 588.2545 | 0.12369 | 1905.9444 |  | 28 | [7 empty] | 28 |  |  | 44 | 21 | 79 | 1549 | 472.1352 | 28.3611 | 22.0206 | -23.7344 | -22.4547 | -5.0632 | 0.08616 | -2776.1158 | -0.58371 | -8994.6153 |  | 28 | [7 empty] | 28
National Institute of Standards & Technology - CONTAM Library - | [38 empty] | OR Window Area (%) | 60 | 50 | 65 | 65 | 60 | 45 | 45 | 60 |  | 43 | 20 | 78 | 1539 | 469.0872 | 1 |  | 43 | 20 | 78 | 1539 | 469.0872 | 28.3715 | 12.9374 | 91.3012 | 72.5687 | 37.2227 | 0.066771 | 565.9352 | 0.11899 | 1833.6302 |  | 31 | [7 empty] | 31 |  |  | 43 | 20 | 78 | 1539 | 469.0872 | 28.3715 | 21.906 | -23.6988 | -22.4313 | -5.0572 | 0.086185 | -2743.3399 | -0.57682 | -8888.4212 |  | 31 | [7 empty] | 31
0.0001 |  |  | 0.035 |  |  | Pi-Po = PD |  |  | 0.0741 | OA Air Dens |  |  |  |  | 0.65 |  |  | Cd | [20 empty] | OR Lkg-A % Envl (0.01-0.15) | 0.95 | 0.75 |  |  |  | 0.85 | 0.95 | 0.65 |  | 42 | 18 | 76 | 1519 | 462.9912 | 1 |  | 42 | 18 | 76 | 1519 | 462.9912 | 28.3922 | 12.7846 | 91.3724 | 72.6155 | 37.2513 | 0.06681 | 518.0419 | 0.10892 | 1678.4558 |  | 34 | [7 empty] | 34 |  |  | 42 | 18 | 76 | 1519 | 462.9912 | 28.3922 | 21.6769 | -23.6276 | -22.3845 | -5.0451 | 0.086234 | -2676.6605 | -0.5628 | -8672.3799 |  | 34 | [7 empty] | 34
Element ID |  |  |  |  | Description |  |  |  |  | Mean |  | Max |  | Mean |  |  | Max |  | A = Infltr cfm / ft2 Envel Area | [19 empty] | Wall Leakage Area (ft2 / ft2) | 0.00199 | 0.00199 | 0.00199 | 0.00199 | 0.00199 | 0.00199 | 0.00199 | 0.00199 |  | 41 | 16 | 74 | 1499 | 456.8952 | 1 |  | 41 | 16 | 74 | 1499 | 456.8952 | 28.413 | 12.6318 | 91.4436 | 72.6623 | 37.28 | 0.066849 | 464.6792 | 0.097704 | 1505.5605 |  | 37 | [7 empty] | 37 |  |  | 41 | 16 | 74 | 1499 | 456.8952 | 28.413 | 21.4477 | -23.5564 | -22.3377 | -5.0329 | 0.086284 | -2608.3815 | -0.54844 | -8451.156 |  | 37 | [7 empty] | 37
Exterior Wall (EW) | [8 empty] | Leakg ( cm2 / m2 ) |  |  |  |  | Leakg ( ft2 / ft2 ) |  |  |  |  | B = ft2 / ft2 Leakage Area | [19 empty] | Wndw Leakg Area (ft2 / ft2) | 0.00065 | 0.00025 | 0.00017 | 0.00017 | 0.00035 | 0.00035 | 0.00035 | 0.00025 |  | 40 | 13 | 71 | 1469 | 447.7512 | 1 |  | 40 | 13 | 71 | 1469 | 447.7512 | 28.4441 | 12.4026 | 91.5504 | 72.7325 | 37.3229 | 0.066908 | 369.1619 | 0.07762 | 1196.0845 |  | 36 | [7 empty] | 36 |  |  | 40 | 13 | 71 | 1469 | 447.7512 | 28.4441 | 21.1039 | -23.4496 | -22.2675 | -5.0147 | 0.086358 | -2502.6765 | -0.52622 | -8108.6718 |  | 36 | [7 empty] | 36
WLEXMA |  |  |  |  | EW, masonry |  |  |  |  | 4.2 |  | 11.4 |  | 0.00042 |  |  | 0.00114 |  | A |  |  | B | [16 empty] | Envel Leakage Flow Coeff | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 |  | 39 | 10 | 68 | 1439 | 438.6072 | 1 |  | 39 | 10 | 68 | 1439 | 438.6072 | 28.4753 | 12.1734 | 91.6572 | 72.8027 | 37.366 | 0.066967 | 235.4827 | 0.049513 | 762.9638 |  | 38 | [7 empty] | 38 |  |  | 39 | 10 | 68 | 1439 | 438.6072 | 28.4753 | 20.7601 | -23.3428 | -22.1973 | -4.9965 | 0.086433 | -2392.5617 | -0.50306 | -7751.8998 |  | 38 | [7 empty] | 38
WLEXCP |  |  |  |  | EW, concrete panel |  |  |  |  | 4 |  | 10 |  | 0.0004 |  |  | 0.001 |  | cfm/ft2 |  |  | ft2/ft2 | [16 empty] | Indr-Outdr PD (in.wg) PI - PO | 0.005 | 0.015 | 0.025 | 0.025 | 0.02 | 0.01 | 0.01 | 0.015 |  | 38 | 7 | 65 | 1409 | 429.4632 | 1 |  | 38 | 7 | 65 | 1409 | 429.4632 | 28.5064 | 11.9442 | 91.764 | 72.8729 | 37.409 | 0.067025 | -162.9679 | -0.034266 | -528.016 |  | 40 | [7 empty] | 40 |  |  | 38 | 7 | 65 | 1409 | 429.4632 | 28.5064 | 20.4163 | -23.236 | -22.1271 | -4.9783 | 0.086507 | -2277.3975 | -0.47885 | -7378.7678 |  | 40 | [7 empty] | 40
WLEXFRMA |  |  |  |  | EW, frame/masonry |  |  |  |  | 9.1 |  | 19.9 |  | 0.00091 |  |  | 0.00199 |  | 0 |  |  | 0 | [9 empty] | Offices | [6 empty] | Occup / Floor Area (P / ft2) | 50 | 30 | 100 | 150 | 150 | 250 | 250 | 75 |  | 37 | 5 | 63 | 1389 | 423.3672 | 1 |  | 37 | 5 | 63 | 1389 | 423.3672 | 28.5273 | 11.7914 | 91.8352 | 72.9197 | 37.4377 | 0.067064 | -286.1626 | -0.060169 | -927.167 |  | 43 | [7 empty] | 43 |  |  | 37 | 5 | 63 | 1389 | 423.3672 | 28.5273 | 20.1872 | -23.1648 | -22.0803 | -4.9662 | 0.086557 | -2197.4255 | -0.46203 | -7119.6587 |  | 43 | [7 empty] | 43
WLEXFR |  |  |  |  | EW, frame |  |  |  |  | 8.6 |  | 15.6 |  | 0.00086 |  |  | 0.00156 |  | 0.005 |  |  | 0.029074 | [16 empty] | Outdr Air / Person (cfm / P) | 15 | 10 | 20 | 20 | 15 | 30 | 30 | 25 |  | 36 | 3 | 61 | 1369 | 417.2712 | 1 |  | 36 | 3 | 61 | 1369 | 417.2712 | 28.5481 | 11.6387 | 91.9064 | 72.9665 | 37.4664 | 0.067104 | -371.1401 | -0.078036 | -1202.494 |  | 47 | [7 empty] | 47 |  |  | 36 | 3 | 61 | 1369 | 417.2712 | 28.5481 | 19.958 | -23.0936 | -22.0335 | -4.9541 | 0.086607 | -2114.5599 | -0.44461 | -6851.1742 |  | 47 | [7 empty] | 47
WLEXMN |  |  |  |  | EW, manufactured |  |  |  |  | 4.3 |  | 8.7 |  | 0.00043 |  |  | 0.00087 |  | 0.01 |  |  | 0.058148 | [16 empty] | Exhaust (cfm/ft2 Core-Zn) | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 |  | 35 | 1 | 59 | 1349 | 411.1752 | 1 |  | 35 | 1 | 59 | 1349 | 411.1752 | 28.5689 | 11.4859 | 91.9776 | 73.0133 | 37.4952 | 0.067143 | -440.5977 | -0.092641 | -1427.5366 |  | 51 | [7 empty] | 51 |  |  | 35 | 1 | 59 | 1349 | 411.1752 | 28.5689 | 19.7288 | -23.0224 | -21.9867 | -4.9419 | 0.086656 | -2028.446 | -0.4265 | -6572.1652 |  | 51 | [7 empty] | 51
WLEXME |  |  |  |  | EW, metal |  |  |  |  | 4.6 |  | 8 |  | 0.00046 |  |  | 0.0008 |  | 0.015 |  |  | 0.087223 | [5 empty] | S-5 |  |  | MECHANICAL Flr | [7 empty] | OR Exhaust / floor (cfm) | 15360 | 11200 |  |  |  | 3600 | 3600 | 3600 |  | Section >> |  | 5-Srv | # flrs >> | 5 | 5 |  | Section >> |  | 5-Srv | # flrs >> | 5 | in.Hg | Wnd-V | Tdb | Twb | Enth | Dens | Q cfm | Q/ EnA | Tons |  | 53 | [7 empty] | 53 |  |  | Section >> |  | 5-Srv | # flrs >> | 5 | in.Hg | Wnd-V | Tdb | Twb | Enth | Dens | Q cfm | Q/ EnA | Tons |  | 53 | [7 empty] | 53
WLEXCW |  |  |  |  | EW, curtain wall |  |  |  |  | 2.7 |  | 6.9 |  | 0.00027 |  |  | 0.00069 |  | 0.02 |  |  | 0.1163 | [16 empty] | Perm-Zone Sup Air (cfm / ft2) | 2.1 | 2.1 | 2.1 | 2.1 | 2.1 | 2.1 | 2.1 | 2.1 |  | 34 | 0 | XX | XX | XX | 0 |  | 34 | 0 | XX | XX | XX | XX | XX | XX | XX | XX | XX | 0 | XX | 0 |  | 4-Ofc | [7 empty] | 4-Ofc |  |  | 34 | 0 | XX | XX | XX | XX | XX | XX | XX | XX | XX | 0 | XX | 0 |  | 4-Ofc | [7 empty] | 4-Ofc
WLEXOF |  |  |  |  | EW, office bldg |  |  |  |  | 4.1 |  | 19.9 |  | 0.00041 |  |  | 0.00199 |  | 0.025 |  |  | 0.14537 | [16 empty] | Core-Zone Sup Air (cfm / ft2) | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 |  | 33 | 5 | 58 | 1339 | 408.1272 | 1 |  | 33 | 5 | 58 | 1339 | 408.1272 | 28.5793 | 11.4095 | 92.0132 | 73.0367 | 37.5095 | 0.067163 | -234.4008 | -0.024417 | -759.4584 |  | 54 | [7 empty] | 54 |  |  | 33 | 5 | 58 | 1339 | 408.1272 | 28.5793 | 19.6142 | -22.9868 | -21.9633 | -4.9359 | 0.086681 | -507.3346 | -0.052847 | -1643.764 |  | 54 | [7 empty] | 54
WLEXSC |  |  |  |  | EW, school |  |  |  |  | 3.1 |  | 8.6 |  | 0.00031 |  |  | 0.00086 |  | 0.03 |  |  | 0.17445 | [16 empty] | Inter-Zone Sup Air (cfm / ft2) | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 |  | 32 | 4 | 57 | 1324 | 403.5552 | 1 |  | 32 | 4 | 57 | 1324 | 403.5552 | 28.595 | 11.2949 | 92.0666 | 73.0718 | 37.5311 | 0.067192 | -239.5192 | -0.02495 | -776.0422 |  | 55 | [7 empty] | 55 |  |  | 32 | 4 | 57 | 1324 | 403.5552 | 28.595 | 19.4423 | -22.9334 | -21.9282 | -4.9268 | 0.086719 | -492.0725 | -0.051258 | -1594.3148 |  | 55 | [7 empty] | 55
WLEXID |  |  |  |  | EW, industrial bldg |  |  |  |  | 3.8 |  | 15.6 |  | 0.00038 |  |  | 0.00156 |  | 0.035 |  |  | 0.20352 | [26 empty] | 31 | 3 | 56 | 1309 | 398.9832 | 1 |  | 31 | 3 | 56 | 1309 | 398.9832 | 28.6106 | 11.1803 | 92.12 | 73.1069 | 37.5527 | 0.067221 | -244.565 | -0.025476 | -792.3907 |  | 56 | [7 empty] | 56 |  |  | 31 | 3 | 56 | 1309 | 398.9832 | 28.6106 | 19.2704 | -22.88 | -21.8931 | -4.9177 | 0.086756 | -476.34 | -0.049619 | -1543.3415 |  | 56 | [7 empty] | 56
WLEXRE |  |  |  |  | EW, retail |  |  |  |  | 6.9 |  | 12 |  | 0.00069 |  |  | 0.0012 |  | 0.04 |  |  | 0.23259 | [14 empty] | Bldg-Model |  | SECTION No. >> | 1-Grd | 2-Rtl | 3-Fin | 4-Ofc | 5-Srv | 6-Htl | 7-Apt | 8-din |  | 30 | 2 | 55 | 1294 | 394.4112 | 1 |  | 30 | 2 | 55 | 1294 | 394.4112 | 28.6263 | 11.0657 | 92.1734 | 73.142 | 37.5742 | 0.067251 | -249.5427 | -0.025994 | -808.5183 |  | 57 | [7 empty] | 57 |  |  | 30 | 2 | 55 | 1294 | 394.4112 | 28.6263 | 19.0985 | -22.8266 | -21.858 | -4.9086 | 0.086793 | -460.0888 | -0.047926 | -1490.6878 |  | 57 | [7 empty] | 57
WLEXRS |  |  |  |  | EW, restaurant |  |  |  |  | 3.8 |  | 5.5 |  | 0.00038 |  |  | 0.00055 |  | 0.045 |  |  | 0.26167 | [16 empty] | No. of Flrs (Incl Mech Flr) | 2 | 4 | 6 | 41 | 5 | 25 | 16 | 3 |  | 29 | 1 | 54 | 1279 | 389.8392 | 1 |  | 29 | 1 | 54 | 1279 | 389.8392 | 28.6419 | 10.9511 | 92.2268 | 73.1771 | 37.5958 | 0.06728 | -254.4561 | -0.026506 | -824.4379 |  | 58 | [7 empty] | 58 |  |  | 29 | 1 | 54 | 1279 | 389.8392 | 28.6419 | 18.9267 | -22.7732 | -21.8229 | -4.8995 | 0.086831 | -443.262 | -0.046173 | -1436.1689 |  | 58 | [7 empty] | 58
WLEXAS |  |  |  |  | EW, assembly |  |  |  |  | 3.7 |  | 6.3 |  | 0.00037 |  |  | 0.00063 |  | 0.05 |  |  | 0.29074 | [16 empty] | Area per Flr (ft2) | 76800 | 56000 | 38400 | 30800 | 24000 | 18000 | 18000 | 18000 |  | Section >> |  | 4-Ofc | # flrs >> | 41 | 15 |  | Section >> |  | 4-Ofc | # flrs >> | 41 | in.Hg | Wnd-V | Tdb | Twb | Enth | Dens | Q cfm | Q/ EnA | Tons |  | XX | [7 empty] | XX |  |  | Section >> |  | 4-Ofc | # flrs >> | 41 | in.Hg | Wnd-V | Tdb | Twb | Enth | Dens | Q cfm | Q/ EnA | Tons |  | XX | [7 empty] | XX
WLEXHC |  |  |  |  | EW, healthcare |  |  |  |  | 5.6 |  | 7.6 |  | 0.00056 |  |  | 0.00076 |  | 0.055 |  |  | 0.31982 | [16 empty] | SECTION-Height (ft) | 40 | 74 | 90 | 560 | 75 | 250 | 170 | 50 |  | 28 | 41 | 53 | 1257.5 | 383.286 | 1 |  | 28 | 41 | 53 | 1257.5 | 383.286 | 28.6644 | 10.7869 | 92.3033 | 73.2275 | 37.6267 | 0.067323 | -242.8491 | -0.024984 | -786.8312 |  | 5-Srv | [7 empty] | 5-Srv |  |  | 28 | 41 | 53 | 1257.5 | 383.286 | 28.6644 | 18.6803 | -22.6967 | -21.7725 | -4.8864 | 0.086884 | -355.0148 | -0.036524 | -1150.2478 |  | 5-Srv | [7 empty] | 5-Srv
WLEXSP |  |  |  |  | EW, sports facility |  |  |  |  | 7.4 |  | 9.8 |  | 0.00074 |  |  | 0.00098 |  | 0.06 |  |  | 0.34889 | [16 empty] | Total Section Flr Area (ft2) | 153600 | 224000 | 230400 | 1262800 | 120000 | 450000 | 288000 | 54000 |  | 27 | 39 | 51 | 1230.5 | 375.0564 | 1 |  | 27 | 39 | 51 | 1230.5 | 375.0564 | 28.6926 | 10.5806 | 92.3994 | 73.2906 | 37.6656 | 0.067376 | -248.9219 | -0.025609 | -806.5068 |  | 59 | [7 empty] | 59 |  |  | 27 | 39 | 51 | 1230.5 | 375.0564 | 28.6926 | 18.3709 | -22.6006 | -21.7094 | -4.8701 | 0.086952 | -328.6886 | -0.033816 | -1064.9512 |  | 59 | [7 empty] | 59
WLEXPC6A |  |  |  |  | EW: Precast concrete panel |  |  |  |  | 2.19 |  |  |  | 0.000219 |  |  | 0 |  | 0.065 |  |  | 0.37796 | [8 empty] | Offices | [7 empty] | Envelope Perim Length (ft) | 982.3936 | 838.8783 | 800 | 720 | 640 | 475.5993 | 475.5993 | 475.5993 |  | 26 | 35 | 47 | 1176.5 | 358.5972 | 1 |  | 26 | 35 | 47 | 1176.5 | 358.5972 | 28.7491 | 10.1681 | 92.5917 | 73.417 | 37.7434 | 0.067482 | -260.8508 | -0.026836 | -845.1564 |  | 61 | [7 empty] | 61 |  |  | 26 | 35 | 47 | 1176.5 | 358.5972 | 28.7491 | 17.7521 | -22.4083 | -21.583 | -4.8373 | 0.087086 | -268.6074 | -0.027635 | -870.288 |  | 61 | [7 empty] | 61
WLEXTV6AA |  |  |  |  | EW: Tile veneer |  |  |  |  | 1.34 |  |  |  | 0.000134 |  |  | 0 |  | 0.07 |  |  | 0.40704 | [16 empty] | Envelope Area per Flr (ft2) | 19647.8729 | 15099.809 | 12000 | 9720 | 9600 | 4755.9928 | 4755.9928 | 7133.9892 |  | 25 | 31 | 43 | 1122.5 | 342.138 | 1 |  | 25 | 31 | 43 | 1122.5 | 342.138 | 28.8057 | 9.7555 | 92.7839 | 73.5434 | 37.8213 | 0.067588 | -272.5224 | -0.028037 | -882.9727 |  | 63 | [7 empty] | 63 |  |  | 25 | 31 | 43 | 1122.5 | 342.138 | 28.8057 | 17.1333 | -22.2161 | -21.4566 | -4.8045 | 0.087221 | -190.8227 | -0.019632 | -618.2657 |  | 63 | [7 empty] | 63
WLEXCC |  |  |  |  | EW, cast-in-place concrete |  |  |  |  | 0.5 |  | 1.8 |  | 5e-05 |  |  | 0.00018 |  | 0.075 |  |  | 0.43611 | [16 empty] | Wall+Wndw Area / Bay (ft2) | 620 | 558 | 465 | 418.5 | 465 | 310 | 310 | 465 |  | 24 | 28 | 40 | 1082 | 329.7936 | 1 |  | 24 | 28 | 40 | 1082 | 329.7936 | 28.8482 | 9.4461 | 92.9281 | 73.6381 | 37.8798 | 0.067668 | -281.1267 | -0.028923 | -910.8506 |  | 65 | [7 empty] | 65 |  |  | 24 | 28 | 40 | 1082 | 329.7936 | 28.8482 | 16.6692 | -22.0719 | -21.3619 | -4.78 | 0.087323 | -98.5346 | -0.010137 | -319.2521 |  | 65 | [7 empty] | 65
WLEXPC |  |  |  |  | EW, precast concrete panel |  |  |  |  | 1.2 |  | 1.65 |  | 0.00012 |  |  | 0.000165 |  | 0.08 |  |  | 0.46519 | [16 empty] | Window Area per Bay (ft2) | 372 | 279 | 302.25 | 272.025 | 279 | 139.5 | 139.5 | 279 |  | 23 | 26 | 38 | 1055 | 321.564 | 1 |  | 23 | 26 | 38 | 1055 | 321.564 | 28.8766 | 9.2399 | 93.0242 | 73.7013 | 37.9188 | 0.067721 | -286.7981 | -0.029506 | -929.226 |  | 68 | [7 empty] | 68 |  |  | 23 | 26 | 38 | 1055 | 321.564 | 28.8766 | 16.3598 | -21.9758 | -21.2987 | -4.7636 | 0.08739 | 89.705 | 0.0092289 | 290.6443 |  | 68 | [7 empty] | 68
WLELCC14A |  |  |  |  | Elev shaft wall, cast-in-place concr |  |  |  |  | 5.55 |  |  |  | 0.000555 |  |  | 0 |  | 0.085 |  |  | 0.49426 | [16 empty] | Percent Window Area (%) | 60 | 50 | 65 | 65 | 60 | 45 | 45 | 60 |  | 22 | 24 | 36 | 1028 | 313.3344 | 1 |  | 22 | 24 | 36 | 1028 | 313.3344 | 28.905 | 9.0336 | 93.1203 | 73.7645 | 37.9579 | 0.067775 | -292.4213 | -0.030084 | -947.4449 |  | 71 | [7 empty] | 71 |  |  | 22 | 24 | 36 | 1028 | 313.3344 | 28.905 | 16.0504 | -21.8797 | -21.2355 | -4.7472 | 0.087458 | 160.5168 | 0.016514 | 520.0744 |  | 71 | [7 empty] | 71
WLSRCC14C |  |  |  |  | Stair shaft wall, cast-in-place concr |  |  |  |  | 0.15 |  |  |  | 1.5e-05 |  |  | 0 |  | 0.09 |  |  | 0.52334 | [16 empty] | Wall+Wndw Area / Floor (ft2) | 19647.8729 | 15099.809 | 12000 | 9720 | 9600 | 4755.9928 | 4755.9928 | 7133.9892 |  | 21 | 25 | 37 | 1041.5 | 317.4492 | 1 |  | 21 | 25 | 37 | 1041.5 | 317.4492 | 28.8908 | 9.1367 | 93.0723 | 73.7329 | 37.9383 | 0.067748 | -289.6156 | -0.029796 | -938.3544 |  | 74 | [7 empty] | 74 |  |  | 21 | 25 | 37 | 1041.5 | 317.4492 | 28.8908 | 16.2051 | -21.9277 | -21.2671 | -4.7554 | 0.087424 | 130.0423 | 0.013379 | 421.337 |  | 74 | [7 empty] | 74
FLCO15 |  |  |  |  | Floor: Office Bldg, reinforced concr |  |  |  |  | 0.35 |  |  |  | 3.5e-05 |  |  | 0 |  | 0.095 |  |  | 0.55241 | [16 empty] | Window Area per Floor (ft2) | 11788.7238 | 7549.9045 | 7800 | 6318 | 5760 | 2140.1968 | 2140.1968 | 4280.3935 |  | 20 | 22 | 34 | 1001 | 305.1048 | 1 |  | 20 | 22 | 34 | 1001 | 305.1048 | 28.9334 | 8.8273 | 93.2164 | 73.8277 | 37.9969 | 0.067828 | -297.9988 | -0.030658 | -965.5162 |  | 76 | [7 empty] | 76 |  |  | 20 | 22 | 34 | 1001 | 305.1048 | 28.9334 | 15.741 | -21.7836 | -21.1723 | -4.7308 | 0.087525 | 208.4391 | 0.021444 | 675.3428 |  | 76 | [7 empty] | 76
Element ID |  |  |  |  | Description |  |  |  |  | Mean |  | Max |  | Mean |  |  | Max |  | 0.1 |  |  | 0.58148 | [16 empty] | Wall Leakage Area (ft2) | 15.6397 | 15.0243 | 8.358 | 6.77 | 7.6416 | 5.2054 | 5.2054 | 5.6787 |  | 19 | 19 | 31 | 960.5 | 292.7604 | 1 |  | 19 | 19 | 31 | 960.5 | 292.7604 | 28.9761 | 8.518 | 93.3606 | 73.9224 | 38.0555 | 0.067908 | -306.2852 | -0.031511 | -992.3641 |  | 78 | [7 empty] | 78 |  |  | 19 | 19 | 31 | 960.5 | 292.7604 | 28.9761 | 15.2769 | -21.6394 | -21.0776 | -4.7062 | 0.087627 | 264.3834 | 0.0272 | 856.6022 |  | 78 | [7 empty] | 78
Windows (W) | [8 empty] | Leakg ( cm2 / m2 ) |  |  |  |  | Leakg ( ft2 / ft2 ) |  |  |  |  | 0.105 |  |  | 0.61056 | [16 empty] | Window Leakage Area (ft2) | 7.6627 | 1.8875 | 1.326 | 1.0741 | 2.016 | 0.74907 | 0.74907 | 1.0701 |  | 18 | 16 | 28 | 920 | 280.416 | 1 |  | 18 | 16 | 28 | 920 | 280.416 | 29.0188 | 8.2086 | 93.5048 | 74.0172 | 38.1142 | 0.067988 | -314.4823 | -0.032354 | -1018.9228 |  | 79 | [7 empty] | 79 |  |  | 18 | 16 | 28 | 920 | 280.416 | 29.0188 | 14.8128 | -21.4952 | -20.9828 | -4.6816 | 0.087729 | 310.2678 | 0.031921 | 1005.2676 |  | 79 | [7 empty] | 79
WNIO6A |  |  |  |  | W Inoperable, Building A |  |  |  |  | 1.1 |  | 1.73 |  | 0.00011 |  |  | 0.000173 |  | 0.11 |  |  | 0.63963 | [16 empty] | Envl Leakg Area / Floor (ft2) | 186.6548 | 113.2486 | 9.684 | 7.844 | 9.6576 | 40.4259 | 45.1819 | 46.3709 |  | 17 | 13 | 25 | 879.5 | 268.0716 | 1 |  | 17 | 13 | 25 | 879.5 | 268.0716 | 29.0615 | 7.8992 | 93.649 | 74.112 | 38.1729 | 0.068069 | -322.597 | -0.033189 | -1045.2144 |  | 81 | [7 empty] | 81 |  |  | 17 | 13 | 25 | 879.5 | 268.0716 | 29.0615 | 14.3487 | -21.351 | -20.888 | -4.657 | 0.08783 | 350.0706 | 0.036015 | 1134.2287 |  | 81 | [7 empty] | 81
WNOO6C |  |  |  |  | W Operable, Building C |  |  |  |  | 2.6 |  | 3.46 |  | 0.00026 |  |  | 0.000346 |  | 0.115 |  |  | 0.66871 | [16 empty] | Totl Section Envel Area (ft2) | 39295.7459 | 60399.236 | 72000 | 398520 | 48000 | 118899.8198 | 76095.8847 | 21401.9676 |  | 16 | 10 | 22 | 839 | 255.7272 | 1 |  | 16 | 10 | 22 | 839 | 255.7272 | 29.1043 | 7.5898 | 93.7932 | 74.2067 | 38.2317 | 0.068149 | -330.6354 | -0.034016 | -1071.2586 |  | 82 | [7 empty] | 82 |  |  | 16 | 10 | 22 | 839 | 255.7272 | 29.1043 | 13.8846 | -21.2068 | -20.7933 | -4.6325 | 0.087932 | 385.6794 | 0.039679 | 1249.6011 |  | 82 | [7 empty] | 82
FRWNMACA |  |  |  |  | W framing, masonry, caulked |  |  |  |  | 1.3 |  | 2.1 |  | 0.00013 |  |  | 0.00021 |  | 0.12 |  |  | 0.69778 | [16 empty] | Totl Section Leakg Area (ft2) | 373.3096 | 452.9943 | 58.104 | 321.6056 | 48.288 | 1010.6485 | 722.9109 | 139.1128 |  | 15 | 7 | 19 | 798.5 | 243.3828 | 1 |  | 15 | 7 | 19 | 798.5 | 243.3828 | 29.1472 | 7.2804 | 93.9373 | 74.3015 | 38.2905 | 0.068229 | -338.6028 | -0.034836 | -1097.073 |  | 83 | [7 empty] | 83 |  |  | 15 | 7 | 19 | 798.5 | 243.3828 | 29.1472 | 13.4206 | -21.0627 | -20.6985 | -4.6079 | 0.088034 | 418.1669 | 0.043021 | 1354.8607 |  | 83 | [7 empty] | 83
FRWNWDCA |  |  |  |  | W framing, wood, caulked |  |  |  |  | 0.3 |  | 0.3 |  | 3e-05 |  |  | 3e-05 |  | 0.125 |  |  | 0.72685 | [26 empty] | 14 | 5 | 17 | 771.5 | 235.1532 | 1 |  | 14 | 5 | 17 | 771.5 | 235.1532 | 29.1758 | 7.0741 | 94.0335 | 74.3647 | 38.3297 | 0.068283 | -343.8774 | -0.035378 | -1114.1628 |  | 6-Htl | [7 empty] | 6-Htl |  |  | 14 | 5 | 17 | 771.5 | 235.1532 | 29.1758 | 13.1112 | -20.9665 | -20.6353 | -4.5915 | 0.088102 | 438.4367 | 0.045107 | 1420.5349 |  | 6-Htl | [7 empty] | 6-Htl
WNDBNW |  |  |  |  | W, dbl hung, no wthrstrp |  |  |  |  | 2.5 |  | 6.1 |  | 0.00025 |  |  | 0.00061 |  | 0.13 |  |  | 0.75593 |  |  |  |  | S-4 |  |  | Banking Trading | [6 empty] | Air-Systm |  | SECTION No. >> | 1-Grd | 2-Rtl | 3-Fin | 4-Ofc | 5-Srv | 6-Htl | 7-Apt | 8-din |  | 13 | 3 | 15 | 744.5 | 226.9236 | 1 |  | 13 | 3 | 15 | 744.5 | 226.9236 | 29.2044 | 6.8678 | 94.1296 | 74.4279 | 38.369 | 0.068336 | -349.124 | -0.035918 | -1131.1618 |  | 84 | [7 empty] | 84 |  |  | 13 | 3 | 15 | 744.5 | 226.9236 | 29.2044 | 12.8018 | -20.8704 | -20.5721 | -4.5751 | 0.08817 | 457.7691 | 0.047096 | 1483.1718 |  | 84 | [7 empty] | 84
WNDBNWM |  |  |  |  | W, dbl hung with storm, no wthrstrp |  |  |  |  | 0.97 |  | 1.7 |  | 9.7e-05 |  |  | 0.00017 |  | 0.135 |  |  | 0.785 | [16 empty] | Ventil Air Supply (cfm / flr) | 23040 | 18666.6667 | 7680 | 4106.6667 | 2400 | 2160 | 2160 | 6000 |  | 12 | 1 | 13 | 717.5 | 218.694 | 1 |  | 12 | 1 | 13 | 717.5 | 218.694 | 29.2331 | 6.6616 | 94.2257 | 74.4911 | 38.4082 | 0.06839 | -354.3439 | -0.036455 | -1148.0742 |  | 85 | [7 empty] | 85 |  |  | 12 | 1 | 13 | 717.5 | 218.694 | 29.2331 | 12.4924 | -20.7743 | -20.5089 | -4.5587 | 0.088238 | 476.2782 | 0.049 | 1543.1413 |  | 85 | [7 empty] | 85
WNDBWE |  |  |  |  | W, dbl hung, wthrstrp |  |  |  |  | 0.65 |  | 1.9 |  | 6.5e-05 |  |  | 0.00019 |  | 0.14 |  |  | 0.81408 | [16 empty] | Core Exhaust Air (cfm / flr) | 15360 | 11200 | 5760 | 4620 | 3600 | 3600 | 3600 | 3600 |  | Section >> |  | 3-Fin | # flrs >> | 6 | 4 |  | Section >> |  | 3-Fin | # flrs >> | 6 | in.Hg | Wnd-V | Tdb | Twb | Enth | Dens | Q cfm | Q/ EnA | Tons |  | 86 | [7 empty] | 86 |  |  | Section >> |  | 3-Fin | # flrs >> | 6 | in.Hg | Wnd-V | Tdb | Twb | Enth | Dens | Q cfm | Q/ EnA | Tons |  | 86 | [7 empty] | 86
WNDBWESM |  |  |  |  | W, dbl hung with storm, wthrstrp |  |  |  |  | 0.79 |  | 1 |  | 7.9e-05 |  |  | 0.0001 |  | 0.145 |  |  | 0.84315 | [16 empty] | Perim-Zone Sup Air (cfm / flr) | 30945.3999 | 26424.6657 | 25200 | 22680 | 20160 | 14981.3773 | 14981.3773 | 14981.3773 |  | 11 | 6 | 12 | 704 | 214.5792 |  |  | 11 | 6 | 12 | 704 | 214.5792 | 29.2474 | 6.5584 | 94.2738 | 74.5226 | 38.4279 | 0.068417 | -440.6718 | -0.036723 | -1427.7765 |  | 88 | [7 empty] | 88 |  |  | 11 | 6 | 12 | 704 | 214.5792 | 29.2474 | 12.3377 | -20.7262 | -20.4774 | -4.5505 | 0.088272 | 599.0785 | 0.049923 | 1941.0145 |  | 88 | [7 empty] | 88
WNSISHWE |  |  |  |  | W, sngl hung, wthrstrp |  |  |  |  | 0.87 |  | 1.24 |  | 8.7e-05 |  |  | 0.000124 |  | 0.15 |  |  | 0.87223 |  |  |  | S-3 |  |  |  | MECHANICAL Flr | [8 empty] | Core-Zone Sup Air (cfm / flr) | 17280 | 12600 | 8640 | 6930 | 5400 | 4050 | 4050 | 4050 |  | 10 | 5 | 11 | 689 | 210.0072 |  |  | 10 | 5 | 11 | 689 | 210.0072 | 29.2634 | 6.4439 | 94.3272 | 74.5577 | 38.4497 | 0.068447 | -444.2296 | -0.037019 | -1439.3039 |  | 90 | [7 empty] | 90 |  |  | 10 | 5 | 11 | 689 | 210.0072 | 29.2634 | 12.1658 | -20.6728 | -20.4423 | -4.5414 | 0.08831 | 611.1413 | 0.050928 | 1980.0977 |  | 90 | [7 empty] | 90
WNSISLAL |  |  |  |  | W, sngl horiz slider, alum |  |  |  |  | 0.8 |  | 2.06 |  | 8e-05 |  |  | 0.000206 |  | 0.155 |  |  | 0.9013 | [5 empty] | Restaurants | [10 empty] | Inter-Zone Sup Air (cfm / flr) | 62064.0953 | 43416.8258 | 26400 | 20000 | 14400 | 10866.0108 | 10866.0108 | 10866.0108 |  | 9 | 4 | 10 | 674 | 205.4352 | 1 |  | 9 | 4 | 10 | 674 | 205.4352 | 29.2793 | 6.3293 | 94.3806 | 74.5928 | 38.4716 | 0.068476 | -447.7781 | -0.037315 | -1450.8011 |  | 92 | [7 empty] | 92 |  |  | 9 | 4 | 10 | 674 | 205.4352 | 29.2793 | 11.9939 | -20.6194 | -20.4072 | -4.5323 | 0.088348 | 622.9563 | 0.051913 | 2018.3784 |  | 92 | [7 empty] | 92
WNSISLWD |  |  |  |  | W, sngl horiz slider, wood |  |  |  |  | 0.44 |  | 0.99 |  | 4.4e-05 |  |  | 9.9e-05 |  | 0.16 |  |  | 0.93037 | [16 empty] | Total Supply Air (cfm / flr) | 110289.4952 | 82441.4916 | 60240 | 49610 | 39960 | 29897.3881 | 29897.3881 | 29897.3881 |  | 8 | 3 | 9 | 659 | 200.8632 | 1 |  | 8 | 3 | 9 | 659 | 200.8632 | 29.2952 | 6.2147 | 94.434 | 74.6279 | 38.4934 | 0.068506 | -451.3175 | -0.03761 | -1462.2688 |  | 94 | [7 empty] | 94 |  |  | 8 | 3 | 9 | 659 | 200.8632 | 29.2952 | 11.822 | -20.566 | -20.3721 | -4.5232 | 0.088386 | 634.5375 | 0.052878 | 2055.9016 |  | 94 | [7 empty] | 94
WNSLALWE |  |  |  |  | W, dbl horiz slider, alum, wthrstrp |  |  |  |  | 0.72 |  | 0.8 |  | 7.2e-05 |  |  | 8e-05 |  | 0.165 |  |  | 0.95945 | [14 empty] | Building Model Summary | [11 empty] | 7 | 2 | 8 | 644 | 196.2912 | 1 |  | 7 | 2 | 8 | 644 | 196.2912 | 29.3112 | 6.1001 | 94.4874 | 74.663 | 38.5153 | 0.068536 | -454.8481 | -0.037904 | -1473.7077 |  | 96 | [7 empty] | 96 |  |  | 7 | 2 | 8 | 644 | 196.2912 | 29.3112 | 11.6501 | -20.5126 | -20.337 | -4.514 | 0.088424 | 645.8975 | 0.053825 | 2092.708 |  | 96 | [7 empty] | 96
WNSLNW |  |  |  |  | W, dbl horiz slider, no wthrstrp |  |  |  |  | 1.1 |  | 3.4 |  | 0.00011 |  |  | 0.00034 |  | 0.17 |  |  | 0.98852 | [14 empty] | # Flrs | Bldg-H | Ntrl-H | Site-Alt |  | Totl Bldg-Area |  | Totl Envl-Area |  | Totl Leakg-Area | % Lkg-A |  | 6 | 1 | 7 | 629 | 191.7192 | 1 |  | 6 | 1 | 7 | 629 | 191.7192 | 29.3272 | 5.9855 | 94.5408 | 74.6981 | 38.5371 | 0.068566 | -458.3699 | -0.038197 | -1485.1185 |  | 98 | [7 empty] | 98 |  |  | 6 | 1 | 7 | 629 | 191.7192 | 29.3272 | 11.4782 | -20.4592 | -20.3019 | -4.5049 | 0.088462 | 657.0477 | 0.054754 | 2128.8347 |  | 98 | [7 empty] | 98
WNSLWDWE |  |  |  |  | W, dbl horiz slider, wood, wthrstrp |  |  |  |  | 0.55 |  | 1.72 |  | 5.5e-05 |  |  | 0.000172 | [7 empty] | S-2 |  | Retail | [9 empty] | 102 | 1309 | 654.5 | 500 | 2782800 |  | 834612.6539 |  | 3126.9737 |  | 0.37466 |  | Section >> |  | 2-Rtl | # flrs >> | 4 | 3 |  | Section >> |  | 2-Rtl | # flrs >> | 4 | in.Hg | Wnd-V | Tdb | Twb | Enth | Dens | Q cfm | Q/ EnA | Tons |  | 100 | [7 empty] | 100 |  |  | Section >> |  | 2-Rtl | # flrs >> | 4 | in.Hg | Wnd-V | Tdb | Twb | Enth | Dens | Q cfm | Q/ EnA | Tons |  | 100 | [7 empty] | 100
Element ID |  |  |  |  | Description |  |  |  |  | Mean |  | Max |  | Mean |  |  | Max | [19 empty] | Infiltration per Vertical Bldg Sections | [11 empty] | 5 | 3 | 5 | 594 | 181.0512 | 1 |  | 5 | 3 | 5 | 594 | 181.0512 | 29.3644 | 5.7181 | 94.6654 | 74.78 | 38.5882 | 0.068636 | -4907.601 | -0.32501 | -15900.6271 |  | 102 | [7 empty] | 102 |  |  | 5 | 3 | 5 | 594 | 181.0512 | 29.3644 | 11.0772 | -20.3346 | -20.22 | -4.4837 | 0.08855 | 8250.6365 | 0.54641 | 26732.0623 |  | 102 | [7 empty] | 102
Exterior Doors (ED) | [8 empty] | Leakg ( cm2 / m2 ) |  |  |  |  | Leakg ( ft2 / ft2 ) | [10 empty] | S-1 | [7 empty] | 2-level Atrium | [5 empty] | SCTN (max=5 chars) >> | 1-Grd | 2-Rtl | 3-Fin | 4-Ofc | 5-Srv | 6-Htl | 7-Apt | 8-din |  | 4 | 2 | 4 | 576 | 175.5648 | 1 |  | 4 | 2 | 4 | 576 | 175.5648 | 29.3836 | 5.5806 | 94.7294 | 74.8222 | 38.6144 | 0.068672 | -4962.348 | -0.32864 | -16078.0076 |  | XX | [7 empty] | XX |  |  | 4 | 2 | 4 | 576 | 175.5648 | 29.3836 | 10.8709 | -20.2706 | -20.1778 | -4.4727 | 0.088596 | 8393.1546 | 0.55585 | 27193.8209 |  | XX | [7 empty] | XX
DREXFRWD |  |  |  |  | Door, exterior, wood, frame, typical |  |  |  |  | 1.7 |  |  |  | 0.00017 |  |  | 0 | [21 empty] | SMMR: Infltr - cfm / Section | 15092.8265 | 19849.0395 | 2675.9955 | 12107.5319 | 1222.4838 | 11481.7225 | 17888.0737 | 2511.9371 |  | 3 | 1 | 3 | 558 | 170.0784 | 1 |  | 3 | 1 | 3 | 558 | 170.0784 | 29.4028 | 5.4431 | 94.7935 | 74.8643 | 38.6407 | 0.068708 | -5016.8306 | -0.33224 | -16254.5313 |  | 7-Apt | [7 empty] | 7-Apt |  |  | 3 | 1 | 3 | 558 | 170.0784 | 29.4028 | 10.6646 | -20.2065 | -20.1357 | -4.4618 | 0.088641 | 8533.0898 | 0.56511 | 27647.2108 |  | 7-Apt | [7 empty] | 7-Apt
DREXSLGL |  |  |  |  | Door, exterior, sliding glass, typical |  |  |  |  | 22 |  |  |  | 0.0022 |  |  | 0 |  | S = Vertical Section | [19 empty] | SMMR: Infltr cfm/sf Envel-A | 0.38408 | 0.32863 | 0.037167 | 0.030381 | 0.025468 | 0.096566 | 0.23507 | 0.11737 |  | Section >> |  | 1-Grd | # flrs >> | 2 | 2 |  | Section >> |  | 1-Grd | # flrs >> | 2 | in.Hg | Wnd-V | Tdb | Twb | Enth | Dens | Q cfm | Q/ EnA | Tons |  | 100 | [7 empty] | 100 |  |  | Section >> |  | 1-Grd | # flrs >> | 2 | in.Hg | Wnd-V | Tdb | Twb | Enth | Dens | Q cfm | Q/ EnA | Tons |  | 100 | [7 empty] | 100
DREX_R |  |  |  |  | Door, exterior |  |  |  |  | 6 |  |  |  | 0.0006 |  |  | 0 | [21 empty] | WNTR: Infltr - cfm / Section | 30122.1794 | 33569.1745 | 3701.5705 | 10926.1615 | 2379.0978 | 64387.1327 | 68538.017 | 12039.8696 |  | 2 | 2 | 2 | 520 | 158.496 | 1 |  | 2 | 2 | 2 | 520 | 158.496 | 29.4434 | 5.1528 | 94.9288 | 74.9532 | 38.6962 | 0.068783 | -7490.6939 | -0.38125 | -24269.8482 |  | 101 | [7 empty] | 101 |  |  | 2 | 2 | 2 | 520 | 158.496 | 29.4434 | 10.2292 | -20.0712 | -20.0468 | -4.4387 | 0.088737 | 14943.0824 | 0.76054 | 48415.587 |  | 101 | [7 empty] | 101
DREX_RM |  |  |  |  | Door, exterior (MH) |  |  |  |  | 4 |  |  |  | 0.0004 |  |  | 0 | [6 empty] | S-0 |  |  |  |  | MECHANICAL Flr | [9 empty] | WNTR: Infltr cfm/sf Envel-A | 0.76655 | 0.55579 | 0.051411 | 0.027417 | 0.049565 | 0.54152 | 0.90068 | 0.56256 |  | 1 | 1 | 1 | 500 | 152.4 | 1 |  | 1 | 1 | 1 | 500 | 152.4 | 29.4647 | 5 | 95 | 75 | 38.7254 | 0.068823 | -7602.1326 | -0.38692 | -24630.9096 |  | XX | [7 empty] | XX |  |  | 1 | 1 | 1 | 500 | 152.4 | 29.4647 | 10 | -20 | -20 | -4.4266 | 0.088788 | 15179.097 | 0.77256 | 49180.2743 |  | XX | [7 empty] | XX

## SMMR-Calcs
1 | 5 | 5 | 5 | 6 | 6 | 6 | 6 | 6.5 | 6 | 6 | 6 | 6 | 6 | 7 | 6 | 6 | 7.5 | 7 | 6 | 6 | 7 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 7.5 | 6.5 | 2 | 2 | 5 | 5 | 5 | 6 | 6 |  | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 9 | 6.5 | 6.5 | 7 | 9
| Site Altit |  | 500 | Bldg-H | 1309 | NPL-H | 654.5 | Total Bldg Area |  | 2782800 |  | Total Envel Area |  | 834612.6539 |  | Leakg-A | 3126.9737 | Wnd-Vel Diff |  | 10 |  | Temp Drop with Altitude |  |  | DB | 0.00356 | WB | 0.00234 |  |  | ∆PS = C1*ρO* [ (TO - TI) / TI ] * g * (HNPL - H) | [5 empty] | ∆PS = | Stack Effect Press Diff (in.wg) |  |  |  | PI - PO | Bldg Pressuriz (Indr Press - Outdr Press)
|  |  |  | Alt ref Sea-Lvl |  | Outdr Std. Atm. Press. @ Altit |  |  |  | Wnd V | DB | WB | DP | W | RH | V | d | H | Tdb | Twb |  | Psychrometric Calculations for DP, RH, V, W, H, TR | [8 empty] | Q = Cd * A * ( 2 * ∆P/d )0.5 |  |  |  | TO (OR) , Ti (OR) |  | ∆PW = | Wind Press (in.wg) |  |  | UH = mph |  | ρO = OA dens |  | Coolg/yr = CFM*1.08*CDD
|  |  |  | feet | meters | K-Pa | in.Hg | in.H2O | psi | mph | F | F | F | lbs/b | % | ft3/lb | lbs/ft3 | btu/lb | R | R |  | PWSwb | WSwb | PWSdb | VPs | VPa | a | WSdb |  |  | ∆PW = C2 * s2 * CP * ρO * (UH)2 / 2 | [5 empty] | Q = | Airflow Rate (ft3/sec) |  |  | A = Leakg-A |  | Iniltr SHG/hr = CFM * 1.08 (To-Ti))
| At Sea-Level |  |  | 0 | 0 | 101.325 | 29.9213 | 406.0345 | 14.6546 | 10 | 75 | 62 | 53.2919 | 0.0089201 | 48.1285 | 13.6728 | 0.073138 | 27.7612 | 534.7 | 521.7 |  | 0.27548 | 0.011916 | 0.43051 | 0.87899 | 0.42305 | -1.5741 | 0.018825 |  |  | Convert K-Pa to |  |  | In.Hg | 0.29611 | in.wg | 4.0186 | PSI | 0.14504 | C1 = | 0.000598 | g = | 32.17 | C2 = | 0.013 | Clg-DD | 2680
| Indoor Conditions |  |  | 500 | 152.4 | 99.5077 | 29.3846 | 398.752 | 14.3917 | 5 | 75 | 62 | 66.0781 | 0.014436 | 40.0699 | 14.53 | 0.068823 | 38.7254 | 554.7 | 534.7 |  | 0.43051 | 0.019179 | 0.817 | 1.6681 | 0.66653 | -1.1195 | 0.037434 |  |  | Convert in.H20 to |  |  | In.Hg | 0.073684 | K-Pa | 0.24885 | PSI | 0.036092 | s = | 0.4 | CF = | 0.65 | CP = | 0.065 | SpHt-A | 0.24
| Level | Sctn | Bldg | Alt ref Sea-Lvl |  | Outdr Std. Atm. Press. @ Altit |  |  |  | Wnd V | DB | WB | DP | W | RH | V | d | H | Tdb | Twb |  | Psychrometric Calculations for DP, RH, V, W, H, TR | [8 empty] | Level | Sctn | Bldg | Alt ref Sea-Lvl |  | Floor | Floor | ∆PS | ∆PW | ∆P = | ∆P + | Leakg Q | Exfl - | Leakage | Q / | SHG | SHG/yr
| ID No. | Flr No. | Flr No. | feet | meters | K-Pa | in.Hg | in.H2O | psi | mph | F | F | F | lbs/b | % | ft3/lb | lbs/ft3 | btu/lb | R | R |  | PWSwb | WSwb | PWSdb | VPs | VPa | a | WSdb |  |  | ID No. | Flr No. | Flr No. | feet | meters | Data | Hght | in.H2O | in.H2O | ∆PW+∆PS | PI - PO | cfm | Infl + | ft3/min | Envel-A | btuh | tons
| Section >> |  | 8-din | Flrs/S | 3 | Section Ht (ft) |  | 50 | Per-L | 475.5993 | Floor-Envel-Area (ft2) |  |  | 7133.9892 | S-Flr-Area (ft2) |  | 54000 | Wndw Area (%) |  | 60 |  | Inside-Outside (PI-PO) |  |  | 0.015 | Leakg Flow Cf |  | 0.65 |  |  | Section >> |  | 8-din | Flrs/S | 3 | 2 | Envel Leakg A |  | 46.3709 | Appr. Sctn-Infltr (cfm) |  |  | 2511.9371 | Appr. Sctn Infltr (tons) |  |  | 7270.5507
| 61 | 0 | XX | XX | XX | XX | XX | XX | XX | XX | [11 empty] | XX | XX | XX | XX | XX | XX | XX |  |  | 61 | 0 | XX | XX | XX | 0 | XX | XX | XX | XX | XX | 0 | XX | 0 | XX | XX | 0 | bar: DB to Twb
| 60 | 2 | 101 | 1789 | 545.2872 | 94.944 | 28.1134 | 381.5388 | 13.7705 | 14.8472 | 90.4112 | 71.9837 | 63.4224 | 0.013774 | 42.1022 | 15.0867 | 0.066284 | 36.8657 | 550.1112 | 531.6837 |  | 0.389 | 0.018081 | 0.70862 | 1.4468 | 0.60909 | -1.2096 | 0.033743 |  |  | 60 | 2 | 101 | 1789 | 545.2872 | 1 | 1289 | -0.023319 | 0.00098774 | -0.022332 | -0.0073315 | 850.5892 | Exfl | 850.5892 | 0.11923 | 14157.2514 | 2461.9453
| 59 | 1 | 100 | 1774 | 540.7152 | 94.9961 | 28.1288 | 381.7482 | 13.778 | 14.7326 | 90.4646 | 72.0188 | 63.4531 | 0.013781 | 42.0773 | 15.0801 | 0.066313 | 36.8871 | 550.1646 | 531.7188 |  | 0.38946 | 0.018093 | 0.7098 | 1.4493 | 0.60975 | -1.2085 | 0.033783 |  |  | 59 | 1 | 100 | 1774 | 540.7152 | 1 | 1274 | -0.022857 | 0.00097298 | -0.021884 | -0.006884 | 824.0355 | Exfl | 824.0355 | 0.11551 | 13762.8147 | 2385.0884
| Section >> |  | 7-Apt | Flrs/S | 19 | Section Ht (ft) |  | 170 | Per-L | 475.5993 | Floor-Envel-Area (ft2) |  |  | 4755.9928 | S-Flr-Area (ft2) |  | 288000 | Wndw Area (%) |  | 45 |  | Inside-Outside (PI-PO) |  |  | 0.01 | Leakg Flow Cf |  | 0.65 |  |  | Section >> |  | 7-Apt | Flrs/S | 19 | 9 | Envel Leakg A |  | 45.1819 | Appr. Sctn-Infltr (cfm) |  |  | 17888.0737 | Appr. Sctn Infltr (tons) |  |  | 57957.3587
| 58 | 0 | XX | XX | XX | XX | XX | XX | XX | XX | [11 empty] | XX | XX | XX | XX | XX | XX | XX |  |  | 58 | 0 | XX | XX | XX | 0 | XX | XX | XX | XX | XX | 0 | XX | 0 | XX | XX | 0 | bar: DB to Twb
| 57 | 19 | 102 | 1779 | 542.2392 | 94.9788 | 28.1237 | 381.6784 | 13.7755 | 14.7708 | 90.4468 | 72.0071 | 63.4428 | 0.013779 | 42.0856 | 15.0823 | 0.066303 | 36.88 | 550.1468 | 531.7071 |  | 0.38931 | 0.018089 | 0.70941 | 1.4484 | 0.60953 | -1.2089 | 0.03377 |  |  | 57 | 19 | 102 | 1779 | 542.2392 | 1 | 1279 | -0.023012 | 0.00097789 | -0.022034 | -0.012034 | 1061.637 | Exfl | 1061.637 | 0.22322 | 17710.7605 | 3439.704
| 56 | 17 | 100 | 1759 | 536.1432 | 95.0483 | 28.1443 | 381.9577 | 13.7856 | 14.618 | 90.518 | 72.0539 | 63.4838 | 0.013789 | 42.0524 | 15.0734 | 0.066342 | 36.9085 | 550.218 | 531.7539 |  | 0.38992 | 0.018105 | 0.71099 | 1.4517 | 0.61041 | -1.2074 | 0.033823 |  |  | 56 | 17 | 100 | 1759 | 536.1432 | 1 | 1259 | -0.02239 | 0.00095832 | -0.021432 | -0.011432 | 1034.4563 | Exfl | 1034.4563 | 0.21751 | 17336.8641 | 3351.6385
| 55 | 15 | 98 | 1739 | 530.0472 | 95.1178 | 28.1649 | 382.2372 | 13.7957 | 14.4652 | 90.5892 | 72.1007 | 63.5247 | 0.013799 | 42.0192 | 15.0646 | 0.066381 | 36.937 | 550.2892 | 531.8007 |  | 0.39054 | 0.018121 | 0.71258 | 1.4549 | 0.61129 | -1.206 | 0.033876 |  |  | 55 | 15 | 98 | 1739 | 530.0472 | 1 | 1239 | -0.021762 | 0.00093895 | -0.020823 | -0.010823 | 1006.2158 | Exfl | 1006.2158 | 0.21157 | 16940.9443 | 3260.1393
| 54 | 13 | 96 | 1719 | 523.9512 | 95.1874 | 28.1855 | 382.5169 | 13.8058 | 14.3125 | 90.6604 | 72.1475 | 63.5656 | 0.013809 | 41.9861 | 15.0558 | 0.06642 | 36.9655 | 550.3604 | 531.8475 |  | 0.39116 | 0.018137 | 0.71416 | 1.4582 | 0.61217 | -1.2046 | 0.03393 |  |  | 54 | 13 | 96 | 1719 | 523.9512 | 1 | 1219 | -0.021125 | 0.00091976 | -0.020206 | -0.010206 | 976.8236 | Exfl | 976.8236 | 0.20539 | 16521.2022 | 3164.9085
| 53 | 11 | 94 | 1699 | 517.8552 | 95.257 | 28.2061 | 382.7967 | 13.8159 | 14.1597 | 90.7316 | 72.1943 | 63.6065 | 0.013819 | 41.953 | 15.0469 | 0.066459 | 36.994 | 550.4316 | 531.8943 |  | 0.39178 | 0.018152 | 0.71576 | 1.4614 | 0.61305 | -1.2031 | 0.033983 |  |  | 53 | 11 | 94 | 1699 | 517.8552 | 1 | 1199 | -0.020482 | 0.00090075 | -0.019581 | -0.0095808 | 946.1723 | Exfl | 946.1723 | 0.19894 | 16075.5484 | 3065.5984
| 52 | 9 | 92 | 1679 | 511.7592 | 95.3267 | 28.2267 | 383.0767 | 13.826 | 14.0069 | 90.8028 | 72.2411 | 63.6475 | 0.013829 | 41.92 | 15.0381 | 0.066498 | 37.0226 | 550.5028 | 531.9411 |  | 0.3924 | 0.018168 | 0.71735 | 1.4647 | 0.61393 | -1.2017 | 0.034037 |  |  | 52 | 9 | 92 | 1679 | 511.7592 | 1 | 1179 | -0.01983 | 0.00088193 | -0.018948 | -0.0089483 | 914.1354 | Exfl | 914.1354 | 0.19221 | 15601.5313 | 2961.7987
| 51 | 7 | 90 | 1659 | 505.6632 | 95.3964 | 28.2474 | 383.3569 | 13.8361 | 13.8541 | 90.874 | 72.2879 | 63.6885 | 0.013839 | 41.8871 | 15.0293 | 0.066537 | 37.0511 | 550.574 | 531.9879 |  | 0.39302 | 0.018184 | 0.71895 | 1.4679 | 0.61481 | -1.2003 | 0.034091 |  |  | 51 | 7 | 90 | 1659 | 505.6632 | 1 | 1159 | -0.019171 | 0.0008633 | -0.018308 | -0.0083079 | 880.5615 | Exfl | 880.5615 | 0.18515 | 15096.2385 | 2853.0194
| 50 | 5 | 88 | 1639 | 499.5672 | 95.4662 | 28.268 | 383.6372 | 13.8462 | 13.7013 | 90.9452 | 72.3347 | 63.7294 | 0.013849 | 41.8542 | 15.0205 | 0.066576 | 37.0797 | 550.6452 | 532.0347 |  | 0.39364 | 0.0182 | 0.72055 | 1.4712 | 0.6157 | -1.1988 | 0.034144 |  |  | 50 | 5 | 88 | 1639 | 499.5672 | 1 | 1139 | -0.018505 | 0.00084486 | -0.01766 | -0.0076598 | 845.2676 | Exfl | 845.2676 | 0.17773 | 14556.1619 | 2738.6671
| 49 | 3 | 86 | 1619 | 493.4712 | 95.536 | 28.2887 | 383.9177 | 13.8563 | 13.5485 | 91.0164 | 72.3815 | 63.7704 | 0.013859 | 41.8214 | 15.0117 | 0.066615 | 37.1083 | 550.7164 | 532.0815 |  | 0.39427 | 0.018216 | 0.72216 | 1.4745 | 0.61659 | -1.1974 | 0.034198 |  |  | 49 | 3 | 86 | 1619 | 493.4712 | 1 | 1119 | -0.01783 | 0.00082661 | -0.017004 | -0.0070038 | 808.0283 | Exfl | 808.0283 | 0.1699 | 13977.0068 | 2618.0119
| 48 | 2 | 85 | 1609 | 490.4232 | 95.5709 | 28.299 | 384.058 | 13.8614 | 13.4721 | 91.052 | 72.4049 | 63.7909 | 0.013864 | 41.805 | 15.0073 | 0.066634 | 37.1225 | 550.752 | 532.1049 |  | 0.39458 | 0.018224 | 0.72296 | 1.4761 | 0.61703 | -1.1967 | 0.034225 |  |  | 48 | 2 | 85 | 1609 | 490.4232 | 1 | 1109 | -0.01749 | 0.00081755 | -0.016673 | -0.0066729 | 788.5936 | Exfl | 788.5936 | 0.16581 | 13671.1512 | 2555.0434
| 47 | 1 | 84 | 1599 | 487.3752 | 95.6058 | 28.3094 | 384.1984 | 13.8664 | 13.3957 | 91.0876 | 72.4283 | 63.8114 | 0.013869 | 41.7886 | 15.0029 | 0.066654 | 37.1368 | 550.7876 | 532.1283 |  | 0.39489 | 0.018232 | 0.72376 | 1.4778 | 0.61747 | -1.1959 | 0.034252 |  |  | 47 | 1 | 84 | 1599 | 487.3752 | 1 | 1099 | -0.017149 | 0.00080854 | -0.01634 | -0.00634 | 768.5609 | Exfl | 768.5609 | 0.1616 | 13353.4119 | 2490.1375
| Section >> |  | 6-Htl | Flrs/S | 25 | Section Ht (ft) |  | 250 | Per-L | 475.5993 | Floor-Envel-Area (ft2) |  |  | 4755.9928 | S-Flr-Area (ft2) |  | 450000 | Wndw Area (%) |  | 45 |  | Inside-Outside (PI-PO) |  |  | 0.01 | Leakg Flow Cf |  | 0.65 |  |  | Section >> |  | 6-Htl | Flrs/S | 25 | 12 | Envel Leakg A |  | 40.4259 | Appr. Sctn-Infltr (cfm) |  |  | 11481.7225 | Appr. Sctn Infltr (tons) |  |  | 26127.1269
| 46 | 25 | 83 | 1589 | 484.3272 | 95.6408 | 28.3197 | 384.3388 | 13.8715 | 13.3193 | 91.1232 | 72.4517 | 63.8319 | 0.013874 | 41.7723 | 14.9985 | 0.066673 | 37.1511 | 550.8232 | 532.1517 |  | 0.3952 | 0.01824 | 0.72457 | 1.4794 | 0.61792 | -1.1952 | 0.034279 |  |  | 46 | 25 | 83 | 1589 | 484.3272 | 1 | 1089 | -0.016805 | 0.00079958 | -0.016005 | -0.0060052 | 669.1578 | Exfl | 669.1578 | 0.1407 | 11652.0534 | 2168.0713
| 46 | 24 | 82 | 1579 | 481.2792 | 95.6757 | 28.3301 | 384.4792 | 13.8766 | 13.2429 | 91.1588 | 72.4751 | 63.8524 | 0.013879 | 41.7559 | 14.9941 | 0.066693 | 37.1654 | 550.8588 | 532.1751 |  | 0.39551 | 0.018248 | 0.72537 | 1.481 | 0.61836 | -1.1945 | 0.034306 |  |  | 46 | 24 | 82 | 1579 | 481.2792 | 1 | 1079 | -0.016459 | 0.00079067 | -0.015668 | -0.0056684 | 650.0284 | Exfl | 650.0284 | 0.13668 | 11343.946 | 2106.0922
| 45 | 23 | 81 | 1569 | 478.2312 | 95.7107 | 28.3404 | 384.6197 | 13.8817 | 13.1665 | 91.1944 | 72.4985 | 63.8729 | 0.013884 | 41.7396 | 14.9897 | 0.066712 | 37.1797 | 550.8944 | 532.1985 |  | 0.39583 | 0.018256 | 0.72618 | 1.4827 | 0.61881 | -1.1938 | 0.034333 |  |  | 45 | 23 | 81 | 1569 | 478.2312 | 1 | 1069 | -0.016112 | 0.0007818 | -0.01533 | -0.0053297 | 630.2146 | Exfl | 630.2146 | 0.13251 | 11022.3959 | 2041.8953
| 44 | 21 | 79 | 1549 | 472.1352 | 95.7806 | 28.3611 | 384.9007 | 13.8918 | 13.0138 | 91.2656 | 72.5453 | 63.9139 | 0.013894 | 41.7069 | 14.981 | 0.066751 | 37.2084 | 550.9656 | 532.2453 |  | 0.39645 | 0.018272 | 0.72779 | 1.486 | 0.6197 | -1.1923 | 0.034387 |  |  | 44 | 21 | 79 | 1549 | 472.1352 | 1 | 1049 | -0.015411 | 0.00076421 | -0.014646 | -0.0046463 | 588.2545 | Exfl | 588.2545 | 0.12369 | 10333.7511 | 1905.9444
| 43 | 20 | 78 | 1539 | 469.0872 | 95.8156 | 28.3715 | 385.0413 | 13.8969 | 12.9374 | 91.3012 | 72.5687 | 63.9344 | 0.013899 | 41.6906 | 14.9766 | 0.066771 | 37.2227 | 551.0012 | 532.2687 |  | 0.39676 | 0.01828 | 0.7286 | 1.4876 | 0.62015 | -1.1916 | 0.034414 |  |  | 43 | 20 | 78 | 1539 | 469.0872 | 1 | 1039 | -0.015057 | 0.00075548 | -0.014302 | -0.0043017 | 565.9352 | Exfl | 565.9352 | 0.11899 | 9963.4329 | 1833.6302
| 42 | 18 | 76 | 1519 | 462.9912 | 95.8856 | 28.3922 | 385.3227 | 13.907 | 12.7846 | 91.3724 | 72.6155 | 63.9754 | 0.013909 | 41.6581 | 14.9678 | 0.06681 | 37.2513 | 551.0724 | 532.3155 |  | 0.39739 | 0.018296 | 0.73022 | 1.4909 | 0.62104 | -1.1902 | 0.034468 |  |  | 42 | 18 | 76 | 1519 | 462.9912 | 1 | 1019 | -0.014345 | 0.00073818 | -0.013607 | -0.0036065 | 518.0419 | Exfl | 518.0419 | 0.10892 | 9160.0941 | 1678.4558
| 41 | 16 | 74 | 1499 | 456.8952 | 95.9557 | 28.413 | 385.6042 | 13.9172 | 12.6318 | 91.4436 | 72.6623 | 64.0165 | 0.013919 | 41.6256 | 14.9591 | 0.066849 | 37.28 | 551.1436 | 532.3623 |  | 0.39802 | 0.018312 | 0.73185 | 1.4943 | 0.62194 | -1.1887 | 0.034523 |  |  | 41 | 16 | 74 | 1499 | 456.8952 | 1 | 999 | -0.013625 | 0.00072106 | -0.012904 | -0.0029035 | 464.6792 | Exfl | 464.6792 | 0.097704 | 8252.2579 | 1505.5605
| 40 | 13 | 71 | 1469 | 447.7512 | 96.0608 | 28.4441 | 386.0267 | 13.9324 | 12.4026 | 91.5504 | 72.7325 | 64.0781 | 0.013934 | 41.577 | 14.9459 | 0.066908 | 37.3229 | 551.2504 | 532.4325 |  | 0.39896 | 0.018336 | 0.73429 | 1.4992 | 0.62328 | -1.1866 | 0.034604 |  |  | 40 | 13 | 71 | 1469 | 447.7512 | 1 | 969 | -0.01253 | 0.00069574 | -0.011834 | -0.0018341 | 369.1619 | Exfl | 369.1619 | 0.07762 | 6598.5431 | 1196.0845
| 39 | 10 | 68 | 1439 | 438.6072 | 96.1661 | 28.4753 | 386.4496 | 13.9477 | 12.1734 | 91.6572 | 72.8027 | 64.1396 | 0.01395 | 41.5284 | 14.9328 | 0.066967 | 37.366 | 551.3572 | 532.5027 |  | 0.39991 | 0.01836 | 0.73673 | 1.5042 | 0.62463 | -1.1844 | 0.034686 |  |  | 39 | 10 | 68 | 1439 | 438.6072 | 1 | 939 | -0.011418 | 0.00067086 | -0.010747 | -0.00074696 | 235.4827 | Exfl | 235.4827 | 0.049513 | 4236.27 | 762.9638
| 38 | 7 | 65 | 1409 | 429.4632 | 96.2714 | 28.5064 | 386.8729 | 13.963 | 11.9442 | 91.764 | 72.8729 | 64.2013 | 0.013965 | 41.48 | 14.9197 | 0.067025 | 37.409 | 551.464 | 532.5729 |  | 0.40086 | 0.018384 | 0.73919 | 1.5093 | 0.62598 | -1.1823 | 0.034768 |  |  | 38 | 7 | 65 | 1409 | 429.4632 | 1 | 909 | -0.010288 | 0.0006464 | -0.0096419 | 0.00035807 | 162.9679 | Infl | -162.9679 | -0.034266 | -2950.5463 | -528.016
| 37 | 5 | 63 | 1389 | 423.3672 | 96.3417 | 28.5273 | 387.1553 | 13.9732 | 11.7914 | 91.8352 | 72.9197 | 64.2423 | 0.013975 | 41.4478 | 14.911 | 0.067064 | 37.4377 | 551.5352 | 532.6197 |  | 0.40149 | 0.0184 | 0.74083 | 1.5126 | 0.62688 | -1.1808 | 0.034822 |  |  | 37 | 5 | 63 | 1389 | 423.3672 | 1 | 889 | -0.0095257 | 0.00063034 | -0.0088953 | 0.0011047 | 286.1626 | Infl | -286.1626 | -0.060169 | -5203.0013 | -927.167
| 36 | 3 | 61 | 1369 | 417.2712 | 96.412 | 28.5481 | 387.4379 | 13.9834 | 11.6387 | 91.9064 | 72.9665 | 64.2834 | 0.013985 | 41.4157 | 14.9023 | 0.067104 | 37.4664 | 551.6064 | 532.6665 |  | 0.40212 | 0.018416 | 0.74247 | 1.516 | 0.62778 | -1.1794 | 0.034877 |  |  | 36 | 3 | 61 | 1369 | 417.2712 | 1 | 869 | -0.0087552 | 0.00061447 | -0.0081407 | 0.0018593 | 371.1401 | Infl | -371.1401 | -0.078036 | -6776.599 | -1202.494
| 35 | 1 | 59 | 1349 | 411.1752 | 96.4823 | 28.5689 | 387.7207 | 13.9936 | 11.4859 | 91.9776 | 73.0133 | 64.3245 | 0.013995 | 41.3836 | 14.8936 | 0.067143 | 37.4952 | 551.6776 | 532.7133 |  | 0.40276 | 0.018432 | 0.74412 | 1.5193 | 0.62869 | -1.1779 | 0.034932 |  |  | 35 | 1 | 59 | 1349 | 411.1752 | 1 | 849 | -0.007977 | 0.00059879 | -0.0073782 | 0.0026218 | 440.5977 | Infl | -440.5977 | -0.092641 | -8078.6964 | -1427.5366
| Section >> |  | 5-Srv | Flrs/S | 5 | Section Ht (ft) |  | 75 | Per-L | 640 | Floor-Envel-Area (ft2) |  |  | 9600 | S-Flr-Area (ft2) |  | 120000 | Wndw Area (%) |  | 60 |  | Inside-Outside (PI-PO) |  |  | 0.02 | Leakg Flow Cf |  | 0.65 |  |  | Section >> |  | 5-Srv | Flrs/S | 5 | 5 | Envel Leakg A |  | 9.6576 | Appr. Sctn-Infltr (cfm) |  |  | 1222.4838 | Appr. Sctn Infltr (tons) |  |  | -3960.8476
| 34 | 0 | XX | XX | XX | XX | XX | XX | XX | XX | [11 empty] | XX | XX | XX | XX | XX | XX | XX |  |  | 34 | 0 | XX | XX | XX | 0 | XX | XX | XX | XX | XX | 0 | XX | 0 | XX | XX | 0 | bar: DB to Twb
| 33 | 5 | 58 | 1339 | 408.1272 | 96.5175 | 28.5793 | 387.8621 | 13.9987 | 11.4095 | 92.0132 | 73.0367 | 64.3451 | 0.014 | 41.3676 | 14.8893 | 0.067163 | 37.5095 | 551.7132 | 532.7367 |  | 0.40307 | 0.01844 | 0.74494 | 1.521 | 0.62914 | -1.1772 | 0.034959 |  |  | 33 | 5 | 58 | 1339 | 408.1272 | 1 | 839 | -0.0075849 | 0.00059102 | -0.0069939 | 0.013006 | 234.4008 | Infl | -234.4008 | -0.024417 | -4306.9294 | -759.4584
| 32 | 4 | 57 | 1324 | 403.5552 | 96.5704 | 28.595 | 388.0743 | 14.0063 | 11.2949 | 92.0666 | 73.0718 | 64.3759 | 0.014008 | 41.3436 | 14.8827 | 0.067192 | 37.5311 | 551.7666 | 532.7718 |  | 0.40355 | 0.018452 | 0.74618 | 1.5235 | 0.62982 | -1.1761 | 0.035 |  |  | 32 | 4 | 57 | 1324 | 403.5552 | 1 | 824 | -0.0069932 | 0.00057947 | -0.0064137 | 0.013586 | 239.5192 | Infl | -239.5192 | -0.02495 | -4414.7904 | -776.0422
| 31 | 3 | 56 | 1309 | 398.9832 | 96.6232 | 28.6106 | 388.2866 | 14.014 | 11.1803 | 92.12 | 73.1069 | 64.4068 | 0.014016 | 41.3196 | 14.8762 | 0.067221 | 37.5527 | 551.82 | 532.8069 |  | 0.40403 | 0.018464 | 0.74742 | 1.5261 | 0.6305 | -1.1751 | 0.035041 |  |  | 31 | 3 | 56 | 1309 | 398.9832 | 1 | 809 | -0.0063971 | 0.00056802 | -0.0058291 | 0.014171 | 244.565 | Infl | -244.565 | -0.025476 | -4521.8993 | -792.3907
| 30 | 2 | 55 | 1294 | 394.4112 | 96.676 | 28.6263 | 388.4991 | 14.0217 | 11.0657 | 92.1734 | 73.142 | 64.4376 | 0.014023 | 41.2957 | 14.8697 | 0.067251 | 37.5742 | 551.8734 | 532.842 |  | 0.40451 | 0.018476 | 0.74866 | 1.5286 | 0.63118 | -1.174 | 0.035083 |  |  | 30 | 2 | 55 | 1294 | 394.4112 | 1 | 794 | -0.0057965 | 0.00055668 | -0.0052399 | 0.01476 | 249.5427 | Infl | -249.5427 | -0.025994 | -4628.3253 | -808.5183
| 29 | 1 | 54 | 1279 | 389.8392 | 96.7289 | 28.6419 | 388.7116 | 14.0293 | 10.9511 | 92.2268 | 73.1771 | 64.4685 | 0.014031 | 41.2717 | 14.8632 | 0.06728 | 37.5958 | 551.9268 | 532.8771 |  | 0.40498 | 0.018488 | 0.74991 | 1.5311 | 0.63187 | -1.1729 | 0.035124 |  |  | 29 | 1 | 54 | 1279 | 389.8392 | 1 | 779 | -0.0051916 | 0.00054545 | -0.0046462 | 0.015354 | 254.4561 | Infl | -254.4561 | -0.026506 | -4734.131 | -824.4379
| Section >> |  | 4-Ofc | Flrs/S | 41 | Section Ht (ft) |  | 560 | Per-L | 720 | Floor-Envel-Area (ft2) |  |  | 9720 | S-Flr-Area (ft2) |  | 1262800 | Wndw Area (%) |  | 65 |  | Inside-Outside (PI-PO) |  |  | 0.025 | Leakg Flow Cf |  | 0.65 |  |  | Section >> |  | 4-Ofc | Flrs/S | 41 | 15 | Envel Leakg A |  | 7.844 | Appr. Sctn-Infltr (cfm) |  |  | 12107.5319 | Appr. Sctn Infltr (tons) |  |  | -39228.4035
| 28 | 41 | 53 | 1257.5 | 383.286 | 96.8048 | 28.6644 | 389.0163 | 14.0403 | 10.7869 | 92.3033 | 73.2275 | 64.5127 | 0.014042 | 41.2375 | 14.8539 | 0.067323 | 37.6267 | 552.0033 | 532.9275 |  | 0.40567 | 0.018506 | 0.75169 | 1.5348 | 0.63284 | -1.1713 | 0.035183 |  |  | 28 | 41 | 53 | 1257.5 | 383.286 | 1 | 757.5 | -0.0043169 | 0.00052954 | -0.0037873 | 0.021213 | 242.8491 | Infl | -242.8491 | -0.024984 | -4538.259 | -786.8312
| 27 | 39 | 51 | 1230.5 | 375.0564 | 96.9001 | 28.6926 | 389.3993 | 14.0542 | 10.5806 | 92.3994 | 73.2906 | 64.5683 | 0.014056 | 41.1946 | 14.8421 | 0.067376 | 37.6656 | 552.0994 | 532.9906 |  | 0.40653 | 0.018527 | 0.75394 | 1.5394 | 0.63408 | -1.1694 | 0.035258 |  |  | 27 | 39 | 51 | 1230.5 | 375.0564 | 1 | 730.5 | -0.0032055 | 0.00050988 | -0.0026956 | 0.022304 | 248.9219 | Infl | -248.9219 | -0.025609 | -4677.5836 | -806.5068
| 26 | 35 | 47 | 1176.5 | 358.5972 | 97.0909 | 28.7491 | 390.1663 | 14.0818 | 10.1681 | 92.5917 | 73.417 | 64.6795 | 0.014083 | 41.1091 | 14.8188 | 0.067482 | 37.7434 | 552.2917 | 533.117 |  | 0.40826 | 0.018571 | 0.75845 | 1.5486 | 0.63655 | -1.1655 | 0.035407 |  |  | 26 | 35 | 47 | 1176.5 | 358.5972 | 1 | 676.5 | -0.00093964 | 0.00047164 | -0.00046799 | 0.024532 | 260.8508 | Infl | -260.8508 | -0.026836 | -4955.9016 | -845.1564
| 25 | 31 | 43 | 1122.5 | 342.138 | 97.2821 | 28.8057 | 390.9344 | 14.1096 | 9.7555 | 92.7839 | 73.5434 | 64.7907 | 0.014111 | 41.024 | 14.7955 | 0.067588 | 37.8213 | 552.4839 | 533.2433 |  | 0.41 | 0.018615 | 0.76299 | 1.5578 | 0.63903 | -1.1616 | 0.035557 |  |  | 25 | 31 | 43 | 1122.5 | 342.138 | 1 | 622.5 | 0.0013839 | 0.00043483 | 0.0018187 | 0.026819 | 272.5224 | Infl | -272.5224 | -0.028037 | -5234.2328 | -882.9727
| 24 | 28 | 40 | 1082 | 329.7936 | 97.4256 | 28.8482 | 391.5113 | 14.1304 | 9.4461 | 92.9281 | 73.6381 | 64.8742 | 0.014132 | 40.9604 | 14.778 | 0.067668 | 37.8798 | 552.6281 | 533.3381 |  | 0.41131 | 0.018647 | 0.7664 | 1.5648 | 0.6409 | -1.1587 | 0.03567 |  |  | 24 | 28 | 40 | 1082 | 329.7936 | 1 | 582 | 0.0031645 | 0.00040817 | 0.0035726 | 0.028573 | 281.1267 | Infl | -281.1267 | -0.028923 | -5443.2673 | -910.8506
| 23 | 26 | 38 | 1055 | 321.564 | 97.5214 | 28.8766 | 391.8963 | 14.1443 | 9.2399 | 93.0242 | 73.7013 | 64.9299 | 0.014146 | 40.9181 | 14.7664 | 0.067721 | 37.9188 | 552.7242 | 533.4013 |  | 0.41218 | 0.018669 | 0.76869 | 1.5695 | 0.64214 | -1.1568 | 0.035745 |  |  | 23 | 26 | 38 | 1055 | 321.564 | 1 | 555 | 0.0043697 | 0.00039085 | 0.0047605 | 0.029761 | 286.7981 | Infl | -286.7981 | -0.029506 | -5582.8515 | -929.226
| 22 | 24 | 36 | 1028 | 313.3344 | 97.6173 | 28.905 | 392.2816 | 14.1582 | 9.0336 | 93.1203 | 73.7645 | 64.9856 | 0.01416 | 40.876 | 14.7547 | 0.067775 | 37.9579 | 552.8203 | 533.4645 |  | 0.41306 | 0.018691 | 0.77098 | 1.5742 | 0.64339 | -1.1548 | 0.03582 |  |  | 22 | 24 | 36 | 1028 | 313.3344 | 1 | 528 | 0.0055894 | 0.00037388 | 0.0059633 | 0.030963 | 292.4213 | Infl | -292.4213 | -0.030084 | -5722.6682 | -947.4449
| 21 | 25 | 37 | 1041.5 | 317.4492 | 97.5694 | 28.8908 | 392.0889 | 14.1512 | 9.1367 | 93.0723 | 73.7329 | 64.9577 | 0.014153 | 40.897 | 14.7606 | 0.067748 | 37.9383 | 552.7723 | 533.4329 |  | 0.41262 | 0.01868 | 0.76984 | 1.5718 | 0.64277 | -1.1558 | 0.035783 |  |  | 21 | 25 | 37 | 1041.5 | 317.4492 | 1 | 541.5 | 0.0049777 | 0.00038232 | 0.00536 | 0.03036 | 289.6156 | Infl | -289.6156 | -0.029796 | -5652.7283 | -938.3544
| 20 | 22 | 34 | 1001 | 305.1048 | 97.7133 | 28.9334 | 392.6672 | 14.1721 | 8.8273 | 93.2164 | 73.8277 | 65.0413 | 0.014174 | 40.8339 | 14.7431 | 0.067828 | 37.9969 | 552.9164 | 533.5277 |  | 0.41394 | 0.018713 | 0.77328 | 1.5789 | 0.64465 | -1.1529 | 0.035896 |  |  | 20 | 22 | 34 | 1001 | 305.1048 | 1 | 501 | 0.0068238 | 0.00035729 | 0.007181 | 0.032181 | 297.9988 | Infl | -297.9988 | -0.030658 | -5862.7561 | -965.5162
| 19 | 19 | 31 | 960.5 | 292.7604 | 97.8573 | 28.9761 | 393.2462 | 14.193 | 8.518 | 93.3606 | 73.9224 | 65.1249 | 0.014195 | 40.7709 | 14.7258 | 0.067908 | 38.0555 | 553.0606 | 533.6224 |  | 0.41525 | 0.018746 | 0.77674 | 1.5859 | 0.64653 | -1.15 | 0.03601 |  |  | 19 | 19 | 31 | 960.5 | 292.7604 | 1 | 460.5 | 0.0087027 | 0.00033307 | 0.0090358 | 0.034036 | 306.2852 | Infl | -306.2852 | -0.031511 | -6073.4732 | -992.3641
| 18 | 16 | 28 | 920 | 280.416 | 98.0016 | 29.0188 | 393.8258 | 14.2139 | 8.2086 | 93.5048 | 74.0172 | 65.2085 | 0.014216 | 40.7082 | 14.7084 | 0.067988 | 38.1142 | 553.2048 | 533.7172 |  | 0.41658 | 0.018779 | 0.78021 | 1.593 | 0.64842 | -1.147 | 0.036124 |  |  | 18 | 16 | 28 | 920 | 280.416 | 1 | 420 | 0.010615 | 0.00030968 | 0.010924 | 0.035924 | 314.4823 | Infl | -314.4823 | -0.032354 | -6284.9875 | -1018.9228
| 17 | 13 | 25 | 879.5 | 268.0716 | 98.146 | 29.0615 | 394.4062 | 14.2349 | 7.8992 | 93.649 | 74.112 | 65.2922 | 0.014237 | 40.6457 | 14.6911 | 0.068069 | 38.1729 | 553.349 | 533.812 |  | 0.4179 | 0.018812 | 0.78369 | 1.6001 | 0.65032 | -1.1441 | 0.036238 |  |  | 17 | 13 | 25 | 879.5 | 268.0716 | 1 | 379.5 | 0.01256 | 0.00028711 | 0.012847 | 0.037847 | 322.597 | Infl | -322.597 | -0.033189 | -6497.3943 | -1045.2144
| 16 | 10 | 22 | 839 | 255.7272 | 98.2906 | 29.1043 | 394.9873 | 14.2558 | 7.5898 | 93.7932 | 74.2067 | 65.3759 | 0.014258 | 40.5834 | 14.6738 | 0.068149 | 38.2317 | 553.4932 | 533.9067 |  | 0.41923 | 0.018845 | 0.78719 | 1.6073 | 0.65222 | -1.1412 | 0.036352 |  |  | 16 | 10 | 22 | 839 | 255.7272 | 1 | 339 | 0.014538 | 0.00026538 | 0.014803 | 0.039803 | 330.6354 | Infl | -330.6354 | -0.034016 | -6710.7781 | -1071.2586
| 15 | 7 | 19 | 798.5 | 243.3828 | 98.4354 | 29.1472 | 395.569 | 14.2768 | 7.2804 | 93.9373 | 74.3015 | 65.4597 | 0.014279 | 40.5213 | 14.6565 | 0.068229 | 38.2905 | 553.6373 | 534.0015 |  | 0.42056 | 0.018878 | 0.7907 | 1.6144 | 0.65412 | -1.1383 | 0.036467 |  |  | 15 | 7 | 19 | 798.5 | 243.3828 | 1 | 298.5 | 0.016549 | 0.00024447 | 0.016794 | 0.041794 | 338.6028 | Infl | -338.6028 | -0.034836 | -6925.2147 | -1097.073
| 14 | 5 | 17 | 771.5 | 235.1532 | 98.532 | 29.1758 | 395.9572 | 14.2908 | 7.0741 | 94.0335 | 74.3647 | 65.5155 | 0.014293 | 40.48 | 14.645 | 0.068283 | 38.3297 | 553.7335 | 534.0647 |  | 0.42146 | 0.0189 | 0.79305 | 1.6192 | 0.6554 | -1.1363 | 0.036544 |  |  | 14 | 5 | 17 | 771.5 | 235.1532 | 1 | 271.5 | 0.017909 | 0.00023099 | 0.01814 | 0.04314 | 343.8774 | Infl | -343.8774 | -0.035378 | -7068.791 | -1114.1628
| 13 | 3 | 15 | 744.5 | 226.9236 | 98.6287 | 29.2044 | 396.3457 | 14.3049 | 6.8678 | 94.1296 | 74.4279 | 65.5714 | 0.014307 | 40.4388 | 14.6335 | 0.068336 | 38.369 | 553.8296 | 534.1279 |  | 0.42235 | 0.018923 | 0.7954 | 1.624 | 0.65667 | -1.1344 | 0.036621 |  |  | 13 | 3 | 15 | 744.5 | 226.9236 | 1 | 244.5 | 0.019283 | 0.00021789 | 0.019501 | 0.044501 | 349.124 | Infl | -349.124 | -0.035918 | -7212.8836 | -1131.1618
| 12 | 1 | 13 | 717.5 | 218.694 | 98.7254 | 29.2331 | 396.7346 | 14.3189 | 6.6616 | 94.2257 | 74.4911 | 65.6273 | 0.014321 | 40.3977 | 14.622 | 0.06839 | 38.4082 | 553.9257 | 534.1911 |  | 0.42324 | 0.018945 | 0.79776 | 1.6288 | 0.65795 | -1.1324 | 0.036698 |  |  | 12 | 1 | 13 | 717.5 | 218.694 | 1 | 217.5 | 0.020673 | 0.00020516 | 0.020878 | 0.045878 | 354.3439 | Infl | -354.3439 | -0.036455 | -7357.5099 | -1148.0742
| Section >> |  | 3-Fin | Flrs/S | 6 | Section Ht (ft) |  | 90 | Per-L | 800 | Floor-Envel-Area (ft2) |  |  | 12000 | S-Flr-Area (ft2) |  | 230400 | Wndw Area (%) |  | 65 |  | Inside-Outside (PI-PO) |  |  | 0.025 | Leakg Flow Cf |  | 0.65 |  |  | Section >> |  | 3-Fin | Flrs/S | 6 | 4 | Envel Leakg A |  | 9.684 | Appr. Sctn-Infltr (cfm) |  |  | 2675.9955 | Appr. Sctn Infltr (tons) |  |  | -8670.2255
| 11 | 6 | 12 | 704 | 214.5792 | 98.7738 | 29.2474 | 396.9291 | 14.3259 | 6.5584 | 94.2738 | 74.5226 | 65.6552 | 0.014328 | 40.3772 | 14.6163 | 0.068417 | 38.4279 | 553.9738 | 534.2226 |  | 0.42369 | 0.018956 | 0.79894 | 1.6313 | 0.65859 | -1.1315 | 0.036736 |  |  | 11 | 6 | 12 | 704 | 214.5792 | 1 | 204 | 0.021373 | 0.00019893 | 0.021572 | 0.046572 | 440.6718 | Infl | -440.6718 | -0.036723 | -9172.8742 | -1427.7765
| 10 | 5 | 11 | 689 | 210.0072 | 98.8276 | 29.2634 | 397.1453 | 14.3337 | 6.4439 | 94.3272 | 74.5577 | 65.6863 | 0.014336 | 40.3544 | 14.6099 | 0.068447 | 38.4497 | 554.0272 | 534.2577 |  | 0.42419 | 0.018968 | 0.80026 | 1.6339 | 0.65931 | -1.1304 | 0.036779 |  |  | 10 | 5 | 11 | 689 | 210.0072 | 1 | 189 | 0.022156 | 0.00019213 | 0.022348 | 0.047348 | 444.2296 | Infl | -444.2296 | -0.037019 | -9272.5523 | -1439.3039
| 9 | 4 | 10 | 674 | 205.4352 | 98.8815 | 29.2793 | 397.3617 | 14.3415 | 6.3293 | 94.3806 | 74.5928 | 65.7173 | 0.014344 | 40.3317 | 14.6036 | 0.068476 | 38.4716 | 554.0806 | 534.2928 |  | 0.42469 | 0.01898 | 0.80158 | 1.6366 | 0.66002 | -1.1293 | 0.036822 |  |  | 9 | 4 | 10 | 674 | 205.4352 | 1 | 174 | 0.022943 | 0.00018544 | 0.023128 | 0.048128 | 447.7781 | Infl | -447.7781 | -0.037315 | -9372.4458 | -1450.8011
| 8 | 3 | 9 | 659 | 200.8632 | 98.9353 | 29.2952 | 397.5781 | 14.3493 | 6.2147 | 94.434 | 74.6279 | 65.7484 | 0.014352 | 40.309 | 14.5972 | 0.068506 | 38.4934 | 554.134 | 534.3279 |  | 0.42519 | 0.018993 | 0.8029 | 1.6393 | 0.66073 | -1.1282 | 0.036865 |  |  | 8 | 3 | 9 | 659 | 200.8632 | 1 | 159 | 0.023734 | 0.00017886 | 0.023913 | 0.048913 | 451.3175 | Infl | -451.3175 | -0.03761 | -9472.5577 | -1462.2688
| 7 | 2 | 8 | 644 | 196.2912 | 98.9892 | 29.3112 | 397.7946 | 14.3572 | 6.1001 | 94.4874 | 74.663 | 65.7795 | 0.01436 | 40.2863 | 14.5908 | 0.068536 | 38.5153 | 554.1874 | 534.363 |  | 0.42568 | 0.019005 | 0.80422 | 1.642 | 0.66145 | -1.1271 | 0.036908 |  |  | 7 | 2 | 8 | 644 | 196.2912 | 1 | 144 | 0.024531 | 0.0001724 | 0.024703 | 0.049703 | 454.8481 | Infl | -454.8481 | -0.037904 | -9572.8909 | -1473.7077
| 6 | 1 | 7 | 629 | 191.7192 | 99.0431 | 29.3272 | 398.0112 | 14.365 | 5.9855 | 94.5408 | 74.6981 | 65.8106 | 0.014368 | 40.2636 | 14.5845 | 0.068566 | 38.5371 | 554.2408 | 534.3981 |  | 0.42618 | 0.019017 | 0.80554 | 1.6447 | 0.66216 | -1.1261 | 0.036951 |  |  | 6 | 1 | 7 | 629 | 191.7192 | 1 | 129 | 0.025332 | 0.00016606 | 0.025498 | 0.050498 | 458.3699 | Infl | -458.3699 | -0.038197 | -9673.4483 | -1485.1185
| Section >> |  | 2-Rtl | Flrs/S | 4 | Section Ht (ft) |  | 74 | Per-L | 838.8783 | Floor-Envel-Area (ft2) |  |  | 15099.809 | S-Flr-Area (ft2) |  | 224000 | Wndw Area (%) |  | 50 |  | Inside-Outside (PI-PO) |  |  | 0.015 | Leakg Flow Cf |  | 0.65 |  |  | Section >> |  | 2-Rtl | Flrs/S | 4 | 3 | Envel Leakg A |  | 113.2486 | Appr. Sctn-Infltr (cfm) |  |  | 19849.0395 | Appr. Sctn Infltr (tons) |  |  | -64310.888
| 5 | 3 | 5 | 594 | 181.0512 | 99.169 | 29.3644 | 398.5171 | 14.3832 | 5.7181 | 94.6654 | 74.78 | 65.8831 | 0.014386 | 40.2109 | 14.5697 | 0.068636 | 38.5882 | 554.3654 | 534.48 |  | 0.42735 | 0.019046 | 0.80864 | 1.6511 | 0.66384 | -1.1235 | 0.037051 |  |  | 5 | 3 | 5 | 594 | 181.0512 | 1 | 94 | 0.027219 | 0.00015171 | 0.027371 | 0.042371 | 4907.601 | Infl | -4907.601 | -0.32501 | -104230.5188 | -15900.6271
| 4 | 2 | 4 | 576 | 175.5648 | 99.2338 | 29.3836 | 398.7774 | 14.3926 | 5.5806 | 94.7294 | 74.8222 | 65.9204 | 0.014396 | 40.1838 | 14.5621 | 0.068672 | 38.6144 | 554.4294 | 534.5222 |  | 0.42796 | 0.019061 | 0.81023 | 1.6543 | 0.6647 | -1.1222 | 0.037103 |  |  | 4 | 2 | 4 | 576 | 175.5648 | 1 | 76 | 0.028199 | 0.00014457 | 0.028344 | 0.043344 | 4962.348 | Infl | -4962.348 | -0.32864 | -105736.6956 | -16078.0076
| 3 | 1 | 3 | 558 | 170.0784 | 99.2986 | 29.4028 | 399.0379 | 14.402 | 5.4431 | 94.7935 | 74.8643 | 65.9577 | 0.014405 | 40.1568 | 14.5544 | 0.068708 | 38.6407 | 554.4935 | 534.5643 |  | 0.42856 | 0.019076 | 0.81183 | 1.6576 | 0.66556 | -1.1209 | 0.037155 |  |  | 3 | 1 | 3 | 558 | 170.0784 | 1 | 58 | 0.029186 | 0.00013761 | 0.029324 | 0.044324 | 5016.8306 | Infl | -5016.8306 | -0.33224 | -107244.7967 | -16254.5313
| Section >> |  | 1-Grd | Flrs/S | 2 | Section Ht (ft) |  | 40 | Per-L | 982.3936 | Floor-Envel-Area (ft2) |  |  | 19647.8729 | S-Flr-Area (ft2) |  | 153600 | Wndw Area (%) |  | 60 |  | Inside-Outside (PI-PO) |  |  | 0.005 | Leakg Flow Cf |  | 0.65 |  |  | Section >> |  | 1-Grd | Flrs/S | 2 | 2 | Envel Leakg A |  | 186.6548 | Appr. Sctn-Infltr (cfm) |  |  | 15092.8265 | Appr. Sctn Infltr (tons) |  |  | -48900.7578
| 2 | 2 | 2 | 520 | 158.496 | 99.4355 | 29.4434 | 399.5882 | 14.4219 | 5.1528 | 94.9288 | 74.9532 | 66.0366 | 0.014425 | 40.0998 | 14.5384 | 0.068783 | 38.6962 | 554.6288 | 534.6532 |  | 0.42983 | 0.019107 | 0.81521 | 1.6645 | 0.66739 | -1.1182 | 0.037264 |  |  | 2 | 2 | 2 | 520 | 158.496 | 1 | 20 | 0.031292 | 0.00012346 | 0.031416 | 0.036416 | 7490.6939 | Infl | -7490.6939 | -0.38125 | -161222.9839 | -24269.8482
| 1 | 1 | 1 | 500 | 152.4 | 99.5077 | 29.4647 | 399.8781 | 14.4324 | 5 | 95 | 75 | 66.0781 | 0.014436 | 40.0699 | 14.53 | 0.068823 | 38.7254 | 554.7 | 534.7 |  | 0.43051 | 0.019124 | 0.817 | 1.6681 | 0.66835 | -1.1168 | 0.037322 |  |  | 1 | 1 | 1 | 500 | 152.4 | 1 | 0 | 0.032413 | 0.00011631 | 0.032529 | 0.037529 | 7602.1326 | Infl | -7602.1326 | -0.38692 | -164206.064 | -24630.9096

## WNTR-Calcs
1 | 5 | 5 | 5 | 6 | 6 | 6 | 6 | 6.5 | 6 | 6 | 6 | 6 | 6 | 7 | 6 | 6 | 7.5 | 7 | 6 | 6 | 7 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 7.5 | 6.5 | 2 | 2 | 5 | 5 | 5 | 6 | 6 |  | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 9 | 6.5 | 6.5 | 7 | 10
| Site Altit |  | 500 | Bldg-H | 1309 | NPL-H | 654.5 | Total Bldg Area |  | 2782800 |  | Total Envl Area |  | 834612.6539 |  | Lkg-A | 3126.9737 | Wnd-Vel Diff |  | 15 |  | Temp Drop with Altitude |  |  | DB | 0.00356 | WB | 0.00234 |  |  | ∆PS = C1*ρO* [ (TO - TI) / TI ] * g * (HNPL - H) | [5 empty] | ∆PS = | Stack Effect Press Diff (in.wg) |  |  |  | PI - PO | Bldg Pressuriz (Indr Press - Outdr Press)
|  |  |  | Alt ref Sea-Lvl |  | Outdr Std. Atm. Press. @ Altit |  |  |  | Wnd V | DB | WB | DP | W | RH | V | d | H | Tdb | Twb |  | Psychrometric Calculations for DP, RH, V, W, H, TR | [8 empty] | Q = Cd * A * ( 2 * ∆P/d )0.5 |  |  |  | TO (OR) , Ti (OR) |  | ∆PW = | Wind Press (in.wg) |  |  | UH = mph |  | ρO = OA dens |  | Coolg/yr = CFM*1.08*CDD
|  |  |  | feet | meters | K-Pa | in.Hg | in.H2O | psi | mph | F | F | F | lbs/b | % | ft3/lb | lbs/ft3 | btu/lb | R | R |  | PWSwb | WSwb | PWSdb | VPs | VPa | a | WSdb |  |  | ∆PW = C2 * s2 * CP * ρO * (UH)2 / 2 | [5 empty] | Q = | Airflow Rate (ft3/sec) |  |  | A = Leakg-A |  | Iniltr SHG/hr = CFM * 1.08 (To-Ti))
| At Sea-Level |  |  | 0 | 0 | 101.325 | 29.9213 | 406.0345 | 14.6546 | 10 | 75 | 62 | 53.2919 | 0.0089201 | 48.1285 | 13.6728 | 0.073138 | 27.7612 | 534.7 | 521.7 |  | 0.27548 | 0.011916 | 0.43051 | 0.87899 | 0.42305 | -1.5741 | 0.018825 |  |  | Convert K-Pa to |  |  | In.Hg | 0.29611 | in.wg | 4.0186 | PSI | 0.14504 | C1 = | 0.000598 | g = | 32.17 | C2 = | 0.013 | Htg-DD | 7981
| Indoor Conditions |  |  | 500 | 152.4 | 99.5077 | 29.3846 | 398.752 | 14.3917 | 10 | 75 | 62 | -24.3284 | 0.00035492 | 100 | 11.2628 | 0.088788 | -4.4266 | 439.7 | 439.7 |  | 0.0082308 | 0.00035592 | 0.0082308 | 0.016805 | 0.016758 | -4.8027 | 0.00035592 |  |  | Convert in.H20 to |  |  | In.Hg | 0.073684 | K-Pa | 0.24885 | PSI | 0.036092 | s = | 0.4 | CF = | 0.65 | CP = | 0.065 | SpHt-A | 0.24
| Level | Sctn | Bldg | Alt ref Sea-Lvl |  | Outdr Std. Atm. Press. @ Altit |  |  |  | Wnd V | DB | WB | DP | W | RH | V | d | H | Tdb | Twb |  | Psychrometric Calculations for DP, RH, V, W, H, TR | [8 empty] | Level | Sctn | Bldg | Alt ref Sea-Lvl |  | Floor | Floor | ∆PS | ∆PW | ∆P = | ∆P + | Leakg Q | Exfl - | Leakage | Q / | SHL | SHL/yr
| ID No. | Flr No. | Flr No. | feet | meters | K-Pa | in.Hg | in.H2O | psi | mph | F | F | F | lbs/b | % | ft3/lb | lbs/ft3 | btu/lb | R | R |  | PWSwb | WSwb | PWSdb | VPs | VPa | a | WSdb |  |  | ID No. | Flr No. | Flr No. | feet | meters | Data | Hght | in.H2O | in.H2O | ∆PW+∆PS | PI - PO | cfm | Infl + | ft3/min | Envel-A | btuh | K-btu
| Section >> |  | 8-din | Flrs/S | 3 | Section Ht (ft) |  | 50 | Per-L | 475.5993 | Floor-Envel-Area (ft2) |  |  | 7133.9892 | S-Flr-Area (ft2) |  | 54000 | Wndw Area (%) |  | 60 |  | Inside-Outside (PI-PO) |  |  | 0.015 | Leakg Flow Cf |  | 0.65 |  |  | Section >> |  | 8-din | Flrs/S | 3 | 2 | Envel Leakg A |  | 46.3709 | Appr. Sctn-Infltr (cfm) |  |  | 12039.8696 | Appr. Sctn Infltr (tons) |  |  | -103777.4156
| 61 | 0 | XX | XX | XX | XX | XX | XX | XX | XX | [11 empty] | XX | XX | XX | XX | XX | XX | XX |  |  | 61 | 0 | XX | XX | XX | 0 | XX | XX | XX | XX | XX | 0 | XX | 0 | XX | XX | 0 | bar: DB to Twb
| 60 | 2 | 101 | 1789 | 545.2872 | 94.944 | 28.1134 | 381.5388 | 13.7705 | 24.7708 | -24.5888 | -23.0163 | -11.3346 | 0.00065954 | 225.3573 | 11.6867 | 0.085567 | -5.2088 | 435.1112 | 436.6837 |  | 0.0070326 | 0.00031781 | 0.0064726 | 0.013216 | 0.029779 | -4.2278 | 0.00029249 |  |  | 60 | 2 | 101 | 1789 | 545.2872 | 1 | 1289 | 0.19453 | 0.0035492 | 0.19808 | 0.21308 | 4035.9389 | Infl | -4035.9389 | -0.56573 | 434089.2347 | -34787.6949
| 59 | 1 | 100 | 1774 | 540.7152 | 94.9961 | 28.1288 | 381.7482 | 13.778 | 24.5989 | -24.5354 | -22.9812 | -11.4451 | 0.00065597 | 223.6315 | 11.6816 | 0.085604 | -5.1997 | 435.1646 | 436.7188 |  | 0.0070456 | 0.00031822 | 0.0064909 | 0.013253 | 0.029635 | -4.2326 | 0.00029316 |  |  | 59 | 1 | 100 | 1774 | 540.7152 | 1 | 1274 | 0.18991 | 0.0035017 | 0.19342 | 0.20842 | 3990.6408 | Infl | -3990.6408 | -0.55938 | 428987.0062 | -34397.2488
| Section >> |  | 7-Apt | Flrs/S | 19 | Section Ht (ft) |  | 170 | Per-L | 475.5993 | Floor-Envel-Area (ft2) |  |  | 4755.9928 | S-Flr-Area (ft2) |  | 288000 | Wndw Area (%) |  | 45 |  | Inside-Outside (PI-PO) |  |  | 0.01 | Leakg Flow Cf |  | 0.65 |  |  | Section >> |  | 7-Apt | Flrs/S | 19 | 9 | Envel Leakg A |  | 45.1819 | Appr. Sctn-Infltr (cfm) |  |  | 68538.017 | Appr. Sctn Infltr (tons) |  |  | -222063.175
| 58 | 0 | XX | XX | XX | XX | XX | XX | XX | XX | [11 empty] | XX | XX | XX | XX | XX | XX | XX |  |  | 58 | 0 | XX | XX | XX | 0 | XX | XX | XX | XX | XX | 0 | XX | 0 | XX | XX | 0 | bar: DB to Twb
| 57 | 19 | 102 | 1779 | 542.2392 | 94.9788 | 28.1237 | 381.6784 | 13.7755 | 24.6562 | -24.5532 | -22.9929 | -11.4082 | 0.00065716 | 224.206 | 11.6833 | 0.085592 | -5.2027 | 435.1468 | 436.7071 |  | 0.0070413 | 0.00031808 | 0.0064848 | 0.013241 | 0.029683 | -4.231 | 0.00029293 |  |  | 57 | 19 | 102 | 1779 | 542.2392 | 1 | 1279 | 0.19145 | 0.0035175 | 0.19497 | 0.20497 | 3856.3273 | Infl | -3856.3273 | -0.81084 | 414622.6685 | -12494.5005
| 56 | 17 | 100 | 1759 | 536.1432 | 95.0483 | 28.1443 | 381.9577 | 13.7856 | 24.427 | -24.482 | -22.9461 | -11.5562 | 0.00065241 | 221.9126 | 11.6766 | 0.085641 | -5.1906 | 435.218 | 436.7539 |  | 0.0070586 | 0.00031863 | 0.0065093 | 0.013291 | 0.02949 | -4.2375 | 0.00029383 |  |  | 56 | 17 | 100 | 1759 | 536.1432 | 1 | 1259 | 0.1853 | 0.0034544 | 0.18875 | 0.19875 | 3796.2681 | Infl | -3796.2681 | -0.79821 | 407873.3355 | -12299.9087
| 55 | 15 | 98 | 1739 | 530.0472 | 95.1178 | 28.1649 | 382.2372 | 13.7957 | 24.1979 | -24.4108 | -22.8993 | -11.7054 | 0.00064767 | 219.6317 | 11.6699 | 0.085691 | -5.1784 | 435.2892 | 436.8007 |  | 0.007076 | 0.00031919 | 0.0065339 | 0.013341 | 0.029298 | -4.2441 | 0.00029472 |  |  | 55 | 15 | 98 | 1739 | 530.0472 | 1 | 1239 | 0.17914 | 0.0033918 | 0.18253 | 0.19253 | 3735.3345 | Infl | -3735.3345 | -0.7854 | 401039.3548 | -12102.4836
| 54 | 13 | 96 | 1719 | 523.9512 | 95.1874 | 28.1855 | 382.5169 | 13.8058 | 23.9687 | -24.3396 | -22.8525 | -11.8558 | 0.00064292 | 217.3629 | 11.6632 | 0.08574 | -5.1663 | 435.3604 | 436.8475 |  | 0.0070934 | 0.00031974 | 0.0065586 | 0.013391 | 0.029104 | -4.2507 | 0.00029562 |  |  | 54 | 13 | 96 | 1719 | 523.9512 | 1 | 1219 | 0.17299 | 0.0033298 | 0.17632 | 0.18632 | 3673.4828 | Infl | -3673.4828 | -0.77239 | 394116.2594 | -11902.0844
| 53 | 11 | 94 | 1699 | 517.8552 | 95.257 | 28.2061 | 382.7967 | 13.8159 | 23.7395 | -24.2684 | -22.8057 | -12.0074 | 0.00063818 | 215.1064 | 11.6565 | 0.085789 | -5.1542 | 435.4316 | 436.8943 |  | 0.0071108 | 0.00032029 | 0.0065833 | 0.013442 | 0.028911 | -4.2574 | 0.00029652 |  |  | 53 | 11 | 94 | 1699 | 517.8552 | 1 | 1199 | 0.16683 | 0.0032683 | 0.1701 | 0.1801 | 3610.6661 | Infl | -3610.6661 | -0.75918 | 387099.2035 | -11698.5581
| 52 | 9 | 92 | 1679 | 511.7592 | 95.3267 | 28.2267 | 383.0767 | 13.826 | 23.5103 | -24.1972 | -22.7589 | -12.1602 | 0.00063343 | 212.862 | 11.6498 | 0.085839 | -5.1421 | 435.5028 | 436.9411 |  | 0.0071283 | 0.00032084 | 0.0066081 | 0.013492 | 0.028717 | -4.2641 | 0.00029742 |  |  | 52 | 9 | 92 | 1679 | 511.7592 | 1 | 1179 | 0.16068 | 0.0032074 | 0.16389 | 0.17389 | 3546.8329 | Infl | -3546.8329 | -0.74576 | 379982.9161 | -11491.7386
| 51 | 7 | 90 | 1659 | 505.6632 | 95.3964 | 28.2474 | 383.3569 | 13.8361 | 23.2811 | -24.126 | -22.7121 | -12.3143 | 0.00062869 | 210.6297 | 11.6431 | 0.085888 | -5.1299 | 435.574 | 436.9879 |  | 0.0071459 | 0.0003214 | 0.0066331 | 0.013543 | 0.028523 | -4.2709 | 0.00029832 |  |  | 51 | 7 | 90 | 1659 | 505.6632 | 1 | 1159 | 0.15453 | 0.0031469 | 0.15768 | 0.16768 | 3481.9274 | Infl | -3481.9274 | -0.73211 | 372761.6472 | -11281.4447
| 50 | 5 | 88 | 1639 | 499.5672 | 95.4662 | 28.268 | 383.6372 | 13.8462 | 23.0519 | -24.0548 | -22.6653 | -12.4696 | 0.00062395 | 208.4095 | 11.6364 | 0.085938 | -5.1178 | 435.6452 | 437.0347 |  | 0.0071634 | 0.00032195 | 0.0066581 | 0.013594 | 0.028329 | -4.2777 | 0.00029923 |  |  | 50 | 5 | 88 | 1639 | 499.5672 | 1 | 1139 | 0.14839 | 0.0030871 | 0.15147 | 0.16147 | 3415.8884 | Infl | -3415.8884 | -0.71823 | 365429.1048 | -11067.4785
| 49 | 3 | 86 | 1619 | 493.4712 | 95.536 | 28.2887 | 383.9177 | 13.8563 | 22.8228 | -23.9836 | -22.6185 | -12.6263 | 0.0006192 | 206.2012 | 11.6297 | 0.085987 | -5.1057 | 435.7164 | 437.0815 |  | 0.007181 | 0.00032251 | 0.0066832 | 0.013645 | 0.028134 | -4.2846 | 0.00030014 |  |  | 49 | 3 | 86 | 1619 | 493.4712 | 1 | 1119 | 0.14224 | 0.0030277 | 0.14527 | 0.15527 | 3348.649 | Infl | -3348.649 | -0.70409 | 357978.382 | -10849.6227
| 48 | 2 | 85 | 1609 | 490.4232 | 95.5709 | 28.299 | 384.058 | 13.8614 | 22.7082 | -23.948 | -22.5951 | -12.705 | 0.00061683 | 205.1015 | 11.6263 | 0.086012 | -5.0996 | 435.752 | 437.1049 |  | 0.0071899 | 0.00032279 | 0.0066957 | 0.013671 | 0.028037 | -4.288 | 0.00030059 |  |  | 48 | 2 | 85 | 1609 | 490.4232 | 1 | 1109 | 0.13917 | 0.0029983 | 0.14217 | 0.15217 | 3314.5563 | Infl | -3314.5563 | -0.69692 | 354206.355 | -10739.1623
| 47 | 1 | 84 | 1599 | 487.3752 | 95.6058 | 28.3094 | 384.1984 | 13.8664 | 22.5936 | -23.9124 | -22.5717 | -12.7842 | 0.00061446 | 204.0047 | 11.623 | 0.086036 | -5.0936 | 435.7876 | 437.1283 |  | 0.0071987 | 0.00032307 | 0.0067083 | 0.013697 | 0.02794 | -4.2915 | 0.00030105 |  |  | 47 | 1 | 84 | 1599 | 487.3752 | 1 | 1099 | 0.1361 | 0.0029689 | 0.13907 | 0.14907 | 3280.1352 | Infl | -3280.1352 | -0.68968 | 350401.869 | -10627.638
| Section >> |  | 6-Htl | Flrs/S | 25 | Section Ht (ft) |  | 250 | Per-L | 475.5993 | Floor-Envel-Area (ft2) |  |  | 4755.9928 | S-Flr-Area (ft2) |  | 450000 | Wndw Area (%) |  | 45 |  | Inside-Outside (PI-PO) |  |  | 0.01 | Leakg Flow Cf |  | 0.65 |  |  | Section >> |  | 6-Htl | Flrs/S | 25 | 12 | Envel Leakg A |  | 40.4259 | Appr. Sctn-Infltr (cfm) |  |  | 64387.1327 | Appr. Sctn Infltr (tons) |  |  | -208614.3101
| 46 | 25 | 83 | 1589 | 484.3272 | 95.6408 | 28.3197 | 384.3388 | 13.8715 | 22.479 | -23.8768 | -22.5483 | -12.8636 | 0.00061209 | 202.911 | 11.6196 | 0.086061 | -5.0875 | 435.8232 | 437.1517 |  | 0.0072075 | 0.00032334 | 0.0067209 | 0.013723 | 0.027842 | -4.295 | 0.0003015 |  |  | 46 | 25 | 83 | 1589 | 484.3272 | 1 | 1089 | 0.13303 | 0.0029397 | 0.13596 | 0.14596 | 2903.7568 | Infl | -2903.7568 | -0.61055 | 310083.4412 | -9408.1721
| 46 | 24 | 82 | 1579 | 481.2792 | 95.6757 | 28.3301 | 384.4792 | 13.8766 | 22.3644 | -23.8412 | -22.5249 | -12.9434 | 0.00060972 | 201.8202 | 11.6163 | 0.086086 | -5.0814 | 435.8588 | 437.1751 |  | 0.0072164 | 0.00032362 | 0.0067336 | 0.013748 | 0.027744 | -4.2985 | 0.00030196 |  |  | 46 | 24 | 82 | 1579 | 481.2792 | 1 | 1079 | 0.12995 | 0.0029107 | 0.13286 | 0.14286 | 2872.3428 | Infl | -2872.3428 | -0.60394 | 306618.3976 | -9306.3907
| 45 | 23 | 81 | 1569 | 478.2312 | 95.7107 | 28.3404 | 384.6197 | 13.8817 | 22.2498 | -23.8056 | -22.5015 | -13.0235 | 0.00060735 | 200.7323 | 11.613 | 0.086111 | -5.0754 | 435.8944 | 437.1985 |  | 0.0072252 | 0.0003239 | 0.0067463 | 0.013774 | 0.027647 | -4.3021 | 0.00030242 |  |  | 45 | 23 | 81 | 1569 | 478.2312 | 1 | 1069 | 0.12688 | 0.0028817 | 0.12977 | 0.13977 | 2840.6054 | Infl | -2840.6054 | -0.59727 | 303121.2589 | -9203.5614
| 44 | 21 | 79 | 1549 | 472.1352 | 95.7806 | 28.3611 | 384.9007 | 13.8918 | 22.0206 | -23.7344 | -22.4547 | -13.1847 | 0.00060261 | 198.5654 | 11.6063 | 0.08616 | -5.0632 | 435.9656 | 437.2453 |  | 0.007243 | 0.00032446 | 0.0067716 | 0.013826 | 0.027451 | -4.3092 | 0.00030334 |  |  | 44 | 21 | 79 | 1549 | 472.1352 | 1 | 1049 | 0.12074 | 0.0028243 | 0.12357 | 0.13357 | 2776.1158 | Infl | -2776.1158 | -0.58371 | 296026.1023 | -8994.6153
| 43 | 20 | 78 | 1539 | 469.0872 | 95.8156 | 28.3715 | 385.0413 | 13.8969 | 21.906 | -23.6988 | -22.4313 | -13.2659 | 0.00060024 | 197.4863 | 11.603 | 0.086185 | -5.0572 | 436.0012 | 437.2687 |  | 0.0072519 | 0.00032474 | 0.0067844 | 0.013852 | 0.027353 | -4.3127 | 0.0003038 |  |  | 43 | 20 | 78 | 1539 | 469.0872 | 1 | 1039 | 0.11767 | 0.0027958 | 0.12047 | 0.13047 | 2743.3399 | Infl | -2743.3399 | -0.57682 | 292425.6198 | -8888.4212
| 42 | 18 | 76 | 1519 | 462.9912 | 95.8856 | 28.3922 | 385.3227 | 13.907 | 21.6769 | -23.6276 | -22.3845 | -13.4292 | 0.0005955 | 195.337 | 11.5963 | 0.086234 | -5.0451 | 436.0724 | 437.3155 |  | 0.0072697 | 0.0003253 | 0.0068099 | 0.013904 | 0.027157 | -4.3199 | 0.00030472 |  |  | 42 | 18 | 76 | 1519 | 462.9912 | 1 | 1019 | 0.11154 | 0.0027392 | 0.11428 | 0.12428 | 2676.6605 | Infl | -2676.6605 | -0.5628 | 285112.1221 | -8672.3799
| 41 | 16 | 74 | 1499 | 456.8952 | 95.9557 | 28.413 | 385.6042 | 13.9172 | 21.4477 | -23.5564 | -22.3377 | -13.5939 | 0.00059076 | 193.1992 | 11.5896 | 0.086284 | -5.0329 | 436.1436 | 437.3623 |  | 0.0072875 | 0.00032586 | 0.0068355 | 0.013957 | 0.026961 | -4.3272 | 0.00030564 |  |  | 41 | 16 | 74 | 1499 | 456.8952 | 1 | 999 | 0.1054 | 0.0026831 | 0.10808 | 0.11808 | 2608.3815 | Infl | -2608.3815 | -0.54844 | 277638.6152 | -8451.156
| 40 | 13 | 71 | 1469 | 447.7512 | 96.0608 | 28.4441 | 386.0267 | 13.9324 | 21.1039 | -23.4496 | -22.2675 | -13.8437 | 0.00058366 | 190.0142 | 11.5796 | 0.086358 | -5.0147 | 436.2504 | 437.4325 |  | 0.0073144 | 0.0003267 | 0.0068741 | 0.014035 | 0.026666 | -4.3382 | 0.00030703 |  |  | 40 | 13 | 71 | 1469 | 447.7512 | 1 | 969 | 0.096201 | 0.0026 | 0.098801 | 0.1088 | 2502.6765 | Infl | -2502.6765 | -0.52622 | 266098.6061 | -8108.6718
| 39 | 10 | 68 | 1439 | 438.6072 | 96.1661 | 28.4753 | 386.4496 | 13.9477 | 20.7601 | -23.3428 | -22.1973 | -14.0967 | 0.00057655 | 186.855 | 11.5697 | 0.086433 | -4.9965 | 436.3572 | 437.5027 |  | 0.0073413 | 0.00032755 | 0.0069128 | 0.014114 | 0.026371 | -4.3493 | 0.00030842 |  |  | 39 | 10 | 68 | 1439 | 438.6072 | 1 | 939 | 0.087005 | 0.0025182 | 0.089524 | 0.099524 | 2392.5617 | Infl | -2392.5617 | -0.50306 | 254114.6139 | -7751.8998
| 38 | 7 | 65 | 1409 | 429.4632 | 96.2714 | 28.5064 | 386.8729 | 13.963 | 20.4163 | -23.236 | -22.1271 | -14.3531 | 0.00056945 | 183.7214 | 11.5597 | 0.086507 | -4.9783 | 436.464 | 437.5729 |  | 0.0073683 | 0.00032839 | 0.0069518 | 0.014194 | 0.026075 | -4.3606 | 0.00030982 |  |  | 38 | 7 | 65 | 1409 | 429.4632 | 1 | 909 | 0.077813 | 0.0024376 | 0.080251 | 0.090251 | 2277.3975 | Infl | -2277.3975 | -0.47885 | 241620.3093 | -7378.7678
| 37 | 5 | 63 | 1389 | 423.3672 | 96.3417 | 28.5273 | 387.1553 | 13.9732 | 20.1872 | -23.1648 | -22.0803 | -14.526 | 0.00056471 | 181.6464 | 11.5531 | 0.086557 | -4.9662 | 436.5352 | 437.6197 |  | 0.0073864 | 0.00032896 | 0.0069779 | 0.014247 | 0.025877 | -4.3682 | 0.00031076 |  |  | 37 | 5 | 63 | 1389 | 423.3672 | 1 | 889 | 0.071687 | 0.0023845 | 0.074072 | 0.084072 | 2197.4255 | Infl | -2197.4255 | -0.46203 | 232966.7203 | -7119.6587
| 36 | 3 | 61 | 1369 | 417.2712 | 96.412 | 28.5481 | 387.4379 | 13.9834 | 19.958 | -23.0936 | -22.0335 | -14.7004 | 0.00055998 | 179.5827 | 11.5464 | 0.086607 | -4.9541 | 436.6064 | 437.6665 |  | 0.0074045 | 0.00032953 | 0.0070041 | 0.014301 | 0.025679 | -4.3759 | 0.0003117 |  |  | 36 | 3 | 61 | 1369 | 417.2712 | 1 | 869 | 0.065563 | 0.002332 | 0.067896 | 0.077896 | 2114.5599 | Infl | -2114.5599 | -0.44461 | 224018.871 | -6851.1742
| 35 | 1 | 59 | 1349 | 411.1752 | 96.4823 | 28.5689 | 387.7207 | 13.9936 | 19.7288 | -23.0224 | -21.9867 | -14.8764 | 0.00055524 | 177.5302 | 11.5398 | 0.086656 | -4.9419 | 436.6776 | 437.7133 |  | 0.0074226 | 0.00033009 | 0.0070303 | 0.014354 | 0.025481 | -4.3836 | 0.00031264 |  |  | 35 | 1 | 59 | 1349 | 411.1752 | 1 | 849 | 0.059441 | 0.0022801 | 0.061721 | 0.071721 | 2028.446 | Infl | -2028.446 | -0.4265 | 214739.8889 | -6572.1652
| Section >> |  | 5-Srv | Flrs/S | 5 | Section Ht (ft) |  | 75 | Per-L | 640 | Floor-Envel-Area (ft2) |  |  | 9600 | S-Flr-Area (ft2) |  | 120000 | Wndw Area (%) |  | 60 |  | Inside-Outside (PI-PO) |  |  | 0.02 | Leakg Flow Cf |  | 0.65 |  |  | Section >> |  | 5-Srv | Flrs/S | 5 | 5 | Envel Leakg A |  | 9.6576 | Appr. Sctn-Infltr (cfm) |  |  | 2379.0978 | Appr. Sctn Infltr (tons) |  |  | -7708.277
| 34 | 0 | XX | XX | XX | XX | XX | XX | XX | XX | [11 empty] | XX | XX | XX | XX | XX | XX | XX |  |  | 34 | 0 | XX | XX | XX | 0 | XX | XX | XX | XX | XX | 0 | XX | 0 | XX | XX | 0 | bar: DB to Twb
| 33 | 5 | 58 | 1339 | 408.1272 | 96.5175 | 28.5793 | 387.8621 | 13.9987 | 19.6142 | -22.9868 | -21.9633 | -14.9651 | 0.00055288 | 176.5082 | 11.5365 | 0.086681 | -4.9359 | 436.7132 | 437.7367 |  | 0.0074317 | 0.00033038 | 0.0070435 | 0.014381 | 0.025382 | -4.3876 | 0.00031311 |  |  | 33 | 5 | 58 | 1339 | 408.1272 | 1 | 839 | 0.056381 | 0.0022543 | 0.058635 | 0.078635 | 507.3346 | Infl | -507.3346 | -0.052847 | 53689.0789 | -1643.764
| 32 | 4 | 57 | 1324 | 403.5552 | 96.5704 | 28.595 | 388.0743 | 14.0063 | 19.4423 | -22.9334 | -21.9282 | -15.0987 | 0.00054933 | 174.9803 | 11.5315 | 0.086719 | -4.9268 | 436.7666 | 437.7718 |  | 0.0074454 | 0.0003308 | 0.0070633 | 0.014422 | 0.025233 | -4.3934 | 0.00031382 |  |  | 32 | 4 | 57 | 1324 | 403.5552 | 1 | 824 | 0.051791 | 0.0022159 | 0.054007 | 0.074007 | 492.0725 | Infl | -492.0725 | -0.051258 | 52045.5774 | -1594.3148
| 31 | 3 | 56 | 1309 | 398.9832 | 96.6232 | 28.6106 | 388.2866 | 14.014 | 19.2704 | -22.88 | -21.8931 | -15.2333 | 0.00054578 | 173.4586 | 11.5266 | 0.086756 | -4.9177 | 436.82 | 437.8069 |  | 0.007459 | 0.00033123 | 0.0070831 | 0.014462 | 0.025083 | -4.3994 | 0.00031453 |  |  | 31 | 3 | 56 | 1309 | 398.9832 | 1 | 809 | 0.047202 | 0.0021779 | 0.04938 | 0.06938 | 476.34 | Infl | -476.34 | -0.049619 | 50354.1101 | -1543.3415
| 30 | 2 | 55 | 1294 | 394.4112 | 96.676 | 28.6263 | 388.4991 | 14.0217 | 19.0985 | -22.8266 | -21.858 | -15.3689 | 0.00054223 | 171.9431 | 11.5216 | 0.086793 | -4.9086 | 436.8734 | 437.842 |  | 0.0074727 | 0.00033166 | 0.007103 | 0.014503 | 0.024934 | -4.4053 | 0.00031524 |  |  | 30 | 2 | 55 | 1294 | 394.4112 | 1 | 794 | 0.042615 | 0.0021401 | 0.044755 | 0.064755 | 460.0888 | Infl | -460.0888 | -0.047926 | 48609.6604 | -1490.6878
| 29 | 1 | 54 | 1279 | 389.8392 | 96.7289 | 28.6419 | 388.7116 | 14.0293 | 18.9267 | -22.7732 | -21.8229 | -15.5054 | 0.00053868 | 170.4338 | 11.5167 | 0.086831 | -4.8995 | 436.9268 | 437.8771 |  | 0.0074864 | 0.00033208 | 0.007123 | 0.014543 | 0.024785 | -4.4114 | 0.00031595 |  |  | 29 | 1 | 54 | 1279 | 389.8392 | 1 | 779 | 0.038028 | 0.0021027 | 0.040131 | 0.060131 | 443.262 | Infl | -443.262 | -0.046173 | 46806.2947 | -1436.1689
| Section >> |  | 4-Ofc | Flrs/S | 41 | Section Ht (ft) |  | 560 | Per-L | 720 | Floor-Envel-Area (ft2) |  |  | 9720 | S-Flr-Area (ft2) |  | 1262800 | Wndw Area (%) |  | 65 |  | Inside-Outside (PI-PO) |  |  | 0.025 | Leakg Flow Cf |  | 0.65 |  |  | Section >> |  | 4-Ofc | Flrs/S | 41 | 15 | Envel Leakg A |  | 7.844 | Appr. Sctn-Infltr (cfm) |  |  | 10926.1615 | Appr. Sctn Infltr (tons) |  |  | 13408.3366
| 28 | 41 | 53 | 1257.5 | 383.286 | 96.8048 | 28.6644 | 389.0163 | 14.0403 | 18.6803 | -22.6967 | -21.7725 | -15.7028 | 0.0005336 | 168.2812 | 11.5096 | 0.086884 | -4.8864 | 437.0033 | 437.9274 |  | 0.0075061 | 0.0003327 | 0.0071516 | 0.014602 | 0.02457 | -4.42 | 0.00031698 |  |  | 28 | 41 | 53 | 1257.5 | 383.286 | 1 | 757.5 | 0.031456 | 0.0020495 | 0.033505 | 0.058505 | 355.0148 | Infl | -355.0148 | -0.036524 | 37458.473 | -1150.2478
| 27 | 39 | 51 | 1230.5 | 375.0564 | 96.9001 | 28.6926 | 389.3993 | 14.0542 | 18.3709 | -22.6006 | -21.7094 | -15.9535 | 0.00052721 | 165.5957 | 11.5007 | 0.086952 | -4.8701 | 437.0994 | 437.9906 |  | 0.0075309 | 0.00033347 | 0.0071878 | 0.014676 | 0.0243 | -4.4311 | 0.00031826 |  |  | 27 | 39 | 51 | 1230.5 | 375.0564 | 1 | 730.5 | 0.023205 | 0.0019837 | 0.025189 | 0.050189 | 328.6886 | Infl | -328.6886 | -0.033816 | 34646.618 | -1064.9512
| 26 | 35 | 47 | 1176.5 | 358.5972 | 97.0909 | 28.7491 | 390.1663 | 14.0818 | 17.7521 | -22.4083 | -21.583 | -16.4647 | 0.00051444 | 160.2837 | 11.4829 | 0.087086 | -4.8373 | 437.2917 | 438.117 |  | 0.0075808 | 0.00033502 | 0.0072606 | 0.014824 | 0.023759 | -4.4536 | 0.00032086 |  |  | 26 | 35 | 47 | 1176.5 | 358.5972 | 1 | 676.5 | 0.0067145 | 0.0018552 | 0.0085697 | 0.03357 | 268.6074 | Infl | -268.6074 | -0.027635 | 28257.77 | -870.288
| 25 | 31 | 43 | 1122.5 | 342.138 | 97.2821 | 28.8057 | 390.9344 | 14.1096 | 17.1333 | -22.2161 | -21.4566 | -16.9898 | 0.00050168 | 155.0495 | 11.4651 | 0.087221 | -4.8045 | 437.4839 | 438.2433 |  | 0.0076309 | 0.00033657 | 0.0073341 | 0.014974 | 0.023216 | -4.4768 | 0.00032347 |  |  | 25 | 31 | 43 | 1122.5 | 342.138 | 1 | 622.5 | -0.0097623 | 0.0017308 | -0.0080315 | 0.016969 | 190.8227 | Infl | -190.8227 | -0.019632 | 20035.1265 | -618.2657
| 24 | 28 | 40 | 1082 | 329.7936 | 97.4256 | 28.8482 | 391.5113 | 14.1304 | 16.6692 | -22.0719 | -21.3619 | -17.393 | 0.00049211 | 151.1742 | 11.4518 | 0.087323 | -4.78 | 437.6281 | 438.3381 |  | 0.0076687 | 0.00033774 | 0.0073896 | 0.015088 | 0.022807 | -4.4945 | 0.00032544 |  |  | 24 | 28 | 40 | 1082 | 329.7936 | 1 | 582 | -0.022111 | 0.0016402 | -0.02047 | 0.0045297 | 98.5346 | Infl | -98.5346 | -0.010137 | 10330.1395 | -319.2521
| 23 | 26 | 38 | 1055 | 321.564 | 97.5214 | 28.8766 | 391.8963 | 14.1443 | 16.3598 | -21.9758 | -21.2987 | -17.6665 | 0.00048573 | 148.6145 | 11.4429 | 0.08739 | -4.7636 | 437.7242 | 438.4013 |  | 0.007694 | 0.00033852 | 0.0074268 | 0.015164 | 0.022534 | -4.5066 | 0.00032676 |  |  | 23 | 26 | 38 | 1055 | 321.564 | 1 | 555 | -0.030338 | 0.0015811 | -0.028757 | -0.0037571 | 89.705 | Exfl | 89.705 | 0.0092289 | -9395.1558 | 290.6443
| 22 | 24 | 36 | 1028 | 313.3344 | 97.6173 | 28.905 | 392.2816 | 14.1582 | 16.0504 | -21.8797 | -21.2355 | -17.9438 | 0.00047936 | 146.0736 | 11.4341 | 0.087458 | -4.7472 | 437.8203 | 438.4645 |  | 0.0077194 | 0.0003393 | 0.0074642 | 0.01524 | 0.02226 | -4.5188 | 0.00032808 |  |  | 22 | 24 | 36 | 1028 | 313.3344 | 1 | 528 | -0.038562 | 0.0015231 | -0.037039 | -0.012039 | 160.5168 | Exfl | 160.5168 | 0.016514 | -16794.8819 | 520.0744
| 21 | 25 | 37 | 1041.5 | 317.4492 | 97.5694 | 28.8908 | 392.0889 | 14.1512 | 16.2051 | -21.9277 | -21.2671 | -17.8047 | 0.00048255 | 147.3417 | 11.4385 | 0.087424 | -4.7554 | 437.7723 | 438.4329 |  | 0.0077067 | 0.00033891 | 0.0074455 | 0.015202 | 0.022397 | -4.5127 | 0.00032742 |  |  | 21 | 25 | 37 | 1041.5 | 317.4492 | 1 | 541.5 | -0.034451 | 0.001552 | -0.032899 | -0.0078988 | 130.0423 | Exfl | 130.0423 | 0.013379 | -13613.0814 | 421.337
| 20 | 22 | 34 | 1001 | 305.1048 | 97.7133 | 28.9334 | 392.6672 | 14.1721 | 15.741 | -21.7836 | -21.1723 | -18.2251 | 0.00047298 | 143.5515 | 11.4253 | 0.087525 | -4.7308 | 437.9164 | 438.5277 |  | 0.0077448 | 0.00034009 | 0.0075018 | 0.015317 | 0.021986 | -4.5312 | 0.00032941 |  |  | 20 | 22 | 34 | 1001 | 305.1048 | 1 | 501 | -0.046783 | 0.001466 | -0.045317 | -0.020317 | 208.4391 | Exfl | 208.4391 | 0.021444 | -21787.3615 | 675.3428
| 19 | 19 | 31 | 960.5 | 292.7604 | 97.8573 | 28.9761 | 393.2462 | 14.193 | 15.2769 | -21.6394 | -21.0776 | -18.6547 | 0.00046342 | 139.8031 | 11.412 | 0.087627 | -4.7062 | 438.0606 | 438.6224 |  | 0.0077831 | 0.00034127 | 0.0075585 | 0.015433 | 0.021573 | -4.5501 | 0.00033141 |  |  | 19 | 19 | 31 | 960.5 | 292.7604 | 1 | 460.5 | -0.059107 | 0.0013825 | -0.057724 | -0.032724 | 264.3834 | Exfl | 264.3834 | 0.0272 | -27593.8347 | 856.6022
| 18 | 16 | 28 | 920 | 280.416 | 98.0016 | 29.0188 | 393.8258 | 14.2139 | 14.8128 | -21.4952 | -20.9828 | -19.0939 | 0.00045387 | 136.0962 | 11.3988 | 0.087729 | -4.6816 | 438.2048 | 438.7172 |  | 0.0078216 | 0.00034245 | 0.0076156 | 0.015549 | 0.02116 | -4.5695 | 0.00033342 |  |  | 18 | 16 | 28 | 920 | 280.416 | 1 | 420 | -0.071422 | 0.0013013 | -0.070121 | -0.045121 | 310.2678 | Exfl | 310.2678 | 0.031921 | -32334.499 | 1005.2676
| 17 | 13 | 25 | 879.5 | 268.0716 | 98.146 | 29.0615 | 394.4062 | 14.2349 | 14.3487 | -21.351 | -20.888 | -19.543 | 0.00044431 | 132.4303 | 11.3856 | 0.08783 | -4.657 | 438.349 | 438.812 |  | 0.0078602 | 0.00034364 | 0.007673 | 0.015667 | 0.020745 | -4.5893 | 0.00033545 |  |  | 17 | 13 | 25 | 879.5 | 268.0716 | 1 | 379.5 | -0.083729 | 0.0012224 | -0.082506 | -0.057506 | 350.0706 | Exfl | 350.0706 | 0.036015 | -36428.0318 | 1134.2287
| 16 | 10 | 22 | 839 | 255.7272 | 98.2906 | 29.1043 | 394.9873 | 14.2558 | 13.8846 | -21.2068 | -20.7933 | -20.0025 | 0.00043476 | 128.8051 | 11.3724 | 0.087932 | -4.6325 | 438.4932 | 438.9067 |  | 0.007899 | 0.00034483 | 0.0077309 | 0.015785 | 0.02033 | -4.6095 | 0.00033748 |  |  | 16 | 10 | 22 | 839 | 255.7272 | 1 | 339 | -0.096027 | 0.0011459 | -0.094881 | -0.069881 | 385.6794 | Exfl | 385.6794 | 0.039679 | -40073.3922 | 1249.6011
| 15 | 7 | 19 | 798.5 | 243.3828 | 98.4354 | 29.1472 | 395.569 | 14.2768 | 13.4206 | -21.0627 | -20.6985 | -20.4728 | 0.00042521 | 125.2201 | 11.3592 | 0.088034 | -4.6079 | 438.6373 | 439.0015 |  | 0.007938 | 0.00034602 | 0.0077891 | 0.015904 | 0.019913 | -4.6302 | 0.00033952 |  |  | 15 | 7 | 19 | 798.5 | 243.3828 | 1 | 298.5 | -0.10832 | 0.0010719 | -0.10725 | -0.082245 | 418.1669 | Exfl | 418.1669 | 0.043021 | -43383.8402 | 1354.8607
| 14 | 5 | 17 | 771.5 | 235.1532 | 98.532 | 29.1758 | 395.9572 | 14.2908 | 13.1112 | -20.9665 | -20.6353 | -20.7927 | 0.00041885 | 122.8522 | 11.3505 | 0.088102 | -4.5915 | 438.7335 | 439.0647 |  | 0.0079641 | 0.00034682 | 0.0078282 | 0.015983 | 0.019634 | -4.6443 | 0.00034089 |  |  | 14 | 5 | 17 | 771.5 | 235.1532 | 1 | 271.5 | -0.11651 | 0.0010238 | -0.11548 | -0.090482 | 438.4367 | Exfl | 438.4367 | 0.045107 | -45441.2738 | 1420.5349
| 13 | 3 | 15 | 744.5 | 226.9236 | 98.6287 | 29.2044 | 396.3457 | 14.3049 | 12.8018 | -20.8704 | -20.5721 | -21.1177 | 0.00041248 | 120.502 | 11.3417 | 0.08817 | -4.5751 | 438.8296 | 439.1279 |  | 0.0079903 | 0.00034761 | 0.0078674 | 0.016063 | 0.019355 | -4.6586 | 0.00034227 |  |  | 13 | 3 | 15 | 744.5 | 226.9236 | 1 | 244.5 | -0.12469 | 0.0009768 | -0.12371 | -0.098713 | 457.7691 | Exfl | 457.7691 | 0.047096 | -47397.4358 | 1483.1718
| 12 | 1 | 13 | 717.5 | 218.694 | 98.7254 | 29.2331 | 396.7346 | 14.3189 | 12.4924 | -20.7743 | -20.5089 | -21.4481 | 0.00040612 | 118.1692 | 11.333 | 0.088238 | -4.5587 | 438.9257 | 439.1911 |  | 0.0080165 | 0.00034842 | 0.0079068 | 0.016144 | 0.019075 | -4.6732 | 0.00034364 |  |  | 12 | 1 | 13 | 717.5 | 218.694 | 1 | 217.5 | -0.13287 | 0.00093088 | -0.13194 | -0.10694 | 476.2782 | Exfl | 476.2782 | 0.049 | -49264.4273 | 1543.1413
| Section >> |  | 3-Fin | Flrs/S | 6 | Section Ht (ft) |  | 90 | Per-L | 800 | Floor-Envel-Area (ft2) |  |  | 12000 | S-Flr-Area (ft2) |  | 230400 | Wndw Area (%) |  | 65 |  | Inside-Outside (PI-PO) |  |  | 0.025 | Leakg Flow Cf |  | 0.65 |  |  | Section >> |  | 3-Fin | Flrs/S | 6 | 4 | Envel Leakg A |  | 9.684 | Appr. Sctn-Infltr (cfm) |  |  | 3701.5705 | Appr. Sctn Infltr (tons) |  |  | 11993.0883
| 11 | 6 | 12 | 704 | 214.5792 | 98.7738 | 29.2474 | 396.9291 | 14.3259 | 12.3377 | -20.7262 | -20.4774 | -21.6154 | 0.00040294 | 117.0093 | 11.3286 | 0.088272 | -4.5505 | 438.9738 | 439.2226 |  | 0.0080297 | 0.00034882 | 0.0079266 | 0.016184 | 0.018935 | -4.6805 | 0.00034433 |  |  | 11 | 6 | 12 | 704 | 214.5792 | 1 | 204 | -0.13696 | 0.00090831 | -0.13605 | -0.11105 | 599.0785 | Exfl | 599.0785 | 0.049923 | -61935.3392 | 1941.0145
| 10 | 5 | 11 | 689 | 210.0072 | 98.8276 | 29.2634 | 397.1453 | 14.3337 | 12.1658 | -20.6728 | -20.4423 | -21.8029 | 0.00039941 | 115.7256 | 11.3237 | 0.08831 | -4.5414 | 439.0272 | 439.2577 |  | 0.0080443 | 0.00034926 | 0.0079486 | 0.016229 | 0.01878 | -4.6888 | 0.0003451 |  |  | 10 | 5 | 11 | 689 | 210.0072 | 1 | 189 | -0.1415 | 0.00088356 | -0.14062 | -0.11562 | 611.1413 | Exfl | 611.1413 | 0.050928 | -63147.1887 | 1980.0977
| 9 | 4 | 10 | 674 | 205.4352 | 98.8815 | 29.2793 | 397.3617 | 14.3415 | 11.9939 | -20.6194 | -20.4072 | -21.9921 | 0.00039588 | 114.4472 | 11.3189 | 0.088348 | -4.5323 | 439.0806 | 439.2928 |  | 0.008059 | 0.00034971 | 0.0079707 | 0.016274 | 0.018624 | -4.6971 | 0.00034587 |  |  | 9 | 4 | 10 | 674 | 205.4352 | 1 | 174 | -0.14604 | 0.00085914 | -0.14518 | -0.12018 | 622.9563 | Exfl | 622.9563 | 0.051913 | -64332.0717 | 2018.3784
| 8 | 3 | 9 | 659 | 200.8632 | 98.9353 | 29.2952 | 397.5781 | 14.3493 | 11.822 | -20.566 | -20.3721 | -22.1832 | 0.00039234 | 113.1741 | 11.314 | 0.088386 | -4.5232 | 439.134 | 439.3279 |  | 0.0080737 | 0.00035015 | 0.0079928 | 0.01632 | 0.018468 | -4.7056 | 0.00034665 |  |  | 8 | 3 | 9 | 659 | 200.8632 | 1 | 159 | -0.15058 | 0.00083505 | -0.14975 | -0.12475 | 634.5375 | Exfl | 634.5375 | 0.052878 | -65491.4589 | 2055.9016
| 7 | 2 | 8 | 644 | 196.2912 | 98.9892 | 29.3112 | 397.7946 | 14.3572 | 11.6501 | -20.5126 | -20.337 | -22.3761 | 0.00038881 | 111.9063 | 11.3092 | 0.088424 | -4.514 | 439.1874 | 439.363 |  | 0.0080884 | 0.0003506 | 0.008015 | 0.016365 | 0.018311 | -4.714 | 0.00034742 |  |  | 7 | 2 | 8 | 644 | 196.2912 | 1 | 144 | -0.15512 | 0.00081129 | -0.15431 | -0.12931 | 645.8975 | Exfl | 645.8975 | 0.053825 | -66626.6882 | 2092.708
| 6 | 1 | 7 | 629 | 191.7192 | 99.0431 | 29.3272 | 398.0112 | 14.365 | 11.4782 | -20.4592 | -20.3019 | -22.5709 | 0.00038528 | 110.6437 | 11.3044 | 0.088462 | -4.5049 | 439.2408 | 439.3981 |  | 0.0081031 | 0.00035105 | 0.0080372 | 0.01641 | 0.018155 | -4.7226 | 0.00034819 |  |  | 6 | 1 | 7 | 629 | 191.7192 | 1 | 129 | -0.15966 | 0.00078786 | -0.15887 | -0.13387 | 657.0477 | Exfl | 657.0477 | 0.054754 | -67738.9809 | 2128.8347
| Section >> |  | 2-Rtl | Flrs/S | 4 | Section Ht (ft) |  | 74 | Per-L | 838.8783 | Floor-Envel-Area (ft2) |  |  | 15099.809 | S-Flr-Area (ft2) |  | 224000 | Wndw Area (%) |  | 50 |  | Inside-Outside (PI-PO) |  |  | 0.015 | Leakg Flow Cf |  | 0.65 |  |  | Section >> |  | 2-Rtl | Flrs/S | 4 | 3 | Envel Leakg A |  | 113.2486 | Appr. Sctn-Infltr (cfm) |  |  | 33569.1745 | Appr. Sctn Infltr (tons) |  |  | 108764.1253
| 5 | 3 | 5 | 594 | 181.0512 | 99.169 | 29.3644 | 398.5171 | 14.3832 | 11.0772 | -20.3346 | -20.22 | -23.0328 | 0.00037704 | 107.7181 | 11.2931 | 0.08855 | -4.4837 | 439.3654 | 439.48 |  | 0.0081376 | 0.0003521 | 0.0080894 | 0.016517 | 0.01779 | -4.743 | 0.00035001 |  |  | 5 | 3 | 5 | 594 | 181.0512 | 1 | 94 | -0.17024 | 0.0007345 | -0.1695 | -0.1545 | 8250.6365 | Exfl | 8250.6365 | 0.54641 | -849497.1781 | 26732.0623
| 4 | 2 | 4 | 576 | 175.5648 | 99.2338 | 29.3836 | 398.7774 | 14.3926 | 10.8709 | -20.2706 | -20.1778 | -23.2745 | 0.0003728 | 106.2245 | 11.2873 | 0.088596 | -4.4727 | 439.4294 | 439.5222 |  | 0.0081554 | 0.00035264 | 0.0081163 | 0.016572 | 0.017601 | -4.7536 | 0.00035094 |  |  | 4 | 2 | 4 | 576 | 175.5648 | 1 | 76 | -0.17568 | 0.00070776 | -0.17497 | -0.15997 | 8393.1546 | Exfl | 8393.1546 | 0.55585 | -863590.1818 | 27193.8209
| 3 | 1 | 3 | 558 | 170.0784 | 99.2986 | 29.4028 | 399.0379 | 14.402 | 10.6646 | -20.2065 | -20.1357 | -23.5192 | 0.00036857 | 104.7384 | 11.2815 | 0.088641 | -4.4618 | 439.4935 | 439.5643 |  | 0.0081732 | 0.00035318 | 0.0081433 | 0.016627 | 0.017413 | -4.7644 | 0.00035188 |  |  | 3 | 1 | 3 | 558 | 170.0784 | 1 | 58 | -0.18111 | 0.00068151 | -0.18043 | -0.16543 | 8533.0898 | Exfl | 8533.0898 | 0.56511 | -877397.8741 | 27647.2108
| Section >> |  | 1-Grd | Flrs/S | 2 | Section Ht (ft) |  | 40 | Per-L | 982.3936 | Floor-Envel-Area (ft2) |  |  | 19647.8729 | S-Flr-Area (ft2) |  | 153600 | Wndw Area (%) |  | 60 |  | Inside-Outside (PI-PO) |  |  | 0.005 | Leakg Flow Cf |  | 0.65 |  |  | Section >> |  | 1-Grd | Flrs/S | 2 | 2 | Envel Leakg A |  | 186.6548 | Appr. Sctn-Infltr (cfm) |  |  | 30122.1794 | Appr. Sctn Infltr (tons) |  |  | 97595.8613
| 2 | 2 | 2 | 520 | 158.496 | 99.4355 | 29.4434 | 399.5882 | 14.4219 | 10.2292 | -20.0712 | -20.0468 | -24.0457 | 0.00035962 | 101.6253 | 11.2692 | 0.088737 | -4.4387 | 439.6288 | 439.6532 |  | 0.0082109 | 0.00035432 | 0.0082005 | 0.016744 | 0.017014 | -4.7875 | 0.00035387 |  |  | 2 | 2 | 2 | 520 | 158.496 | 1 | 20 | -0.19259 | 0.00062767 | -0.19196 | -0.18696 | 14943.0824 | Exfl | 14943.0824 | 0.76054 | -1534309.3182 | 48415.587
| 1 | 1 | 1 | 500 | 152.4 | 99.5077 | 29.4647 | 399.8781 | 14.4324 | 10 | -20 | -20 | -24.3284 | 0.00035492 | 100 | 11.2628 | 0.088788 | -4.4266 | 439.7 | 439.7 |  | 0.0082308 | 0.00035492 | 0.0082308 | 0.016805 | 0.016804 | -4.8 | 0.00035492 |  |  | 1 | 1 | 1 | 500 | 152.4 | 1 | 0 | -0.19862 | 0.00060021 | -0.19802 | -0.19302 | 15179.097 | Exfl | 15179.097 | 0.77256 | -1557375.3522 | 49180.2743

## HRB-Apt-Pressurization Vnt-Exh
High-Rise - Apt-Condo Bldg with operable windows - Ventil-Exhaust - Pressure-Analysis | [26 empty] | Apt Unit Types - Studio, 1, 2, 3 bedrooms | [9 empty] | High-Rise - Apt-Condo Bldg with operable windows - Ventil-Exhaust - Pressure-Analysis | [30 empty] | Apt Unit Types - Studio, 1, 2, 3 bedrooms | [13 empty] | APARTMENT Building: Schedules / Profiles | [9 empty] | DOE2 - 0 to 1 (fraction) |  |  |  | TRACE - 0 to 100 (percent)
# units/flr & unit types vary per section & floor | [11 empty] | Space |  | SF |  |  | Space |  | SF |  |  | Apartment |  |  | cfm/SF |  |  | Diversity/Floor |  |  |  | Core-Exhst fan-cfm/Flr |  |  |  |  | Apt Ktchn & Bthrm Exhaust | [8 empty] | Apt Ktchn & Bthrm Exhaust | [9 empty] | CORE Exhaust & Supply Air | [12 empty] | CORE Exhaust & Supply Air
|  | 2 Bthr per 2-bdrm & 1-bdrm (1-Riser/Apt) | [8 empty] | sfK | Ktchn |  | 200 |  | sf1 | 1-Bdrm |  | 900 |  | oaA | Apt-Ventil |  |  | 0.05 |  | dvA | Apt-Ventil |  | 1 |  | exT | Trash Chute |  |  | 100 | Bldg-Sectn - 1 |  |  |  | Bldg-Sectn - 2 |  |  |  |  | Bldg-Sectn - 3 |  |  |  | Bldg-Sectn - 4 | [6 empty] | Bldg-Sectn - 1 | [5 empty] | Bldg-Sectn - 2 | [6 empty] | Bldg-Sectn - 3 | [5 empty] | Bldg-Sectn - 4 | [5 empty] | Hour No. (DOE2) | Hour No. (TRACE) | Hour From-To | People (Apt-PPL) | Lights (Apt-LGT) | Equipment (Apt-EQP) | Elevators (Apt-ELV) | Domestic Hot Water | Apt Ventil = People Schd | Apt Toilet Exhaust | Apt Kitchen Exhaust | Core General Exhaust | Trash Chute Exhaust | Core Storage Exhaust | Core Laundr Exhaust | System/AHU Operatg Sch | Smmr Inside DB Temp (F) | Heating Unit Operatg Sch | Wntr Inside DB Temp (F)
|  | 1 Bthr per Studio & 1-bdrm (1-Riser/Apt) | [8 empty] | sfB | Bthrm |  | 100 |  | sf2 | 2-Bdrm |  | 1300 |  | exK | Kitchn-Exh |  |  | 0.4 |  | dvK | Kitchn-Exh |  | 1 |  | exS | Storg/Lckrs |  |  | 500 | Flrs/Sectn |  |  | 25 | Flrs/Sectn |  |  | 40 |  | Flrs/Sectn |  |  | 10 | Flrs/Sectn |  |  |  | 3 |  |  | Flrs/Sectn |  |  |  | 25 |  | Flrs/Sectn |  |  |  | 40 |  |  | Flrs/Sectn |  |  |  | 10 |  | Flrs/Sectn |  |  |  | 3
(1) Water Source |  |  |  |  | 1 Ktch per Apt (1-Riser/Apt) | [5 empty] | sfS | Studio |  | 650 |  | sf3 | 3-Bdrm |  | 1600 |  | exB | Bthrm-Exh |  |  | 0.7 |  | dvB | Bthrm-Exh |  | 1 |  | exL | Laundry-Rm |  |  | 900 |  | Kitchen Exh | Bathrm Exh |  |  | Kitchen Exh | Bathrm Exh |  |  |  | Kitchen Exh | Bathrm Exh |  |  | Kitchen Exh |  | Bathrm Exh |  |  |  | Trash Chute | Storage Exh | Laundry Exh | Miscell Exh |  | Supply Air | Trash Chute | Storage Exh | Laundry Exh | Miscell Exh |  | Supply Air |  | Trash Chute | Storage Exh | Laundry Exh | Miscell Exh |  | Supply Air | Trash Chute | Storage Exh | Laundry Exh | Miscell Exh |  | Supply Air
Heat Pumps (WSHP) | [5 empty] | # Bldg-Sctns |  |  | 4 |  | Core-Pressurizition-Ratio (SA/EA) | [7 empty] | 1.5 |  | oaC | Core-Vent |  |  | 0.2 |  | dvC | Core-Exh |  | 1 |  | exM | Miscellan |  |  | 100
Stacked Vertically in Closets | [7 empty] | Ventilation from Corridor | [5 empty] | Windows closed (HVAC System on) when winter dry bulb temp < 65 degF and summer dew point temp > 55 degF
2-Pipe-Risers (WSHP & FCU) | [5 empty] | Plumbing-Pipe-Risers |  |  |  |  | supplied from under Door | [5 empty] | Row |  | Column |  |  | c1 |  | c2 |  | c3 |  | c4 | C O R E Areas |  | Services |  |  | CORE - EA Floor | [20 empty] | ROOF
[18 empty] | Flr-Sections |  |  |  | S1 |  | S2 |  | S3 |  | S4 |  |  | Corridors |  |  | TC | Trash-Chute | [48 empty] | Units | sf/P | W/sf | W/sf | W/Elev | gal/P | cfm/P | cfm/sf | cfm/sf | cfm/sf | cfm/sf | cfm/sf | cfm/sf | MAY - OCT |  | NOV - APR
| NW |  | B |  | N1 |  |  |  | N2 |  |  | B |  | NE |  |  | r1 | # of Studio Apts |  |  |  | 5 |  | 6 |  | 0 |  | 0 |  |  | Flr-Flr-Trvl |  |  | GE | Miscell-Exh | [19 empty] | Flr - N | [26 empty] | Design Basis >> |  |  | 500 | 1 | 0.25 |  |  | 40 | 2 | 2 | 1 | 1 | 1 | 1 | On/Off | Temp | Not | Temp
|  |  | K | OA | [6 empty] | OA | K |  |  |  |  | r2 | # of 1-Bdr Apts |  |  |  | 6 |  | 9 |  | 12 |  | 5 |  |  | Exh Shaft |  |  | LE | Laundr-Exh | [46 empty] | Design Value >> | [14 empty] | 0 / 100 | 75 | Used | 70
[5 empty] | K | B |  |  | B | K |  |  | OA |  |  |  | r3 | # of 2-Bdr Apts |  |  |  | 4 |  | 0 |  | 8 |  | 15 |  | OA | Outdr Air |  |  | EE | Electric-Exh | [46 empty] | 1 | 0 | 0 - 1 | 95 | 5 | 30 | 5 | 5 | 95 | 5 | 5 | 0 | 0 | 0 | 0 | 100 | 75 | 100 | 70
|  |  |  | OA - Corrid to Apts Under Door | [12 empty] | r4 | # of 3-Bdr Apts |  |  |  | 2 |  | 0 |  | 0 |  | 10 | [5 empty] | EA Apartments | [47 empty] | 2 | 1 | 1 - 2 | 95 | 5 | 30 | 5 | 5 | 95 | 5 | 5 | 0 | 0 | 0 | 0 | 100 | 75 | 100 | 70
| W2 |  | K |  | Lockers |  | TC | Washers |  |  |  | K |  | E1 |  |  | r5 | Core-A % of Flr |  |  |  | 15 |  | 15 |  | 15 |  | 15 | Calculations |  |  |  |  | B | Bathrm-Exh | [46 empty] | 3 | 2 | 2 - 3 | 95 | 5 | 30 | 5 | 5 | 95 | 5 | 5 | 0 | 0 | 0 | 0 | 100 | 75 | 100 | 70
|  |  | B | Corridor | Storage |  | GE | Laundry |  |  | Corridor | B |  |  |  |  | r6 | # of Kitch Risers |  |  |  | 17 |  | 15 |  | 20 |  | 30 | r6 = r1 + r2 + r3 + r4 |  |  |  |  | K | Kitchen-Exh | [16 empty] | Intermediate Floors | [29 empty] | 4 | 3 | 3 - 4 | 95 | 5 | 30 | 5 | 5 | 95 | 5 | 5 | 0 | 0 | 0 | 0 | 100 | 75 | 100 | 70
[5 empty] | Lockers |  | LE | Dryers | [8 empty] | r7 | # of Bthr Risers |  |  |  | 23 |  | 15 |  | 28 |  | 55 | r7 = r1 + r2 + 2*r3 + 2*r4 | [52 empty] | 5 | 4 | 4 - 5 | 95 | 5 | 30 | 5 | 5 | 95 | 5 | 5 | 0 | 0 | 0 | 0 | 100 | 75 | 100 | 70
[7 empty] | Corridor | [9 empty] | r8 | Tot-Apart-Area |  |  |  | 17050 |  | 12000 |  | 21200 |  | 40000 | r8 = r1*sfS + r2*sf1 +r3*sf2 + r4*sf3 | [52 empty] | 6 | 5 | 5 - 6 | 95 | 5 | 30 | 5 | 5 | 95 | 50 | 80 | 0 | 0 | 0 | 0 | 100 | 75 | 100 | 70
| W1 |  | B |  | ELEVATORS |  |  |  | STAIRS |  |  | B |  | E2 |  |  | r9 | Tot-Core-A SF |  |  |  | 3008.8235 |  | 2117.6471 |  | 3741.1765 |  | 7058.8235 | r9 = (r8*r5/100) / (1-r5/100) | [52 empty] | 7 | 6 | 6 - 7 | 95 | 25 | 50 | 20 | 30 | 95 | 50 | 80 | 0 | 0 | 0 | 0 | 100 | 75 | 100 | 70
|  |  | K |  | Util-Clo |  | EE | OA |  |  |  | K |  |  |  |  | r10 | Tot-Flr-Area SF |  |  |  | 20058.8235 |  | 14117.6471 |  | 24941.1765 |  | 47058.8235 | r10 = r8 + r9 | [5 empty] | Row-Col #s | [19 empty] | Flr - 3 | [26 empty] | 8 | 7 | 7 - 8 | 80 | 45 | 90 | 40 | 50 | 80 | 50 | 80 | 0 | 0 | 0 | 0 | 100 | 75 | 100 | 70
|  |  |  | OA - Corrid to Apts Under Door | [12 empty] | r11 | Apt Vnt < Corr |  |  |  | 1002.9412 |  | 705.8824 |  | 1247.0588 |  | 2352.9412 | r1 = r10 * oaA * dvA | [52 empty] | 9 | 8 | 8 - 9 | 80 | 45 | 30 | 50 | 40 | 80 | 5 | 5 | 0 | 0 | 0 | 0 | 100 | 75 | 100 | 70
[5 empty] | K | B |  |  | B | K | [6 empty] | r12 | Apt-Kitch-Exh |  |  |  | 1360 |  | 1200 |  | 1600 |  | 2400 | r12 = r6 * exK * dvK * sfK | [25 empty] | Flr - 2 | [26 empty] | 10 | 9 | 9 - 10 | 65 | 35 | 30 | 40 | 30 | 65 | 5 | 5 | 0 | 0 | 0 | 0 | 0 | 95 | 50 | 50
|  |  | K | [8 empty] | K |  |  |  |  | r13 | Apt-Bthrm-Exh |  |  |  | 1610 |  | 1050 |  | 1960 |  | 3850 | r13 = r7 * exB * dvB * sfB | [52 empty] | 11 | 10 | 10 - 11 | 65 | 35 | 30 | 40 | 30 | 65 | 5 | 5 | 0 | 0 | 0 | 0 | 0 | 95 | 50 | 50
| SW |  | B |  |  | S2 |  |  | S1 |  |  | B |  | SE |  |  | r14 | Apt Vnt+Exh |  |  |  | 3972.9412 |  | 2955.8824 |  | 4807.0588 |  | 8602.9412 | r14 = r11 + r12 + r13 | [5 empty] | User Input | [19 empty] | Flr - 1 | [26 empty] | 12 | 11 | 11 - 12 | 65 | 35 | 30 | 35 | 35 | 65 | 50 | 80 | 0 | 0 | 0 | 0 | 0 | 95 | 50 | 50
[17 empty] | r15 | Core-Supp-OA |  |  |  | 5959.4118 |  | 4433.8235 |  | 7210.5882 |  | 12904.4118 | r15 = r14 * SA/EA | [5 empty] | Calculated |  | Bldg-Sectn - 1 |  |  |  | Bldg-Sectn - 2 |  |  |  |  | Bldg-Sectn - 3 |  |  |  | Bldg-Sectn - 4 | [6 empty] | Bldg-Sectn - 1 | [5 empty] | Bldg-Sectn - 2 | [6 empty] | Bldg-Sectn - 3 | [5 empty] | Bldg-Sectn - 4 | [5 empty] | 13 | 12 | 12 - 13 | 65 | 25 | 50 | 35 | 40 | 65 | 50 | 80 | 0 | 0 | 0 | 0 | 0 | 95 | 50 | 50
Alternate HVAC System = (2) Window A-C Units + Electric Baseboard Heat | [16 empty] | r16 | Cor-OA-cfm/SF |  |  |  | 1.9806 |  | 2.0938 |  | 1.9274 |  | 1.8281 | r16 = r15 / r9 | [5 empty] | Aprtmnts |  | Ktch & Bthr Exh |  |  |  | Ktch & Bthr Exh |  |  |  |  | Ktch & Bthr Exh |  |  |  | Ktch & Bthr Exh | [6 empty] | Risers/Section [Exhsts = 1-Trash-Chute, 2-Storage, 3-Laundry, 4-Miscell] 5-Supply-OA | [24 empty] | 14 | 13 | 13 - 14 | 65 | 25 | 90 | 30 | 35 | 65 | 50 | 80 | 0 | 0 | 0 | 0 | 100 | 75 | 100 | 70
|  |  |  | Site Plan |  |  |  |  | or (3a) 2-Pipe (Elctr-Htg) or (3b) 4-Pipe (HW-Htg) Fan-Coil Units (FCU) or (4) Central HVAC System (heating & cooling) | [25 empty] | Ktch-Bthr |  | # Ktc Risers |  |  | 17 | # Ktc Risers |  |  | 15 |  | # Ktc Risers |  |  | 20 | # Ktc Risers |  |  |  | 30 |  |  | 1-Trash |  |  | 2500 |  |  | 1-Trash |  |  | 4000 |  |  |  | 1-Trash |  |  | 4000 |  |  | 1-Trash |  |  | 300 |  |  | 15 | 14 | 14 - 15 | 65 | 25 | 30 | 30 | 35 | 65 | 5 | 5 | 0 | 0 | 0 | 0 | 100 | 75 | 100 | 70
|  |  | N Street | [11 empty] | Bldg-Apt Complex |  |  |  |  | Row |  |  | Column |  |  | c1 |  | c2 | c3 |  | c4 | [5 empty] | Ktch Exh |  | 34000 |  | Ktch Exh |  | 48000 |  |  | Ktch Exh |  | 16000 |  | Ktch Exh |  |  | 7200 |  |  |  | Trash Fan-SP | [5 empty] | Trash Fan-SP | [6 empty] | Trash Fan-SP | [5 empty] | Trash Fan-SP | [5 empty] | 16 | 15 | 15 - 16 | 65 | 25 | 30 | 30 | 30 | 65 | 5 | 5 | 0 | 0 | 0 | 0 | 100 | 75 | 100 | 70
[16 empty] | Elevation |  |  |  |  | Sections |  |  | Divers |  | S1 |  | S2 | S3 |  | S4 | [5 empty] | Ktch Fan-SP |  |  |  | Ktch Fan-SP |  |  |  |  | Ktch Fan-SP |  |  |  | Ktch Fan-SP | [6 empty] | 2-Storage |  |  | 12500 |  |  | 2-Storage |  |  | 20000 |  |  |  | 2-Storage |  |  | 5000 |  |  | 2-Storage |  |  | 1500 |  |  | 17 | 16 | 16 - 17 | 80 | 25 | 30 | 40 | 30 | 80 | 5 | 5 | 0 | 0 | 0 | 0 | 0 | 95 | 50 | 50
| X Avenue | [6 empty] | Z Avenue | [11 empty] | r21 | Flrs/Sectn |  |  |  |  | 25 |  | 40 | 10 |  | 3 |  | Calculations |  |  |  | Bth Risers |  |  | 23 | Bth Risers |  |  | 15 |  | Bth Risers |  |  | 28 | Bth Risers |  |  |  | 55 |  |  | Storg Fan-SP | [5 empty] | Storg Fan-SP | [6 empty] | Storg Fan-SP | [5 empty] | Storg Fan-SP | [5 empty] | 18 | 17 | 17 - 18 | 80 | 35 | 50 | 45 | 50 | 80 | 50 | 80 | 0 | 0 | 0 | 0 | 0 | 95 | 50 | 50
|  |  |  | Court | [15 empty] | r22 | Sctn Flr SF |  |  |  |  | 501470.5882 |  | 564705.8824 | 249411.7647 |  | 141176.4706 |  | Flr-A = r21 * r10 |  |  |  | Bthr Exh |  | 40250 |  | Bthr Exh |  | 42000 |  |  | Bthr Exh |  | 19600 |  | Bthr Exh |  |  | 11550 |  |  |  | 3-Laundry |  |  | 22500 |  |  | 3-Laundry |  |  | 36000 |  |  |  | 3-Laundry |  |  | 9000 |  |  | 3-Laundry |  |  | 2700 |  |  | 19 | 18 | 18 - 19 | 85 | 70 | 90 | 50 | 50 | 85 | 50 | 80 | 0 | 0 | 0 | 0 | 100 | 75 | 100 | 70
|  |  |  | Yard | [15 empty] | r23 | Apt-Vent |  |  | 1 |  | 25073.5294 |  | 28235.2941 | 12470.5882 |  | 7058.8235 |  | Ap-V = r23 * r21 * r11 |  |  |  | Bthr Fan-SP |  |  |  | Bthr Fan-SP |  |  |  |  | Bthr Fan-SP |  |  |  | Bthr Fan-SP | [6 empty] | Lndry Fan-SP | [5 empty] | Lndry Fan-SP | [6 empty] | Lndry Fan-SP | [5 empty] | Lndry Fan-SP | [5 empty] | 20 | 19 | 19 - 20 | 85 | 70 | 30 | 40 | 40 | 85 | 50 | 80 | 0 | 0 | 0 | 0 | 100 | 75 | 100 | 70
[20 empty] | r24 | Kitchn Exh |  |  | 1 |  | 34000 |  | 48000 | 16000 |  | 7200 |  | Kt-Ex = r24 * r21 * r12 |  |  |  | Apt Vnt |  | 148985.2941 |  | Apt Vnt |  | 177352.9412 |  |  | Apt Vnt |  | 72105.8824 |  | Apt Vnt |  |  | 38713.2353 |  |  |  | 4-Miscell |  |  | 2500 |  |  | 4-Miscell |  |  | 4000 |  |  |  | 4-Miscell |  |  | 1000 |  |  | 4-Miscell |  |  | 300 |  |  | 21 | 20 | 20 - 21 | 85 | 70 | 30 | 35 | 35 | 85 | 5 | 5 | 0 | 0 | 0 | 0 | 100 | 75 | 100 | 70
[20 empty] | r25 | Bthrm Exh |  |  | 1 |  | 40250 |  | 42000 | 19600 |  | 11550 |  | Bt-Ex = r25 * r21 * r13 |  |  |  | Apt Exh |  | 74250 |  | Apt Exh |  | 90000 |  |  | Apt Exh |  | 35600 |  | Apt Exh |  |  | 18750 |  |  |  | Miscl Fan-SP | [5 empty] | Miscl Fan-SP | [6 empty] | Miscl Fan-SP | [5 empty] | Miscl Fan-SP | [5 empty] | 22 | 21 | 21 - 22 | 95 | 70 | 30 | 30 | 45 | 95 | 5 | 5 | 0 | 0 | 0 | 0 | 100 | 75 | 100 | 70
|  |  | N+1 Street | [7 empty] | Sctn-1 |  | Sctn-2 |  | Sctn-3 |  | Sctn-4 |  |  | r26 | Core-Exhst |  |  | 1 |  | 99323.5294 |  | 118235.2941 | 48070.5882 |  | 25808.8235 |  | Cr-Ex = r26 * r21 * r14 |  |  |  | Bldg (all sections) Ventil Air (cfm) | [7 empty] | 437157.3529 | [11 empty] | 5-OA |  | 148985.2941 |  |  |  | 5-OA |  | 177352.9412 |  |  |  |  | 5-OA |  | 72105.8824 |  |  |  | 5-OA |  | 38713.2353 |  |  |  | 23 | 22 | 22 - 23 | 95 | 60 | 30 | 10 | 30 | 95 | 5 | 5 | 0 | 0 | 0 | 0 | 100 | 75 | 100 | 70
[11 empty] | Lobby-Services-Offices-Garage | [8 empty] | r27 | Cor-Apt-OA |  |  | 1 |  | 148985.2941 |  | 177352.9412 | 72105.8824 |  | 38713.2353 |  | Ap-SA r27 * r21 * r15 |  |  |  | Bldg (all sections) Exhaust Air (cfm) | [7 empty] | 346400 |  |  | Core-Pressurization | [5 empty] | 1.262 |  |  | S-OA Fan-SP | [5 empty] | S-OA Fan-SP | [6 empty] | S-OA Fan-SP | [5 empty] | S-OA Fan-SP | [5 empty] | 24 | 23 | 23 - 24 | 95 | 5 | 30 | 5 | 5 | 95 | 5 | 5 | 0 | 0 | 0 | 0 | 100 | 75 | 100 | 70

## Bldg-Stck-Eff-Theory
Infltr & Exfltr due to Building Stack Effect, Wind Press | [17 empty] | Basis of Calculations | [5 empty] | Infltr & Exfltr due to Building Stack Effect, Wind Press | [9 empty] | Basis of Calculations
Definitions
ASHRAE def. of Tall Buildings = above 300 ft
CTBUH def. of Super-Tall Bldgs = above 300 meters = above 985 feet
NFPA def. of High Rise Bldg > than 7 stories (> 75 ft approx) fight fire from inside
Def. of Low Rise Bldg varies. Ex. Requires no elevators (up to 3 flrs, less than 35 ft)
Def. of Mid Rise Bldg = between Low Rise and High Rise (4 to 7 flrs, 35 ft to 75 ft)
| Flr to Flr Heights (ft): |  |  |  | Residential = |  |  |  | 10 |  | Office = |  |  | 13.5 |  | Retail = |  |  | 15 |  | Lobby = |  | 18
IP Units |  |  | Grnd Temp = TG F | [5 empty] | SI Units |  |  | Grnd Temp = TG C | [8 empty] | Std. Atm. Press.
| T = TG - 0.00356 * H | [8 empty] | T = TG - 0.00649 * H | [11 empty] | 101.325 | kPa
| D = 2.7 * PSIa / (T + 459.7) | [8 empty] | D = P / ( 0.2869 * ( T + 273.1 ) ) | [11 empty] | 29.92 | in.Hg
| P (in.Hg) = .296 * P (K-Pa) | [8 empty] | P = 101325 (1 - 2.25577 10-5 H)5.25588 | [11 empty] | 14.696 | PSI
[8 empty] | P = air press. (Pa) |  |  |  |  | H = altitude above sea level (m) | [8 empty] | 407.1828 | in.H2O | Building pressure variations are caused by climatic wind pressure and stack effect (air buoyancy) which results
Stack Efect Press Difference | [5 empty] | (ASHRAE Handbook of Fundamentals) | [10 empty] | Stack Efect Press Difference | [6 empty] | in an uncontrolled air flow into and out of a high rise building. The quantity of uncontrolled ventilation is
| ∆PS = C1 * ρO * [ (TO - TI) / TI ] * g * (HNPL - H) | [20 empty] | (Wikipedia) |  | influenced by indoor-outdoor temperature difference, wind velocity, wind direction, height of the building, and
| ∆PS = |  | Difference (Indoor - Outdoor) Stack Press (in.wg) | [12 empty] | ∆PS = C * Atm.Pr. * H * (1/TO-1/TI) | [7 empty] | building construction. In cold climates air infiltrates into the lower half of the high rise building through doors,
| C1 = |  | Conversion Factor = 0.00598 (in.wg . ft.sec2/lbm) | [8 empty] | 0.00598 | [7 empty] | Var. |  | IP | SI | curtain walls, and other paths and rises to upper floors through shafts and other means due to natural stack
| ρO = |  | Outdoor Air Density at Outdoor Air Temp, lbm/ft3 | [16 empty] | C |  | 0.0188 | 0.0342 | effect and ex-filtrates from the upper half of the building.
| g = |  | gravitational constant |  |  |  | ft/sec2 |  | 32.2 |  | m/sec2 |  | 9.81 | [6 empty] | ∆PS |  | PSI | Pa
| TI = |  | Indr | OR=460+OF |  | OK=273+OC | [13 empty] | At.Pr. |  | PSI | Pa | Wind creates a distribution of static pressure on the building envelope, which is dependent on wind direction
| TO = |  | Outdr | (OR=460+OF) |  | OK=273+OC | [13 empty] | H (ht) |  | Ft | m | and location on building envelope. The basic wind pressure theory is expressed as (Hong Kong Univ, 2001):
| HNPL = |  | Neutral Pr. Plane above Ref Plane, ft (0.5*H appr) | [9 empty] | C2 * ρO* g = |  |  |  | 0.014057 |  |  | TO , TI |  | OR | OK | [5 empty] | ρ = | air density, lbm/ft3 (about 0.075)
| H = |  | Building Height above Reference Plane, (ft) | [25 empty] | V = | wind speed, mph
Wind Pressure |  |  |  | Pushes Outdoor Air on Windward side (+ve) - Pulls Indoor Air on Leeward side (-ve) | [24 empty] | I & o = |  | inside & outside
| ∆PW = C2 * s2 * CP * ρO * (UH)2 / 2 | [17 empty] | feet to meters |  |  |  | 0.3048 | ∆PW = |  | wind pressure difference, in of water |  |  | C = | unit conversion, 0.0129
| ∆PW = |  | Wind Pr. above OA Press (in.wg) | [15 empty] | lbs/ft3 to kg/m3 |  |  |  | 16.0185 | CP = | surface (location on building envelope) pressure coefficient, dimensionless
| C2 = |  | Conv. Factor (in.wg * ft3/lbm * mph2) | [6 empty] | 0.0129 | [8 empty] | m3/hr to ft3/min |  |  |  | 0.58858 | Note: Using above equation, wind pressure is 0.1 in. of H2O at 15 mph on windward side | [10 empty] | (0.4 in. of H2O at 30 mph)
| CP = |  | Wind Surface Pr. Coeff ( = 0.5 to 0.8) | [6 empty] | 0.65 | [8 empty] | mph to Km/hr |  |  |  | 1.609
| s = |  | Shelter Factor (0.4 for example) | [5 empty] | 0.4 | [9 empty] | K-Pa to In.wg |  |  |  | 4.0161 | Air density varies with temperature. In cold weather, low density air infiltrates the building, rises within the high rise
| ρO = |  | OA Density at OA Temp, lbm/ft2 | [15 empty] | K-Pa to In.Hg |  |  |  | 0.2953 | bldg’s vertical shafts as it warms & creates stack effect pressure. The basic stack effect theory is expressed as:
| UH = |  | Effective Wind Speed (mph) | [15 empty] | K-Pa to PSI |  |  |  | 0.14504 | [7 empty] | ∆PS = |  |  | stack pressure, in of water
| (Indoor - Outdor) Press (in. H2O) | [5 empty] | 0.02 |  | to | 0.03 | [8 empty] | Sq.Ft to Sq.M |  |  |  | 0.092903 | [7 empty] | T = |  | temperature, oR
Airflow (Leakge) thru Envelope | [7 empty] | Air Pressue and the Building Envelope by Rick Quirouette | [22 empty] | i & o = |  |  | inside & outside
| Q = Cd * A * ( 2 * ∆P/d )0.5 | [5 empty] | Cd = |  | 0.6 | [6 empty] | Convert |  |  | In.Hg |  | Convert |  | in.H2O | C2, ρ, g = |  |  | air density and gravity constant, 0.01444 |  |  |  | h = |  | height, feet
| or | ∆P = (d/2) * (Q / (Cd * A))2 | [13 empty] | K-Pa |  |  | 3.3864 |  | K-Pa |  | 0.24885 | hneutral = |  |  | height of neutral pressure level
| ∆P = |  | PD across Opening, Pa | [12 empty] | In.H2O |  |  | 13.596 |  | In.Hg |  | 0.073684 | Note: Using the above equation, the stack pressure is 1.1 in. of water for a 60 story building with -10oF OA temp
| Q = |  | Airflow Rate, m3/s | [12 empty] | PSI |  |  | 0.49115 |  | PSI |  | 0.036092
| Cd = |  | Discharge Coeff. for Opening, dimensionless (0.6) | [12 empty] | Kgf/m2 |  |  | 0.034532 |  | Kgf/m2 |  | 25.375 | The resultant pressure difference will cause air flow based on the following expression for flow through an orifice:
| A = |  | cross-sectional area of opening, m2 | [12 empty] | mm.Hg |  |  | 25.4 |  | mm.Hg |  | 186.821 |  |  |  |  | Q = | air flow
| d = |  | density of air, kg/m3 |  |  | Std. Atmos. Press. = | [6 empty] | 14.696 |  | PSI |  | 29.92 |  | in.Hg |  | 407.1828 |  | in.H2O |  |  |  |  | ρ = | air density |  |  | Cf = |  | flow coefficient
[6 empty] | Pressurized Bldg: Indoor Press. - Outdoor Press. = | [15 empty] | 0.035 | in.H2O |  |  |  |  | ∆Ptotal = |  | total pressure difference across flow area

## Ref-Psychro-EQNs
PSYCHROMETRICS |  |  |  | Temp t | C1 | -10214.165 | t (DB) | Dry Bulb Temperature (F) | 78
|  |  |  | < 32 F | C2 | -4.8932 | t" (WB) | Wet Bulb Temperature (F) | 63.5
Z-sl | Altitude (Sea-Level) ft |  | 0 |  | C3 | -0.0053766 | Z | Altitude | 0
P-sl | Std Atmos Press (in. Hg) |  | 29.92 |  | C4 | 1.9202e-07 | P (in.Hg) | Atmospheric Pressure (in. Hg) | 29.92 | 29.92 * ( 1 - 6.8753*10^-6 * Z )^5.2559
DB-sl | Dry Bulb T at Std.Atm.Pr. |  | 68 |  | C5 | 3.5576e-10 | VPs | Water Vapor Press. at Saturation | 0.97005 | pws * 2.041772658
Z | Site Alitude of Project (ft) |  | 1000 |  | C6 | -9.0345e-14 | P (psi) | Entering Pressure (psi) | 14.6539 | P (in.Hg) * 2.041772658
p | Atm. Pr. at Site Altit (in.Hg) |  | 28.8545 |  | C7 | 4.1635 | pw | Partial Press Water Vapor | 0.43686 | ( P_in.Hg * W ) / (0.62198 + W )
t (DB) | Dry Bulb Temperature (F) |  | 95 | Temp t | C8 | -10440.397 | T" | Absolute Temp (R) | 523.17 | t* + 459.67
t" (WB) | Wet Bulb Temperature (F) |  | 75 | > 32 F | C9 | -11.2946 | pws" | Satur Water Vap Pr. ( t > 32 ) | 0.29011 | LN(pws") = C8/T + C9 + C10*T +
P (psi) | Atmos Pressure (psi) |  | 14.6539 |  | C10 | -0.027022 |  |  |  | C11*T^2 + C12*T^3 + C13*LN(T)
VPs | Water Vapor Press. at Saturation |  | 1.6666 |  | C11 | 1.289e-05 | Ws" | Humidity Ratio ( t > 32 ) | 0.012562 | 0.62198 * ( pws" / (P_psi - pws" )
pw | Partial Press Water Vapor |  | 0.66421 |  | C12 | -2.4781e-09 | T | Absolute Temp (R) | 537.67 | t + 459.67
T" | Absolute WB Temp (R) |  | 534.67 |  | C13 | 6.546 | W | Humidity Ratio | 0.0092161 | ( ( 1093 - 0.556*t" ) * Ws" -
pws" | Satur Water Vap Pr. ( t > 32 ) |  | 0.43007 | Temp t | C14 | 100.45 |  |  |  | 0.24 * (t - t") / ( 1093 + 0.444 * t - t")
Ws" | Humidity Ratio ( t > 32 ) |  | 0.018806 | > 32 F | C15 | 33.193 | pws | Satur Water Vap Pr. ( t > 32 ) | 0.4751 | LN(pws_db) = C8/T + C9 + C10*T +
T | Absolute DB Temp (R) |  | 554.67 |  | C16 | 2.319 |  |  |  | C11*T^2 + C12*T^3 + C13*LN(T)
W | Humidity Ratio |  | 0.014121 |  | C17 | 0.17074 | Ws | Humidity Ratio ( t > 32 ) | 0.020841 | 0.62198 * ( Ws / ( P_psi - Ws) )
pws | Satur Water Vap Pr. ( t > 32 ) |  | 0.81625 |  | C18 | 1.2063 | m | Mole Fraction Water Vapor | 0.44221 | W/Ws
Ws | Humidity Ratio ( t > 32 ) |  | 0.036689 | Temp t | C19 | 90.12 | f | Degree of Saturation | 0.45035 | m / (1- (1-m) * ( pws / P_psi ) )
m | Mole Fraction Water Vapor |  | 0.38489 | < 32 F | C20 | 26.142 | a |  | -1.542 | LN ( pw * 0.4897705)
f (DS) | Degree of Saturation |  | 0.39855 |  | C21 | 0.8927 |  | Relative Humidity ( % ) | 45.035 | 100 * f
a |  | a | -1.123 |  |  |  | td (DP) | Dew Point Temperature ( t > 32 ) | 54.1673 | td = C14 + C15*a + C16*a^2 +
u (RH) | Relative Humidity ( % ) |  | 39.8547 | Z | Altitude (Z) |  |  |  |  | C17*a^3 + C18*pw^0.1984
td (DP) | Dew Point Temp ( t > 32 F ) |  | 65.8994 | p | Atmos. Press. (in. Hg) at Alt Z |  | W | Humidity Ratio (lbs/lb) | 0.0092161 | ( ( 1093 - 0.556*t" ) * Ws" -
W | Humidity Ratio (lbs/lb) |  | 0.014121 |  | Atmos. Press. (psi) at Alt Z |  |  |  |  | 0.24 * (t - t") / ( 1093 + 0.444 * t - t")
| Humidity Ratio (grains/lb) |  | 98.8485 |  | Dry Bulb Temp (F) at Alt Z |  |  | Humidity Ratio (grains/lb) | 64.5125 | 7000 * W
H | Enthalpy (btu/lb) |  | 38.3782 | W | Humidity Ratio at DB/WB lbs/lb |  | H | Enthalpy | 28.8174 | 0.24*t + W * (1061 + 0.444*t)
V | Specific Volume (ft3/lb) |  | 14.301 |  | Vapor Pressure at DB/WB |  | V | Specific Volume | 13.7558 | 0.7543 * ( T * (1 + 1.6078*W ) ) / P
|  |  |  | m | Mole Fraction of Water Vapor |  | t (DB) | Dry Bulb (DB) Temp (F)
Pws | Satur. Water Vap Press ( > 32 F) |  |  |  | Relative Humidity (%) |  | td (DP) | Dew Point Temp ( t > 32 F )
Ws | Humidity Ratio (lbs/lb) ( > 32 F ) | [6 empty] | Enthalpy
t* (WB) | Dry Bulb (DB) Temp (F) | [6 empty] | Specific Volume
Pws* | Satur. Water Vap Press ( > 32 F)
Ws* | Humidity Ratio (lbs/lb) ( > 32 F )