## A-Schedules - B-Wind-Pressure
Appendix A: CONTAM Schedule Library |  |  | Appendix B: CONTAM Wind Pressure Profile Library
The table below contains information on the schedules contained in the file SCHEDULE.lb1. |  |  | The table below contains information on the wind pressure profiles contained in the
These generic schedules are based on schedules used previously and can be modified by |  |  | file WINDPRS.lb2.
the user to meet the needs of a particular simulation.
|  |  | Name | Description
Name | Description |  | S&C_1_Both | Swami & Chandra 1987 correlation; long wall (= short); Cp(0) = 0.6
Off | Always off; can be used to turn off or close any element. |  | S&C_2_Long | Swami & Chandra 1987 correlation; long wall (= 2x short); Cp(0) = 0.6
5MIN | 5 min on-time per hour, everyday; can be used for forced-air fans. |  | S&C_2_Short | Swami & Chandra 1987 correlation; short wall (= 1/2 long); Cp(0) = 0.6
10MIN | 10 min on-time per hour, everyday; can be used for forced-air fans. |  | S&C_3_Long | Swami & Chandra 1987 correlation; long wall (= 3x short); Cp(0) = 0.6
15MIN | 15 min on-time per hour, everyday; can be used for forced-air fans. |  | S&C_3_Short | Swami & Chandra 1987 correlation; short wall (= 1/3 long); Cp(0) = 0.6
20MIN | 20 min on-time per hour, everyday; can be used for forced-air fans. |  | LowRoof_01 | Low-rise roof, L/W=1, exposed, pitch < 10 deg
25MIN | 25 min on-time per hour, everyday; can be used for forced-air fans. |  | LowRoof_02 | Low-rise roof, L/W=1, 1/2 height obstructions, pitch < 10 deg
Cooking | Schedule for generation of H2O, particles, combustion products or any contaminant associated with cooking; based on 2 | meals per day on weekdays and 3 meals per day on weekends. | LowRoof_03 | Low-rise roof, L/W=1, building height obstructions, pitch < 10 deg
Kitchfan | Kitchen fan schedule based on cooking; 1 h each at breakfast and dinner on weekdays; 1 h each at breakfast, lunch and | dinner on weekends. | LowRoof_04 | Low-rise roof, L/W=1, exposed, pitch 11-30 deg
Bathfan | Bath exhaust fan schedule based on showers; 30 min per day; time differences |  | LowRoof_05 | Low-rise roof, L/W=1, 1/2 height obstructions, pitch 11-30 deg
|  | for weekdays and weekends. | LowRoof_06 | Low-rise roof, L/W=1, building height obstructions, pitch 11-30 deg
BR-door | Bedroom door schedule, open all day, closed all night; time differences for |  | LowRoof_07 | Low-rise roof, L/W=2, exposed, pitch < 10 deg
|  | weekdays and weekends. | LowRoof_08 | Low-rise roof, L/W=2, 1/2 height obstructions, pitch < 10 deg
|  |  | LowRoof_09 | Low-rise roof, L/W=2, building height obstructions, pitch < 10 deg
|  |  | LowRoof_10 | Low-rise roof, L/W=2, exposed, pitch 11-30 deg
|  |  | LowRoof_11 | Low-rise roof, L/W=2, 1/2 height obstructions, pitch 11-30 deg
|  |  | LowRoof_12 | Low-rise roof, L/W=2, building height obstructions, pitch 11-30 deg

## C1 - Residential
8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 10 | 10 | 9.5 | 9.5 | 11 | 11 | 9.5 | 11 | 11 | 10.5
CALCULATIONS |  | Altit | DB | WB | Altit | Atm.Pr | Atm.Pr. | Atm.Pr. | DP | RH | V | d | W | H | Tdb | Twb
Input | ??? | feet | Tdb (F) | Twb (F) | meters | (Pa) | (in.Hg) | (psi) | F | % | ft3/lb | lb/ft3 | lbs/lb | btu/lb | R | R
Altit-H1, DB, WB |  | 0 | 95 | 75 | 0 | 101325 | 29.9213 | 14.656 | 65.9334 | 39.8692 | 14.3016 | 0.069922 | 0.014138 | 38.3964 | 554.7 | 534.7
Altit-H2 |  | 7500 | 68.3 | 57.45 | 2286 | 76714.1242 | 22.6537 | 11.0962 | 51.1213 | 55.7438 | 17.8892 | 0.0559 | 0.010908 | 28.2963 | 528 | 517.15
∆P = Press Diff (in.wg) across Surface (PI - PO) = | [5 empty] | 0.035 | Cd = | 0.65 | DP: Q = Cd * A * ( 2 * ∆P/d ) ^ 0.5; W: A = Q / ( Cd * ( 2 * ∆P/d ) ^ 0.5 )
Tdb=T-(H2-H1)* |  | 0.00356 | Base Altitude - Intermediate Calcs for DP, RH, V, W, H, T-rankine | [5 empty] | RH: Base Altitude - Intermediate Calcs for DP, RH, V, W, H, T-rankine
Twb=T-(H2-H1)* |  | 0.00234 | PWSwb | WSwb | PWSdb | VPs | VPa | a | WSdb | PWSwb | WSwb | PWSdb | VPs | VPa | a | WSdb
T = 59 - 0.00356*H |  |  | 0.43051 | 0.018823 | 0.817 | 1.6681 | 0.665 | -1.1218 | 0.036719 | 0.23422 | 0.013412 | 0.34309 | 0.7005 | 0.39045 | -1.6543 | 0.019845
0.0010764 | * cm2 = ft2 |  | 0.0001 | * cm2/m2 = ft2/ft2 |  |  | 0.56688 | * cm2/m = ft2/ft | RH: 18.2982; V: * cfm/ft2 = m3/m2; W: 1.699; H: * ft3/min = m3/hr
Appendix C1: Residential Leakage Data Library | [6 empty] | Ref = C1 |  | DP: Converted from NIST CONTAM Library - Leakg-A + Infltr @ Alt-1 & Alt-2 in IP & SI units
National Institute of Standards & Technology - CONTAM Library
Element ID |  | Description |  |  |  |  | Leakg-A | SI units | Leakg-A | IP units | H1 cfm | H2 cfm | IP units | H1 cmh | H2 cmh | SI units
CE_RAV |  | Ceiling, general - estimate |  |  |  |  | 1.8 | cm2/m2 | 0.00018 | ft2/ft2 | 0.00011706 | 0.00013093 | cfm/ft2 | 0.0021421 | 0.0023957 | cmh/m2
CE_RMN |  | Ceiling, general - min |  |  |  |  | 0.79 | cm2/m2 | 7.9e-05 | ft2/ft2 | 5.1378e-05 | 5.7462e-05 | cfm/ft2 | 0.00094013 | 0.0010515 | cmh/m2
CE_RMX |  | Ceiling, general - max |  |  |  |  | 2.8 | cm2/m2 | 0.00028 | ft2/ft2 | 0.0001821 | 0.00020366 | cfm/ft2 | 0.0033321 | 0.0037267 | cmh/m2
CERL_RAV |  | Ceiling penetrations, recessed lights- estimate |  |  |  |  | 10 | cm2/item | 0.010764 | ft2/item | 0.0070004 | 0.0078294 | cfm/item | 0.011894 | 0.14326 | cmh/item
CERL_RMN |  | Ceiling penetrations, recessed lights - min |  |  |  |  | 1.5 | cm2/item | 0.0016146 | ft2/item | 0.0010501 | 0.0011744 | cfm/item | 0.0017841 | 0.02149 | cmh/item
CERL_RMX |  | Ceiling penetrations, recessed lights - max |  |  |  |  | 21 | cm2/item | 0.022604 | ft2/item | 0.014701 | 0.016442 | cfm/item | 0.024977 | 0.30085 | cmh/item
CEWF_RAV |  | Ceiling penetrations, whole house fans - estimate |  |  |  |  | 20 | cm2/item | 0.021528 | ft2/item | 0.014001 | 0.015659 | cfm/item | 0.023787 | 0.28653 | cmh/item
CEWF_RMN |  | Ceiling penetrations, whole house fans - min |  |  |  |  | 1.6 | cm2/item | 0.0017222 | ft2/item | 0.0011201 | 0.0012527 | cfm/item | 0.001903 | 0.022922 | cmh/item
CEWF_RMX |  | Ceiling penetrations, whole house fans - max |  |  |  |  | 21 | cm2/item | 0.022604 | ft2/item | 0.014701 | 0.016442 | cfm/item | 0.024977 | 0.30085 | cmh/item
CH_RAV |  | Chimney- estimate |  |  |  |  | 29 | cm2/item | 0.031215 | ft2/item | 0.020301 | 0.022705 | cfm/item | 0.034492 | 0.41546 | cmh/item
CH_RMN |  | Chimney - min |  |  |  |  | 21 | cm2/item | 0.022604 | ft2/item | 0.014701 | 0.016442 | cfm/item | 0.024977 | 0.30085 | cmh/item
CH_RMX |  | Chimney - max |  |  |  |  | 36 | cm2/item | 0.03875 | ft2/item | 0.025202 | 0.028186 | cfm/item | 0.042817 | 0.51575 | cmh/item
DR_RAV |  | Door, general, average- estimate |  |  |  |  | 0.31 | cm2/m | 0.17573 | ft2/ft | 0.11429 | 0.12782 | cfm/ft | 0.19418 | 2.3389 | cmh/m
DR_RMN |  | Door, general, average - min |  |  |  |  | 0.23 | cm2/m | 0.13038 | ft2/ft | 0.084796 | 0.094837 | cfm/ft | 0.14407 | 1.7353 | cmh/m
DR_RMX |  | Door, general, average - max |  |  |  |  | 0.45 | cm2/m | 0.2551 | ft2/ft | 0.1659 | 0.18555 | cfm/ft | 0.28187 | 3.3952 | cmh/m
DRATCSNW_RAV |  | Doors, attic/crawl space, not wthrstrppd - estimate |  |  |  |  | 30 | cm2/item | 0.032292 | ft2/item | 0.021001 | 0.023488 | cfm/item | 0.035681 | 0.42979 | cmh/item
DRATCSNW_RMN |  | Doors, attic/crawl space, not wthrstrppd - min |  |  |  |  | 10 | cm2/item | 0.010764 | ft2/item | 0.0070004 | 0.0078294 | cfm/item | 0.011894 | 0.14326 | cmh/item
DRATCSNW_RMX |  | Doors, attic/crawl space, not wthrstrppd - max |  |  |  |  | 37 | cm2/item | 0.039826 | ft2/item | 0.025902 | 0.028969 | cfm/item | 0.044007 | 0.53007 | cmh/item
DRATCSWE_RAV |  | Doors, attic/crawl space, wthrstrppd - estimate |  |  |  |  | 18 | cm2/item | 0.019375 | ft2/item | 0.012601 | 0.014093 | cfm/item | 0.021409 | 0.25787 | cmh/item
DRATCSWE_RMN |  | Doors, attic/crawl space, wthrstrppd - min |  |  |  |  | 8 | cm2/item | 0.0086111 | ft2/item | 0.0056003 | 0.0062635 | cfm/item | 0.009515 | 0.11461 | cmh/item
DRATCSWE_RMX |  | Doors, attic/crawl space, wthrstrppd - max |  |  |  |  | 18.5 | cm2/item | 0.019913 | ft2/item | 0.012951 | 0.014484 | cfm/item | 0.022003 | 0.26504 | cmh/item
DRATFDNW_RAV |  | Doors, attic fold down, not wthrstrppd - estimate |  |  |  |  | 44 | cm2/item | 0.047361 | ft2/item | 0.030802 | 0.034449 | cfm/item | 0.052332 | 0.63036 | cmh/item
DRATFDNW_RMN |  | Doors, attic fold down, not wthrstrppd - min |  |  |  |  | 23 | cm2/item | 0.024757 | ft2/item | 0.016101 | 0.018008 | cfm/item | 0.027356 | 0.32951 | cmh/item
DRATFDNW_RMX |  | Doors, attic fold down, not wthrstrppd - max |  |  |  |  | 86 | cm2/item | 0.09257 | ft2/item | 0.060204 | 0.067333 | cfm/item | 0.10229 | 1.2321 | cmh/item
DRATFDWE_RAV |  | Doors, attic fold down, wthrstrppd - estimate |  |  |  |  | 22 | cm2/item | 0.023681 | ft2/item | 0.015401 | 0.017225 | cfm/item | 0.026166 | 0.31518 | cmh/item
DRATFDWE_RMN |  | Doors, attic fold down, wthrstrppd - min |  |  |  |  | 14 | cm2/item | 0.015069 | ft2/item | 0.0098006 | 0.010961 | cfm/item | 0.016651 | 0.20057 | cmh/item
DRATFDWE_RMX |  | Doors, attic fold down, wthrstrppd - max |  |  |  |  | 43 | cm2/item | 0.046285 | ft2/item | 0.030102 | 0.033666 | cfm/item | 0.051143 | 0.61603 | cmh/item
DRDBNW_RAV |  | Door, double, not wthrstrppd- estimate |  |  |  |  | 11 | cm2/m2 | 0.0011 | ft2/ft2 | 0.0007154 | 0.00080011 | cfm/ft2 | 0.01309 | 0.014641 | cmh/m2
DRDBNW_RMN |  | Door, double, not wthrstrppd - min |  |  |  |  | 7 | cm2/m2 | 0.0007 | ft2/ft2 | 0.00045525 | 0.00050916 | cfm/ft2 | 0.0083303 | 0.0093167 | cmh/m2
DRDBNW_RMX |  | Door, double, not wthrstrppd - max |  |  |  |  | 22 | cm2/m2 | 0.0022 | ft2/ft2 | 0.0014308 | 0.0016002 | cfm/ft2 | 0.026181 | 0.029281 | cmh/m2
DRDBWE_RAV |  | Door, double, wthrstrppd- estimate |  |  |  |  | 8 | cm2/m2 | 0.0008 | ft2/ft2 | 0.00052029 | 0.0005819 | cfm/ft2 | 0.0095203 | 0.010648 | cmh/m2
DRDBWE_RMN |  | Door, double, wthrstrppd - min |  |  |  |  | 3 | cm2/m2 | 0.0003 | ft2/ft2 | 0.00019511 | 0.00021821 | cfm/ft2 | 0.0035701 | 0.0039929 | cmh/m2
DRDBWE_RMX |  | Door, double, wthrstrppd - max |  |  |  |  | 23 | cm2/m2 | 0.0023 | ft2/ft2 | 0.0014958 | 0.001673 | cfm/ft2 | 0.027371 | 0.030612 | cmh/m2
DREL_CAV |  | Doors, elevator (passenger) - estimate |  |  |  |  | 0.26 | cm2/item | 0.00027986 | ft2/item | 0.00018201 | 0.00020356 | cfm/item | 0.00030924 | 0.0037248 | cmh/item
DREL_CMN |  | Doors, elevator (passenger) - min |  |  |  |  | 0.14 | cm2/item | 0.00015069 | ft2/item | 9.8006e-05 | 0.00010961 | cfm/item | 0.00016651 | 0.0020057 | cmh/item
DREL_CMX |  | Doors, elevator (passenger) - max |  |  |  |  | 0.35 | cm2/item | 0.00037674 | ft2/item | 0.00024501 | 0.00027403 | cfm/item | 0.00041628 | 0.0050142 | cmh/item
DRMS_RAV |  | Door, mail slot - estimate |  |  |  |  | 4 | cm2/m | 2.2675 | ft2/ft | 1.4747 | 1.6493 | cfm/ft | 2.5055 | 30.1798 | cmh/m
DRPTSLAR_RAV |  | Door, sliding exterior glass patio - estimate |  |  |  |  | 5.5 | cm2/m2 | 0.00055 | ft2/ft2 | 0.0003577 | 0.00040006 | cfm/ft2 | 0.0065452 | 0.0073203 | cmh/m2
DRPTSLAR_RMN |  | Door, sliding exterior glass patio - min |  |  |  |  | 0.6 | cm2/m2 | 6e-05 | ft2/ft2 | 3.9022e-05 | 4.3642e-05 | cfm/ft2 | 0.00071402 | 0.00079858 | cmh/m2
DRPTSLAR_RMX |  | Door, sliding exterior glass patio - max |  |  |  |  | 15 | cm2/m2 | 0.0015 | ft2/ft2 | 0.00097554 | 0.0010911 | cfm/ft2 | 0.017851 | 0.019964 | cmh/m2
DRPTSLUN_RAV |  | Door, sliding exterior glass patio - estimate |  |  |  |  | 22 | cm2/item | 0.023681 | ft2/item | 0.015401 | 0.017225 | cfm/item | 0.026166 | 0.31518 | cmh/item
DRPTSLUN_RMN |  | Door, sliding exterior glass patio - min |  |  |  |  | 3 | cm2/item | 0.0032292 | ft2/item | 0.0021001 | 0.0023488 | cfm/item | 0.0035681 | 0.042979 | cmh/item
DRPTSLUN_RMX |  | Door, sliding exterior glass patio - max |  |  |  |  | 60 | cm2/item | 0.064583 | ft2/item | 0.042003 | 0.046976 | cfm/item | 0.071362 | 0.85958 | cmh/item
DRSINW_RAV |  | Door, single, not wthrstrppd - estimate |  |  |  |  | 21 | cm2/item | 0.022604 | ft2/item | 0.014701 | 0.016442 | cfm/item | 0.024977 | 0.30085 | cmh/item
DRSINW_RMN |  | Door, single, not wthrstrppd - min |  |  |  |  | 12 | cm2/item | 0.012917 | ft2/item | 0.0084005 | 0.0093953 | cfm/item | 0.014272 | 0.17192 | cmh/item
DRSINW_RMX |  | Door, single, not wthrstrppd - max |  |  |  |  | 53 | cm2/item | 0.057049 | ft2/item | 0.037102 | 0.041496 | cfm/item | 0.063037 | 0.7593 | cmh/item
DRSIWE_RAV |  | Door, single, wthrstrppd - estimate |  |  |  |  | 12 | cm2/item | 0.012917 | ft2/item | 0.0084005 | 0.0093953 | cfm/item | 0.014272 | 0.17192 | cmh/item
DRSIWE_RMN |  | Door, single, wthrstrppd - min |  |  |  |  | 4 | cm2/item | 0.0043056 | ft2/item | 0.0028002 | 0.0031318 | cfm/item | 0.0047575 | 0.057305 | cmh/item
DRSIWE_RMX |  | Door, single, wthrstrppd - max |  |  |  |  | 27 | cm2/item | 0.029063 | ft2/item | 0.018901 | 0.021139 | cfm/item | 0.032113 | 0.38681 | cmh/item
DRSMDE_RAV |  | Door, storm (difference between with and without) - estimate |  |  |  |  | 6 | cm2/item | 0.0064583 | ft2/item | 0.0042003 | 0.0046976 | cfm/item | 0.0071362 | 0.085958 | cmh/item
DRSMDE_RMN |  | Door, storm (difference between with and without) - min |  |  |  |  | 3 | cm2/item | 0.0032292 | ft2/item | 0.0021001 | 0.0023488 | cfm/item | 0.0035681 | 0.042979 | cmh/item
DRSMDE_RMX |  | Door, storm (difference between with and without) - max |  |  |  |  | 6.2 | cm2/item | 0.0066736 | ft2/item | 0.0043403 | 0.0048542 | cfm/item | 0.0073741 | 0.088823 | cmh/item
FLCS_RAV |  | Floors over crawl spaces, general - estimate |  |  |  |  | 2.2 | cm2/m2 | 0.00022 | ft2/ft2 | 0.00014308 | 0.00016002 | cfm/ft2 | 0.0026181 | 0.0029281 | cmh/m2
FLCS_RMN |  | Floors over crawl spaces, general - min |  |  |  |  | 0.4 | cm2/m2 | 4e-05 | ft2/ft2 | 2.6014e-05 | 2.9095e-05 | cfm/ft2 | 0.00047602 | 0.00053238 | cmh/m2
FLCS_RMX |  | Floors over crawl spaces, general - max |  |  |  |  | 4.9 | cm2/m2 | 0.00049 | ft2/ft2 | 0.00031868 | 0.00035641 | cfm/ft2 | 0.0058312 | 0.0065217 | cmh/m2
FLCSNODW_RAV |  | Floors over crawl spaces, without ductwork in crawl space - estimate |  |  |  |  | 1.98 | cm2/m2 | 0.000198 | ft2/ft2 | 0.00012877 | 0.00014402 | cfm/ft2 | 0.0023563 | 0.0026353 | cmh/m2
FLCSYEDW_RAV |  | Floors over crawl spaces, with ductwork in crawl space - estimate |  |  |  |  | 2.25 | cm2/m2 | 0.000225 | ft2/ft2 | 0.00014633 | 0.00016366 | cfm/ft2 | 0.0026776 | 0.0029947 | cmh/m2
FPDACL_RAV |  | Fireplace, with damper closed - estimate |  |  |  |  | 43 | cm2/m2 | 0.0043 | ft2/ft2 | 0.0027965 | 0.0031277 | cfm/ft2 | 0.051172 | 0.057231 | cmh/m2
FPDACL_RMN |  | Fireplace, with damper closed - min |  |  |  |  | 10 | cm2/m2 | 0.001 | ft2/ft2 | 0.00065036 | 0.00072737 | cfm/ft2 | 0.0119 | 0.01331 | cmh/m2
FPDACL_RMX |  | Fireplace, with damper closed - max |  |  |  |  | 92 | cm2/m2 | 0.0092 | ft2/ft2 | 0.0059833 | 0.0066918 | cfm/ft2 | 0.10948 | 0.12245 | cmh/m2
FPDAOP_RAV |  | Fireplace, with damper open - estimate |  |  |  |  | 350 | cm2/m2 | 0.035 | ft2/ft2 | 0.022763 | 0.025458 | cfm/ft2 | 0.41651 | 0.46584 | cmh/m2
FPDAOP_RMN |  | Fireplace, with damper open - min |  |  |  |  | 145 | cm2/m2 | 0.0145 | ft2/ft2 | 0.0094302 | 0.010547 | cfm/ft2 | 0.17256 | 0.19299 | cmh/m2
FPDAOP_RMX |  | Fireplace, with damper open - max |  |  |  |  | 380 | cm2/m2 | 0.038 | ft2/ft2 | 0.024714 | 0.02764 | cfm/ft2 | 0.45222 | 0.50576 | cmh/m2
FPGLDR_RAV |  | Fireplace, with glass doors - estimate |  |  |  |  | 40 | cm2/m2 | 0.004 | ft2/ft2 | 0.0026014 | 0.0029095 | cfm/ft2 | 0.047602 | 0.053238 | cmh/m2
FPGLDR_RMN |  | Fireplace, with glass doors - min |  |  |  |  | 4 | cm2/m2 | 0.0004 | ft2/ft2 | 0.00026014 | 0.00029095 | cfm/ft2 | 0.0047602 | 0.0053238 | cmh/m2
FPGLDR_RMX |  | Fireplace, with glass doors - max |  |  |  |  | 40 | cm2/m2 | 0.004 | ft2/ft2 | 0.0026014 | 0.0029095 | cfm/ft2 | 0.047602 | 0.053238 | cmh/m2
FRDR_RAV |  | Door frame, general - estimate |  |  |  |  | 12 | cm2/item | 0.012917 | ft2/item | 0.0084005 | 0.0093953 | cfm/item | 0.014272 | 0.17192 | cmh/item
FRDR_RMN |  | Door frame, general - min |  |  |  |  | 2.4 | cm2/item | 0.0025833 | ft2/item | 0.0016801 | 0.0018791 | cfm/item | 0.0028545 | 0.034383 | cmh/item
FRDR_RMX |  | Door frame, general - max |  |  |  |  | 25 | cm2/item | 0.02691 | ft2/item | 0.017501 | 0.019573 | cfm/item | 0.029734 | 0.35816 | cmh/item
FRDRMACA_RAV |  | Door frame, masonry, caulked - estimate |  |  |  |  | 1 | cm2/m2 | 0.0001 | ft2/ft2 | 6.5036e-05 | 7.2737e-05 | cfm/ft2 | 0.00119 | 0.001331 | cmh/m2
FRDRMACA_RMN |  | Door frame, masonry, caulked - min |  |  |  |  | 0.3 | cm2/m2 | 3e-05 | ft2/ft2 | 1.9511e-05 | 2.1821e-05 | cfm/ft2 | 0.00035701 | 0.00039929 | cmh/m2
FRDRMACA_RMX |  | Door frame, masonry, caulked - max |  |  |  |  | 1 | cm2/m2 | 0.0001 | ft2/ft2 | 6.5036e-05 | 7.2737e-05 | cfm/ft2 | 0.00119 | 0.001331 | cmh/m2
FRDRMAUC_RAV |  | Door frame, masonry, uncaulked - estimate |  |  |  |  | 5 | cm2/m2 | 0.0005 | ft2/ft2 | 0.00032518 | 0.00036369 | cfm/ft2 | 0.0059502 | 0.0066548 | cmh/m2
FRDRMAUC_RMN |  | Door frame, masonry, uncaulked - min |  |  |  |  | 1.7 | cm2/m2 | 0.00017 | ft2/ft2 | 0.00011056 | 0.00012365 | cfm/ft2 | 0.0020231 | 0.0022626 | cmh/m2
FRDRMAUC_RMX |  | Door frame, masonry, uncaulked - max |  |  |  |  | 5 | cm2/m2 | 0.0005 | ft2/ft2 | 0.00032518 | 0.00036369 | cfm/ft2 | 0.0059502 | 0.0066548 | cmh/m2
FRDRWDCA_RAV |  | Door frame, wood, caulked - estimate |  |  |  |  | 0.3 | cm2/m2 | 3e-05 | ft2/ft2 | 1.9511e-05 | 2.1821e-05 | cfm/ft2 | 0.00035701 | 0.00039929 | cmh/m2
FRDRWDCA_RMN |  | Door frame, wood, caulked - min |  |  |  |  | 0.1 | cm2/m2 | 1e-05 | ft2/ft2 | 6.5036e-06 | 7.2737e-06 | cfm/ft2 | 0.000119 | 0.0001331 | cmh/m2
FRDRWDCA_RMX |  | Door frame, wood, caulked - max |  |  |  |  | 0.3 | cm2/m2 | 3e-05 | ft2/ft2 | 1.9511e-05 | 2.1821e-05 | cfm/ft2 | 0.00035701 | 0.00039929 | cmh/m2
FRDRWDUC_RAV |  | Door frame, wood, uncaulked - estimate |  |  |  |  | 1.7 | cm2/m2 | 0.00017 | ft2/ft2 | 0.00011056 | 0.00012365 | cfm/ft2 | 0.0020231 | 0.0022626 | cmh/m2
FRDRWDUC_RMN |  | Door frame, wood, uncaulked - min |  |  |  |  | 0.6 | cm2/m2 | 6e-05 | ft2/ft2 | 3.9022e-05 | 4.3642e-05 | cfm/ft2 | 0.00071402 | 0.00079858 | cmh/m2
FRDRWDUC_RMX |  | Door frame, wood, uncaulked - max |  |  |  |  | 1.7 | cm2/m2 | 0.00017 | ft2/ft2 | 0.00011056 | 0.00012365 | cfm/ft2 | 0.0020231 | 0.0022626 | cmh/m2
FRWNMACA_RAV |  | Window framing, masonry, caulked - estimate |  |  |  |  | 1.3 | cm2/m2 | 0.00013 | ft2/ft2 | 8.4547e-05 | 9.4559e-05 | cfm/ft2 | 0.0015471 | 0.0017302 | cmh/m2
FRWNMACA_RMN |  | Window framing, masonry, caulked - min |  |  |  |  | 1.1 | cm2/m2 | 0.00011 | ft2/ft2 | 7.154e-05 | 8.0011e-05 | cfm/ft2 | 0.001309 | 0.0014641 | cmh/m2
FRWNMACA_RMX |  | Window framing, masonry, caulked - max |  |  |  |  | 2.1 | cm2/m2 | 0.00021 | ft2/ft2 | 0.00013658 | 0.00015275 | cfm/ft2 | 0.0024991 | 0.002795 | cmh/m2
FRWNMAUC_RAV |  | Window framing, masonry, uncaulked - estimate |  |  |  |  | 6.5 | cm2/m2 | 0.00065 | ft2/ft2 | 0.00042273 | 0.00047279 | cfm/ft2 | 0.0077353 | 0.0086512 | cmh/m2
FRWNMAUC_RMN |  | Window framing, masonry, uncaulked - min |  |  |  |  | 5.7 | cm2/m2 | 0.00057 | ft2/ft2 | 0.00037071 | 0.0004146 | cfm/ft2 | 0.0067832 | 0.0075865 | cmh/m2
FRWNMAUC_RMX |  | Window framing, masonry, uncaulked - max |  |  |  |  | 10.3 | cm2/m2 | 0.00103 | ft2/ft2 | 0.00066987 | 0.00074919 | cfm/ft2 | 0.012257 | 0.013709 | cmh/m2
FRWNWDCA_RAV |  | Window framing, wood, caulked - estimate |  |  |  |  | 0.3 | cm2/m2 | 3e-05 | ft2/ft2 | 1.9511e-05 | 2.1821e-05 | cfm/ft2 | 0.00035701 | 0.00039929 | cmh/m2
FRWNWDCA_RMN |  | Window framing, wood, caulked - min |  |  |  |  | 0.3 | cm2/m2 | 3e-05 | ft2/ft2 | 1.9511e-05 | 2.1821e-05 | cfm/ft2 | 0.00035701 | 0.00039929 | cmh/m2
FRWNWDCA_RMX |  | Window framing, wood, caulked - max |  |  |  |  | 0.5 | cm2/m2 | 5e-05 | ft2/ft2 | 3.2518e-05 | 3.6369e-05 | cfm/ft2 | 0.00059502 | 0.00066548 | cmh/m2
FRWNWDUC_RAV |  | Window framing, wood, uncaulked - estimate |  |  |  |  | 1.7 | cm2/m2 | 0.00017 | ft2/ft2 | 0.00011056 | 0.00012365 | cfm/ft2 | 0.0020231 | 0.0022626 | cmh/m2
FRWNWDUC_RMN |  | Window framing, wood, uncaulked - min |  |  |  |  | 1.5 | cm2/m2 | 0.00015 | ft2/ft2 | 9.7554e-05 | 0.00010911 | cfm/ft2 | 0.0017851 | 0.0019964 | cmh/m2
FRWNWDUC_RMX |  | Window framing, wood, uncaulked - max |  |  |  |  | 2.7 | cm2/m2 | 0.00027 | ft2/ft2 | 0.0001756 | 0.00019639 | cfm/ft2 | 0.0032131 | 0.0035936 | cmh/m2
JTCEWL_RAV |  | Joints, ceiling wall - estimate |  |  |  |  | 1.5 | cm2/m | 0.85032 | ft2/ft | 0.55301 | 0.6185 | cfm/ft | 0.93957 | 11.3174 | cmh/m
JTCEWL_RMN |  | Joints, ceiling wall - min |  |  |  |  | 0.16 | cm2/m | 0.090701 | ft2/ft | 0.058988 | 0.065973 | cfm/ft | 0.10022 | 1.2072 | cmh/m
JTCEWL_RMX |  | Joints, ceiling wall - max |  |  |  |  | 2.5 | cm2/m | 1.4172 | ft2/ft | 0.92169 | 1.0308 | cfm/ft | 1.566 | 18.8624 | cmh/m
JTFLWLCA_RAV |  | Joints, sole plate, floor/wall, caulked- estimate |  |  |  |  | 0.8 | cm2/m | 0.4535 | ft2/ft | 0.29494 | 0.32987 | cfm/ft | 0.5011 | 6.036 | cmh/m
JTFLWLCA_RMN |  | Joints, sole plate, floor/wall, caulked - min |  |  |  |  | 0.075 | cm2/m | 0.042516 | ft2/ft | 0.027651 | 0.030925 | cfm/ft | 0.046979 | 0.56587 | cmh/m
JTFLWLCA_RMX |  | Joints, sole plate, floor/wall, caulked - max |  |  |  |  | 1.2 | cm2/m | 0.68026 | ft2/ft | 0.44241 | 0.4948 | cfm/ft | 0.75166 | 9.0539 | cmh/m
JTFLWLUC _RMN |  | Joints, sole plate, floor/wall, uncaulked - min |  |  |  |  | 0.38 | cm2/m | 0.21541 | ft2/ft | 0.1401 | 0.15669 | cfm/ft | 0.23802 | 2.8671 | cmh/m
JTFLWLUC _RMX |  | Joints, sole plate, floor/wall, uncaulked - max |  |  |  |  | 5.6 | cm2/m | 3.1745 | ft2/ft | 2.0646 | 2.3091 | cfm/ft | 3.5077 | 42.2517 | cmh/m
JTFLWLUC_RAV |  | Joints, sole plate, floor/wall, uncaulked - estimate |  |  |  |  | 4 | cm2/m | 2.2675 | ft2/ft | 1.4747 | 1.6493 | cfm/ft | 2.5055 | 30.1798 | cmh/m
PECA_RAV |  | Piping/Plumbing/Wiring penetrations, caulked - estimate |  |  |  |  | 2 | cm2/item | 0.0021528 | ft2/item | 0.0014001 | 0.0015659 | cfm/item | 0.0023787 | 0.028653 | cmh/item
PECA_RMN |  | Piping/Plumbing/Wiring penetrations, caulked - min |  |  |  |  | 1 | cm2/item | 0.0010764 | ft2/item | 0.00070004 | 0.00078294 | cfm/item | 0.0011894 | 0.014326 | cmh/item
PECA_RMX |  | Piping/Plumbing/Wiring penetrations, caulked - max |  |  |  |  | 2 | cm2/item | 0.0021528 | ft2/item | 0.0014001 | 0.0015659 | cfm/item | 0.0023787 | 0.028653 | cmh/item
PEECCA_RAV |  | Electrical outlets/switches, gaskets - estimate |  |  |  |  | 0.15 | cm2/item | 0.00016146 | ft2/item | 0.00010501 | 0.00011744 | cfm/item | 0.00017841 | 0.002149 | cmh/item
PEECCA_RMN |  | Electrical outlets/switches, gaskets - min |  |  |  |  | 0.08 | cm2/item | 8.6111e-05 | ft2/item | 5.6003e-05 | 6.2635e-05 | cfm/item | 9.515e-05 | 0.0011461 | cmh/item
PEECCA_RMX |  | Electrical outlets/switches, gaskets - max |  |  |  |  | 3.5 | cm2/item | 0.0037674 | ft2/item | 0.0024501 | 0.0027403 | cfm/item | 0.0041628 | 0.050142 | cmh/item
PEECUC_RAV |  | Electrical outlets/switches, no gaskets - estimate |  |  |  |  | 2.5 | cm2/item | 0.002691 | ft2/item | 0.0017501 | 0.0019573 | cfm/item | 0.0029734 | 0.035816 | cmh/item
PEECUC_RMN |  | Electrical outlets/switches, no gaskets - min |  |  |  |  | 0.5 | cm2/item | 0.0005382 | ft2/item | 0.00035002 | 0.00039147 | cfm/item | 0.00059469 | 0.0071632 | cmh/item
PEECUC_RMX |  | Electrical outlets/switches, no gaskets - max |  |  |  |  | 6.2 | cm2/item | 0.0066736 | ft2/item | 0.0043403 | 0.0048542 | cfm/item | 0.0073741 | 0.088823 | cmh/item
PEUC_RAV |  | Piping/Plumbing/Wiring penetrations, uncaulked - estimate |  |  |  |  | 6 | cm2/item | 0.0064583 | ft2/item | 0.0042003 | 0.0046976 | cfm/item | 0.0071362 | 0.085958 | cmh/item
PEUC_RMN |  | Piping/Plumbing/Wiring penetrations, uncaulked - min |  |  |  |  | 2 | cm2/item | 0.0021528 | ft2/item | 0.0014001 | 0.0015659 | cfm/item | 0.0023787 | 0.028653 | cmh/item
PEUC_RMX |  | Piping/Plumbing/Wiring penetrations, uncaulked - max |  |  |  |  | 24 | cm2/item | 0.025833 | ft2/item | 0.016801 | 0.018791 | cfm/item | 0.028545 | 0.34383 | cmh/item
VEBADACL_RAV |  | Vents, bathroom with damper closed- estimate |  |  |  |  | 10 | cm2/item | 0.010764 | ft2/item | 0.0070004 | 0.0078294 | cfm/item | 0.011894 | 0.14326 | cmh/item
VEBADACL_RMN |  | Vents, bathroom with damper closed - min |  |  |  |  | 2.5 | cm2/item | 0.002691 | ft2/item | 0.0017501 | 0.0019573 | cfm/item | 0.0029734 | 0.035816 | cmh/item
VEBADACL_RMX |  | Vents, bathroom with damper closed - max |  |  |  |  | 20 | cm2/item | 0.021528 | ft2/item | 0.014001 | 0.015659 | cfm/item | 0.023787 | 0.28653 | cmh/item
VEBADAOP_RAV |  | Vents, bathroom with damper open- estimate |  |  |  |  | 20 | cm2/item | 0.021528 | ft2/item | 0.014001 | 0.015659 | cfm/item | 0.023787 | 0.28653 | cmh/item
VEBADAOP_RMN |  | Vents, bathroom with damper open - min |  |  |  |  | 6.1 | cm2/item | 0.006566 | ft2/item | 0.0042703 | 0.0047759 | cfm/item | 0.0072552 | 0.087391 | cmh/item
VEBADAOP_RMX |  | Vents, bathroom with damper open - max |  |  |  |  | 22 | cm2/item | 0.023681 | ft2/item | 0.015401 | 0.017225 | cfm/item | 0.026166 | 0.31518 | cmh/item
VECS_RAV |  | Crawl space, 200 mm by 400 mm vent - estimate |  |  |  |  | 129 | cm2/item | 0.13885 | ft2/item | 0.090305 | 0.101 | cfm/item | 0.15343 | 1.8481 | cmh/item
VEDYDANO_RAV |  | Vents, dryer without damper- estimate |  |  |  |  | 15 | cm2/item | 0.016146 | ft2/item | 0.010501 | 0.011744 | cfm/item | 0.017841 | 0.2149 | cmh/item
VEDYDANO_RMN |  | Vents, dryer without damper - min |  |  |  |  | 12 | cm2/item | 0.012917 | ft2/item | 0.0084005 | 0.0093953 | cfm/item | 0.014272 | 0.17192 | cmh/item
VEDYDANO_RMX |  | Vents, dryer without damper - max |  |  |  |  | 34 | cm2/item | 0.036597 | ft2/item | 0.023801 | 0.02662 | cfm/item | 0.040439 | 0.4871 | cmh/item
VEDYDAYE_RAV |  | Vents, dryer with damper- estimate |  |  |  |  | 3 | cm2/item | 0.0032292 | ft2/item | 0.0021001 | 0.0023488 | cfm/item | 0.0035681 | 0.042979 | cmh/item
VEDYDAYE_RMN |  | Vents, dryer with damper - min |  |  |  |  | 2.9 | cm2/item | 0.0031215 | ft2/item | 0.0020301 | 0.0022705 | cfm/item | 0.0034492 | 0.041546 | cmh/item
VEDYDAYE_RMX |  | Vents, dryer with damper - max |  |  |  |  | 7 | cm2/item | 0.0075347 | ft2/item | 0.0049003 | 0.0054806 | cfm/item | 0.0083256 | 0.10028 | cmh/item
VEKIDACA_RAV |  | Vents, kitchen tight gasket - estimate |  |  |  |  | 1 | cm2/item | 0.0010764 | ft2/item | 0.00070004 | 0.00078294 | cfm/item | 0.0011894 | 0.014326 | cmh/item
VEKIDACL_RAV |  | Vents, kitchen with damper open - estimate |  |  |  |  | 5 | cm2/item | 0.005382 | ft2/item | 0.0035002 | 0.0039147 | cfm/item | 0.0059469 | 0.071632 | cmh/item
VEKIDACL_RMN |  | Vents, kitchen with damper open - min |  |  |  |  | 1 | cm2/item | 0.0010764 | ft2/item | 0.00070004 | 0.00078294 | cfm/item | 0.0011894 | 0.014326 | cmh/item
VEKIDACL_RMX |  | Vents, kitchen with damper open - max |  |  |  |  | 7 | cm2/item | 0.0075347 | ft2/item | 0.0049003 | 0.0054806 | cfm/item | 0.0083256 | 0.10028 | cmh/item
VEKIDAOP_RAV |  | Vents, kitchen with damper open - estimate |  |  |  |  | 40 | cm2/item | 0.043056 | ft2/item | 0.028002 | 0.031318 | cfm/item | 0.047575 | 0.57305 | cmh/item
VEKIDAOP_RMN |  | Vents, kitchen with damper open - min |  |  |  |  | 14 | cm2/item | 0.015069 | ft2/item | 0.0098006 | 0.010961 | cfm/item | 0.016651 | 0.20057 | cmh/item
VEKIDAOP_RMX |  | Vents, kitchen with damper open - max |  |  |  |  | 72 | cm2/item | 0.0775 | ft2/item | 0.050403 | 0.056372 | cfm/item | 0.085635 | 1.0315 | cmh/item
WCCASEWE _RMN |  | Windows, casement with weatherstripping -min |  |  |  |  | 0.1 | cm2/m | 0.056688 | ft2/ft | 0.036868 | 0.041233 | cfm/ft | 0.062638 | 0.75449 | cmh/m
WCCASEWE _RMX |  | Windows, casement with weatherstripping -max |  |  |  |  | 3 | cm2/m | 1.7006 | ft2/ft | 1.106 | 1.237 | cfm/ft | 1.8791 | 22.6348 | cmh/m
WCCASEWE_RAV |  | Windows, casement with weatherstripping - estimate |  |  |  |  | 0.24 | cm2/m | 0.13605 | ft2/ft | 0.088482 | 0.09896 | cfm/ft | 0.15033 | 1.8108 | cmh/m
WHGS_RAV |  | Gas water heater - estimate |  |  |  |  | 20 | cm2/item | 0.021528 | ft2/item | 0.014001 | 0.015659 | cfm/item | 0.023787 | 0.28653 | cmh/item
WHGS_RMN |  | Gas water heater - min |  |  |  |  | 15 | cm2/item | 0.016146 | ft2/item | 0.010501 | 0.011744 | cfm/item | 0.017841 | 0.2149 | cmh/item
WHGS_RMX |  | Gas water heater - max |  |  |  |  | 25 | cm2/item | 0.02691 | ft2/item | 0.017501 | 0.019573 | cfm/item | 0.029734 | 0.35816 | cmh/item
WLCS_RAV |  | Crawl space, general (area for exposed wall) - estimate |  |  |  |  | 10 | cm2/m2 | 0.001 | ft2/ft2 | 0.00065036 | 0.00072737 | cfm/ft2 | 0.0119 | 0.01331 | cmh/m2
WLCS_RMN |  | Crawl space, general (area for exposed wall) - min |  |  |  |  | 8 | cm2/m2 | 0.0008 | ft2/ft2 | 0.00052029 | 0.0005819 | cfm/ft2 | 0.0095203 | 0.010648 | cmh/m2
WLCS_RMX |  | Crawl space, general (area for exposed wall) - max |  |  |  |  | 17 | cm2/m2 | 0.0017 | ft2/ft2 | 0.0011056 | 0.0012365 | cfm/ft2 | 0.020231 | 0.022626 | cmh/m2
WLEXCC_RAV |  | Walls (exterior), cast-in-place concrete - estimate |  |  |  |  | 0.5 | cm2/m2 | 5e-05 | ft2/ft2 | 3.2518e-05 | 3.6369e-05 | cfm/ft2 | 0.00059502 | 0.00066548 | cmh/m2
WLEXCC_RMN |  | Walls (exterior), cast-in-place concrete - min |  |  |  |  | 0.049 | cm2/m2 | 4.9e-06 | ft2/ft2 | 3.1868e-06 | 3.5641e-06 | cfm/ft2 | 5.8312e-05 | 6.5217e-05 | cmh/m2
WLEXCC_RMX |  | Walls (exterior), cast-in-place concrete - max |  |  |  |  | 1.8 | cm2/m2 | 0.00018 | ft2/ft2 | 0.00011706 | 0.00013093 | cfm/ft2 | 0.0021421 | 0.0023957 | cmh/m2
WLEXPC_RAV |  | Walls (exterior), precast concrete panel - estimate |  |  |  |  | 1.2 | cm2/m2 | 0.00012 | ft2/ft2 | 7.8043e-05 | 8.7285e-05 | cfm/ft2 | 0.001428 | 0.0015972 | cmh/m2
WLEXPC_RMN |  | Walls (exterior), precast concrete panel - min |  |  |  |  | 0.28 | cm2/m2 | 2.8e-05 | ft2/ft2 | 1.821e-05 | 2.0366e-05 | cfm/ft2 | 0.00033321 | 0.00037267 | cmh/m2
WLEXPC_RMX |  | Walls (exterior), precast concrete panel - max |  |  |  |  | 1.65 | cm2/m2 | 0.000165 | ft2/ft2 | 0.00010731 | 0.00012002 | cfm/ft2 | 0.0019636 | 0.0021961 | cmh/m2
WNCASENW_RAV |  | Windows, casement, not wthrstrppd - estimate |  |  |  |  | 0.28 | cm2/m | 0.15873 | ft2/ft | 0.10323 | 0.11545 | cfm/ft | 0.17539 | 2.1126 | cmh/m
WNDBNW_RAV |  | Windows, double hung, not wthrstrppd - estimate |  |  |  |  | 2.5 | cm2/m | 1.4172 | ft2/ft | 0.92169 | 1.0308 | cfm/ft | 1.566 | 18.8624 | cmh/m
WNDBNW_RMN |  | Windows, double hung, not wthrstrppd -min |  |  |  |  | 0.86 | cm2/m | 0.48752 | ft2/ft | 0.31706 | 0.35461 | cfm/ft | 0.53869 | 6.4887 | cmh/m
WNDBNW_RMX |  | Windows, double hung, not wthrstrppd -max |  |  |  |  | 6.1 | cm2/m | 3.458 | ft2/ft | 2.2489 | 2.5152 | cfm/ft | 3.8209 | 46.0242 | cmh/m
WNDBNWSM_RAV |  | Windows, double hung with storm, not wthrstrppd - estimate |  |  |  |  | 0.97 | cm2/m | 0.54987 | ft2/ft | 0.35762 | 0.39996 | cfm/ft | 0.60759 | 7.3186 | cmh/m
WNDBNWSM_RMN |  | Windows, double hung with storm, not wthrstrppd -min |  |  |  |  | 0.48 | cm2/m | 0.2721 | ft2/ft | 0.17696 | 0.19792 | cfm/ft | 0.30066 | 3.6216 | cmh/m
WNDBNWSM_RMX |  | Windows, double hung with storm, not wthrstrppd -max |  |  |  |  | 1.7 | cm2/m | 0.9637 | ft2/ft | 0.62675 | 0.70097 | cfm/ft | 1.0648 | 12.8264 | cmh/m
WNDBWE_RAV |  | Windows, double hung, wthrstrppd - estimate |  |  |  |  | 0.65 | cm2/m | 0.36847 | ft2/ft | 0.23964 | 0.26802 | cfm/ft | 0.40715 | 4.9042 | cmh/m
WNDBWE_RMN |  | Windows, double hung, wthrstrppd -min |  |  |  |  | 0.2 | cm2/m | 0.11338 | ft2/ft | 0.073735 | 0.082467 | cfm/ft | 0.12528 | 1.509 | cmh/m
WNDBWE_RMX |  | Windows, double hung, wthrstrppd - max |  |  |  |  | 1.9 | cm2/m | 1.0771 | ft2/ft | 0.70049 | 0.78343 | cfm/ft | 1.1901 | 14.3354 | cmh/m
WNDBWESM_RAV |  | Windows, double hung with storm, wthrstrppd - estimate |  |  |  |  | 0.79 | cm2/m | 0.44784 | ft2/ft | 0.29125 | 0.32574 | cfm/ft | 0.49484 | 5.9605 | cmh/m
WNDBWESM_RMN |  | ndows, double hung with storm, wthrstrppd - min |  |  |  |  | 0.44 | cm2/m | 0.24943 | ft2/ft | 0.16222 | 0.18143 | cfm/ft | 0.27561 | 3.3198 | cmh/m
WNDBWESM_RMX |  | ndows, double hung with storm, wthrstrppd - max |  |  |  |  | 1 | cm2/m | 0.56688 | ft2/ft | 0.36868 | 0.41233 | cfm/ft | 0.62638 | 7.5449 | cmh/m
WNJA_RAV |  | Windows, jalousise - estimate |  |  |  |  | 3.38 | cm2/m | 1.9161 | ft2/ft | 1.2461 | 1.3937 | cfm/ft | 2.1172 | 25.5019 | cmh/m
WNSISHWE_RAV |  | Windows, single hung, wthrstrppd - estimate |  |  |  |  | 0.87 | cm2/m | 0.49319 | ft2/ft | 0.32075 | 0.35873 | cfm/ft | 0.54495 | 6.5641 | cmh/m
WNSISHWE_RMN |  | Windows, single hung, wthrstrppd - min |  |  |  |  | 0.62 | cm2/m | 0.35147 | ft2/ft | 0.22858 | 0.25565 | cfm/ft | 0.38836 | 4.6779 | cmh/m
WNSISHWE_RMX |  | Windows, single hung, wthrstrppd - max |  |  |  |  | 1.24 | cm2/m | 0.70293 | ft2/ft | 0.45716 | 0.51129 | cfm/ft | 0.77671 | 9.3557 | cmh/m
WNSISLAL_RAV |  | Windows, single horizontal slider, aluminum - estimate |  |  |  |  | 0.8 | cm2/m | 0.4535 | ft2/ft | 0.29494 | 0.32987 | cfm/ft | 0.5011 | 6.036 | cmh/m
WNSISLAL_RMN |  | Windows, single horizontal slider, aluminum - min |  |  |  |  | 0.27 | cm2/m | 0.15306 | ft2/ft | 0.099543 | 0.11133 | cfm/ft | 0.16912 | 2.0371 | cmh/m
WNSISLAL_RMX |  | Windows, single horizontal slider, aluminum - max |  |  |  |  | 2.06 | cm2/m | 1.1678 | ft2/ft | 0.75947 | 0.84941 | cfm/ft | 1.2903 | 15.5426 | cmh/m
WNSISLWD_RAV |  | Windows, single horizontal slider, wood - estimate |  |  |  |  | 0.44 | cm2/m | 0.24943 | ft2/ft | 0.16222 | 0.18143 | cfm/ft | 0.27561 | 3.3198 | cmh/m
WNSISLWD_RMN |  | Windows, single horizontal slider, wood - min |  |  |  |  | 0.27 | cm2/m | 0.15306 | ft2/ft | 0.099543 | 0.11133 | cfm/ft | 0.16912 | 2.0371 | cmh/m
WNSISLWD_RMX |  | Windows, single horizontal slider, wood - max |  |  |  |  | 0.99 | cm2/m | 0.56121 | ft2/ft | 0.36499 | 0.40821 | cfm/ft | 0.62012 | 7.4695 | cmh/m
WNSISLWE_RAV |  | Windows, single horizontal slider, wthrstrppd - estimate |  |  |  |  | 0.67 | cm2/m | 0.37981 | ft2/ft | 0.24701 | 0.27626 | cfm/ft | 0.41968 | 5.0551 | cmh/m
WNSISLWE_RMN |  | Windows, single horizontal slider, wthrstrppd - min |  |  |  |  | 0.2 | cm2/m | 0.11338 | ft2/ft | 0.073735 | 0.082467 | cfm/ft | 0.12528 | 1.509 | cmh/m
WNSISLWE_RMX |  | Windows, single horizontal slider, wthrstrppd - max |  |  |  |  | 2.06 | cm2/m | 1.1678 | ft2/ft | 0.75947 | 0.84941 | cfm/ft | 1.2903 | 15.5426 | cmh/m
WNSLALWE_RAV |  | Windows, double horizontal slider, aluminum, wthrstrppd - estimate |  |  |  |  | 0.72 | cm2/m | 0.40815 | ft2/ft | 0.26545 | 0.29688 | cfm/ft | 0.45099 | 5.4324 | cmh/m
WNSLALWE_RMN |  | Windows, double horizontal slider, aluminum, wthrstrppd - min |  |  |  |  | 0.58 | cm2/m | 0.32879 | ft2/ft | 0.21383 | 0.23915 | cfm/ft | 0.3633 | 4.3761 | cmh/m
WNSLALWE_RMX |  | Windows, double horizontal slider, aluminum, wthrstrppd -max |  |  |  |  | 0.8 | cm2/m | 0.4535 | ft2/ft | 0.29494 | 0.32987 | cfm/ft | 0.5011 | 6.036 | cmh/m
WNSLNW_RAV |  | Windows, double horizontal slider, not wthrstrppd - estimate |  |  |  |  | 1.1 | cm2/m | 0.62357 | ft2/ft | 0.40554 | 0.45357 | cfm/ft | 0.68902 | 8.2994 | cmh/m
WNSLNW_RMN |  | Windows, double horizontal slider, not wthrstrppd - min |  |  |  |  | 0.019 | cm2/m | 0.010771 | ft2/ft | 0.0070049 | 0.0078343 | cfm/ft | 0.011901 | 0.14335 | cmh/m
WNSLNW_RMX |  | Windows, double horizontal slider, not wthrstrppd - max |  |  |  |  | 3.4 | cm2/m | 1.9274 | ft2/ft | 1.2535 | 1.4019 | cfm/ft | 2.1297 | 25.6528 | cmh/m
WNSLWDWE_RAV |  | Windows, double horizontal slider, wood, wthrstrppd - estimate |  |  |  |  | 0.55 | cm2/m | 0.31178 | ft2/ft | 0.20277 | 0.22678 | cfm/ft | 0.34451 | 4.1497 | cmh/m
WNSLWDWE_RMN |  | Windows, double horizontal slider, wood, wthrstrppd - min |  |  |  |  | 0.15 | cm2/m | 0.085032 | ft2/ft | 0.055301 | 0.06185 | cfm/ft | 0.093957 | 1.1317 | cmh/m
WNSLWDWE_RMX |  | Windows, double horizontal slider, wood, wthrstrppd - max |  |  |  |  | 1.72 | cm2/m | 0.97503 | ft2/ft | 0.63412 | 0.70921 | cfm/ft | 1.0774 | 12.9773 | cmh/m

## C2 - Miscell-Residential
10 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 10 | 10 | 10 | 10 | 11 | 11 | 10 | 11 | 11 | 10.5
CALCULATIONS |  | Altit | DB | WB | Altit | Atm.Pr | Atm.Pr. | Atm.Pr. | DP | RH | V | d | W | H | Tdb | Twb
Input | ??? | feet | Tdb (F) | Twb (F) | meters | (Pa) | (in.Hg) | (psi) | F | % | ft3/lb | lb/ft3 | lbs/lb | btu/lb | R | R
Altit-H1, DB, WB |  | 0 | 95 | 75 | 0 | 101325 | 29.9213 | 14.656 | 65.9334 | 39.8692 | 14.3016 | 0.069922 | 0.014138 | 38.3964 | 554.7 | 534.7
Altit-H2 |  | 7500 | 68.3 | 57.45 | 2286 | 76714.1242 | 22.6537 | 11.0962 | 51.1213 | 55.7438 | 17.8892 | 0.0559 | 0.010908 | 28.2963 | 528 | 517.15
∆P = Press Diff (in.wg) across Surface (PI - PO) = | [5 empty] | 0.035 | Cd = | 0.65 | DP: Q = Cd * A * ( 2 * ∆P/d ) ^ 0.5; W: A = Q / ( Cd * ( 2 * ∆P/d ) ^ 0.5 )
Tdb=T-(H2-H1)* |  | 0.00356 | Base Altitude - Intermediate Calcs for DP, RH, V, W, H, T-rankine | [5 empty] | RH: Base Altitude - Intermediate Calcs for DP, RH, V, W, H, T-rankine
Twb=T-(H2-H1)* |  | 0.00234 | PWSwb | WSwb | PWSdb | VPs | VPa | a | WSdb | PWSwb | WSwb | PWSdb | VPs | VPa | a | WSdb
T = 59 - 0.00356*H |  |  | 0.43051 | 0.018823 | 0.817 | 1.6681 | 0.665 | -1.1218 | 0.036719 | 0.23422 | 0.013412 | 0.34309 | 0.7005 | 0.39045 | -1.6543 | 0.019845
0.0010764 | * cm2 = ft2 |  | 0.0001 | * cm2/m2 = ft2/ft2 |  |  | 0.56688 | * cm2/m = ft2/ft | RH: 18.2982; V: * cfm/ft2 = m3/m2; W: 1.699; H: * ft3/min = m3/hr
Appendix C2: Miscellaneous Residential Leakage Data (RESMISC.lb3) | [8 empty] | DP: Converted from NIST CONTAM Library - Leakg-A + Infltr @ Alt-1 & Alt-2 in IP & SI units
National Institute of Standards & Technology - CONTAM Library
Element ID |  | Description |  |  |  |  | Leakg-A | SI units | Leakg-A | IP units | H1 cfm | H2 cfm | IP units | H1 cmh | H2 cmh | SI units
DRAT_RAV |  | Attic door, typical value |  |  |  |  | 30 | cm2/item | 0.032292 | ft2/item | 0.021001 | 0.023488 | cfm/item | 0.38428 | 0.42979 | cmh/item
DRAT_RMN |  | Attic door, tight value |  |  |  |  | 18 | cm2/item | 0.019375 | ft2/item | 0.012601 | 0.014093 | cfm/item | 0.23057 | 0.25787 | cmh/item
CE_RAV |  | General ceiling, typical value |  |  |  |  | 1.8 | cm2/m2 | 0.00018 | ft2/ft2 | 0.00011706 | 0.00013093 | cfm/ft2 | 0.0021421 | 0.0023957 | cmh/m2
CE_RMN |  | General ceiling, tight value |  |  |  |  | 0.79 | cm2/m2 | 7.9e-05 | ft2/ft2 | 5.1378e-05 | 5.7462e-05 | cfm/ft2 | 0.00094013 | 0.0010515 | cmh/m2
DRCTCL_RAV |  | Closet door, closed, typical value |  |  |  |  | 0.9 | cm2/m | 0.51019 | ft2/ft | 0.33181 | 0.3711 | cfm/ft | 6.0715 | 6.7905 | cmh/m
DRCTCL_RMN |  | Closet door, closed, tight value |  |  |  |  | 0.25 | cm2/m | 0.14172 | ft2/ft | 0.092169 | 0.10308 | cfm/ft | 1.6865 | 1.8862 | cmh/m
DRCTFR_RAV |  | Closet door frame, typical value |  |  |  |  | 25 | cm2/item | 0.02691 | ft2/item | 0.017501 | 0.019573 | cfm/item | 0.32024 | 0.35816 | cmh/item
DRCTFR_RMN |  | Closet door frame, tight value |  |  |  |  | 12 | cm2/item | 0.012917 | ft2/item | 0.0084005 | 0.0093953 | cfm/item | 0.15371 | 0.17192 | cmh/item
CPEN_RAV |  | HVAC ceiling penetration, typical value |  |  |  |  | 5 | cm2/item | 0.005382 | ft2/item | 0.0035002 | 0.0039147 | cfm/item | 0.064047 | 0.071632 | cmh/item
CPEN_RMN |  | HVAC ceiling penetration, tight value |  |  |  |  | 1 | cm2/item | 0.0010764 | ft2/item | 0.00070004 | 0.00078294 | cfm/item | 0.012809 | 0.014326 | cmh/item
DREXSI_RAV |  | Door, exterior, single, typical value |  |  |  |  | 21 | cm2/item | 0.022604 | ft2/item | 0.014701 | 0.016442 | cfm/item | 0.269 | 0.30085 | cmh/item
DREXSI_RMN |  | Door, exterior, single, tight value |  |  |  |  | 12 | cm2/item | 0.012917 | ft2/item | 0.0084005 | 0.0093953 | cfm/item | 0.15371 | 0.17192 | cmh/item
DREXFRWD_RAV |  | Door, exterior, wood, frame, typical value |  |  |  |  | 1.7 | cm2/m2 | 0.0018299 | ft2/ft2 | 0.0011901 | 0.001331 | cfm/ft2 | 0.021776 | 0.024355 | cmh/m2
DREXFRWD_RMN |  | Door, exterior, wood, frame, tight value |  |  |  |  | 0.3 | cm2/m2 | 0.00032292 | ft2/ft2 | 0.00021001 | 0.00023488 | cfm/ft2 | 0.0038428 | 0.0042979 | cmh/m2
VEBA_RAV |  | Bathroom exhaust vent, typical value |  |  |  |  | 20 | cm2/item | 0.021528 | ft2/item | 0.014001 | 0.015659 | cfm/item | 0.25619 | 0.28653 | cmh/item
VEBA_RMN |  | Bathroom exhaust vent, tight value |  |  |  |  | 10 | cm2/item | 0.010764 | ft2/item | 0.0070004 | 0.0078294 | cfm/item | 0.12809 | 0.14326 | cmh/item
VEKI_RAV |  | Kitchen exhaust vent, typical value |  |  |  |  | 40 | cm2/item | 0.043056 | ft2/item | 0.028002 | 0.031318 | cfm/item | 0.51238 | 0.57305 | cmh/item
VEKI_RMN |  | Kitchen exhaust vent, tight value |  |  |  |  | 5 | cm2/item | 0.005382 | ft2/item | 0.0035002 | 0.0039147 | cfm/item | 0.064047 | 0.071632 | cmh/item
JTCEWL_RAV |  | Ceiling-wall joint, typical value |  |  |  |  | 1.5 | cm2/m | 0.85032 | ft2/ft | 0.55301 | 0.6185 | cfm/ft | 10.1192 | 11.3174 | cmh/m
JTCEWL_RMN |  | Ceiling-wall joint, tight value |  |  |  |  | 0.5 | cm2/m | 0.28344 | ft2/ft | 0.18434 | 0.20617 | cfm/ft | 3.3731 | 3.7725 | cmh/m
JTFLWL_RAV |  | Floor-wall joint, typical value |  |  |  |  | 4 | cm2/m | 2.2675 | ft2/ft | 1.4747 | 1.6493 | cfm/ft | 26.9844 | 30.1798 | cmh/m
JTFLWL_RMN |  | Floor -wall joint, tight value |  |  |  |  | 0.8 | cm2/m | 0.4535 | ft2/ft | 0.29494 | 0.32987 | cfm/ft | 5.3969 | 6.036 | cmh/m
JTWLWL_RAV |  | Wall-wall joint, typical value |  |  |  |  | 1.5 | cm2/m | 0.85032 | ft2/ft | 0.55301 | 0.6185 | cfm/ft | 10.1192 | 11.3174 | cmh/m
JTWLWL_RMN |  | Wall-wall joint, tight value |  |  |  |  | 0.5 | cm2/m | 0.28344 | ft2/ft | 0.18434 | 0.20617 | cfm/ft | 3.3731 | 3.7725 | cmh/m
DRGA_RAV |  | Garage door, typical value |  |  |  |  | 0.45 | cm2/m | 0.2551 | ft2/ft | 0.1659 | 0.18555 | cfm/ft | 3.0357 | 3.3952 | cmh/m
DRGA_RMN |  | Garage door, tight value |  |  |  |  | 0.31 | cm2/m | 0.17573 | ft2/ft | 0.11429 | 0.12782 | cfm/ft | 2.0913 | 2.3389 | cmh/m
DRGAFRWD_RAV |  | Garage door frame, wood, typical value |  |  |  |  | 1.7 | cm2/m2 | 0.0018299 | ft2/ft2 | 0.0011901 | 0.001331 | cfm/ft2 | 0.021776 | 0.024355 | cmh/m2
DRGAFRWD_RMN |  | Garage door frame, wood, tight value |  |  |  |  | 0.3 | cm2/m2 | 0.00032292 | ft2/ft2 | 0.00021001 | 0.00023488 | cfm/ft2 | 0.0038428 | 0.0042979 | cmh/m2
RFGA_RAV |  | Garage roof, typical value |  |  |  |  | 1.8 | cm2/m2 | 0.0019375 | ft2/ft2 | 0.0012601 | 0.0014093 | cfm/ft2 | 0.023057 | 0.025787 | cmh/m2
RFGA_RMN |  | Garage roof, tight value |  |  |  |  | 0.79 | cm2/m2 | 0.00085035 | ft2/ft2 | 0.00055303 | 0.00061852 | cfm/ft2 | 0.01012 | 0.011318 | cmh/m2
DWHA_RAV |  | Hall doorway, typical value |  |  |  |  | 2.4 | m2/item | 228 | ft2/item | 148.2822 | 165.8411 | cfm/item | 2713.2925 | 3034.5888 | cmh/item
DRINCL_RAV |  | Door, interior, closed, typical value |  |  |  |  | 140 | cm2/item | 0.15069 | ft2/item | 0.098006 | 0.10961 | cfm/item | 1.7933 | 2.0057 | cmh/item
DRINCL_RMN |  | Door, interior, closed, tight value |  |  |  |  | 75 | cm2/item | 0.080729 | ft2/item | 0.052503 | 0.05872 | cfm/item | 0.96071 | 1.0745 | cmh/item
DRINOP_RAV |  | Door, interior, open, typical value |  |  |  |  | 2.1 | cm2/item | 0.0022604 | ft2/item | 0.0014701 | 0.0016442 | cfm/item | 0.0269 | 0.030085 | cmh/item
WLIN_RAV |  | Wall, interior, typical value |  |  |  |  | 2 | cm2/m2 | 0.0021528 | ft2/ft2 | 0.0014001 | 0.0015659 | cfm/ft2 | 0.025619 | 0.028653 | cmh/m2
PEEC_RAV |  | Electrical outlet, typical value |  |  |  |  | 2.5 | cm2/item | 0.002691 | ft2/item | 0.0017501 | 0.0019573 | cfm/item | 0.032024 | 0.035816 | cmh/item
PEEC_RMN |  | Electrical outlet, tight value |  |  |  |  | 0.5 | cm2/item | 0.0005382 | ft2/item | 0.00035002 | 0.00039147 | cfm/item | 0.0064047 | 0.0071632 | cmh/item
PEPL_RAV |  | Plumbing penetration, interior, typical value |  |  |  |  | 6 | cm2/item | 0.0064583 | ft2/item | 0.0042003 | 0.0046976 | cfm/item | 0.076857 | 0.085958 | cmh/item
PEPL_RMN |  | Plumbing penetration, interior, tight value |  |  |  |  | 2 | cm2/item | 0.0021528 | ft2/item | 0.0014001 | 0.0015659 | cfm/item | 0.025619 | 0.028653 | cmh/item
DREXSLGL_RAV |  | Door, exterior, sliding glass, typical value |  |  |  |  | 22 | cm2/item | 0.023681 | ft2/item | 0.015401 | 0.017225 | cfm/item | 0.28181 | 0.31518 | cmh/item
DREXSLGL_RMN |  | Door, exterior, sliding glass, tight value |  |  |  |  | 3 | cm2/item | 0.0032292 | ft2/item | 0.0021001 | 0.0023488 | cfm/item | 0.038428 | 0.042979 | cmh/item
VEAT_RAV |  | Attic vent, based on attic floor area, typical value |  |  |  |  | 1 | cm2/300 cm2 | 0.0003588 | ft2/ft2 | 0.00023335 | 0.00026098 | cfm/ft2 | 0.0042698 | 0.0047754 | cmh/m2
WNDB_RAV |  | Window, double hung, typical value |  |  |  |  | 2.5 | cm2/m | 1.4172 | ft2/ft | #VALUE! | 1.0308 | cfm/ft | #VALUE! | 18.8624 | cmh/m
WNDB_RMN |  | Window, double hung, tight value |  |  |  |  | 0.65 | cm2/m | 0.36847 | ft2/ft | #VALUE! | 0.26802 | cfm/ft | #VALUE! | 4.9042 | cmh/m
WNFRWD_RAV |  | Window door frame, wood, typical value |  |  |  |  | 1.7 | cm2/m2 | 0.0018299 | ft2/ft2 | 0.0011901 | 0.001331 | cfm/ft2 | 0.021776 | 0.024355 | cmh/m2
WNFRWD_RMN |  | Window door frame, wood, tight value |  |  |  |  | 0.3 | cm2/m2 | 0.00032292 | ft2/ft2 | 0.00021001 | 0.00023488 | cfm/ft2 | 0.0038428 | 0.0042979 | cmh/m2
WLEX_R |  | Wall, exterior |  |  |  |  | 0.1 | cm2/m2 | 0.00010764 | ft2/ft2 | 7.0004e-05 | 7.8294e-05 | cfm/ft2 | 0.0012809 | 0.0014326 | cmh/m2
JTFLWL_R |  | Floor -wall joint |  |  |  |  | 0.8 | cm2/m | 0.4535 | ft2/ft | 0.29494 | 0.32987 | cfm/ft | 5.3969 | 6.036 | cmh/m
JTCEWL_R |  | Ceiling-wall joint |  |  |  |  | 0.5 | cm2/m | 0.28344 | ft2/ft | 0.18434 | 0.20617 | cfm/ft | 3.3731 | 3.7725 | cmh/m
JTCR_R |  | Wall-wall corner joint |  |  |  |  | 0.5 | cm2/m | 0.28344 | ft2/ft | 0.18434 | 0.20617 | cfm/ft | 3.3731 | 3.7725 | cmh/m
WN_R |  | Window |  |  |  |  | 2 | cm2/m | 1.1338 | ft2/ft | 0.73735 | 0.82467 | cfm/ft | 13.4922 | 15.0899 | cmh/m
DRFREX_R |  | Exterior door frame |  |  |  |  | 0.3 | cm2/m2 | 0.00032292 | ft2/ft2 | 0.00021001 | 0.00023488 | cfm/ft2 | 0.0038428 | 0.0042979 | cmh/m2
DREXSLGL_R |  | Door, exterior, sliding glass |  |  |  |  | 3 | cm2/item | 0.0032292 | ft2/item | 0.0021001 | 0.0023488 | cfm/item | 0.038428 | 0.042979 | cmh/item
DREX_R |  | Door, exterior |  |  |  |  | 6 | cm2/item | 0.0064583 | ft2/item | 0.0042003 | 0.0046976 | cfm/item | 0.076857 | 0.085958 | cmh/item
WLGAEX_R |  | Exterior garage wall, exterior |  |  |  |  | 0.4 | cm2/m2 | 0.00043056 | ft2/ft2 | 0.00028002 | 0.00031318 | cfm/ft2 | 0.0051238 | 0.0057305 | cmh/m2
ITGAEX_R |  | Wall-floor & wall-ceiling interface, exterior garage wall |  |  |  |  | 2 | cm2/m | 1.1338 | ft2/ft | 0.73735 | 0.82467 | cfm/ft | 13.4922 | 15.0899 | cmh/m
CECS_R |  | Crawl space ceiling |  |  |  |  | 0.5 | cm2/m2 | 0.0005382 | ft2/ft2 | 0.00035002 | 0.00039147 | cfm/ft2 | 0.0064047 | 0.0071632 | cmh/m2
FLAT_R |  | Attic floor |  |  |  |  | 0.5 | cm2/m2 | 0.0005382 | ft2/ft2 | 0.00035002 | 0.00039147 | cfm/ft2 | 0.0064047 | 0.0071632 | cmh/m2
PEDW_R |  | Duct penetration in crawl space ceiling or attic floor |  |  |  |  | 1 | cm2/item | 0.0010764 | ft2/item | 0.00070004 | 0.00078294 | cfm/item | 0.012809 | 0.014326 | cmh/item
VECS_R |  | Crawl space vent, based on floor area |  |  |  |  | 1 | cm2/150 cm2 | 0.00071759 | ft2/ft2 | 0.00046669 | 0.00052196 | cfm/ft2 | 0.0085397 | 0.0095509 | cmh/m2
WLIN_R |  | Wall, interior |  |  |  |  | 2 | cm2/m2 | 0.0021528 | ft2/ft2 | 0.0014001 | 0.0015659 | cfm/ft2 | 0.025619 | 0.028653 | cmh/m2
CEIN_R |  | Ceiling, interior |  |  |  |  | 0.79 | cm2/m2 | 0.00085035 | ft2/ft2 | 0.00055303 | 0.00061852 | cfm/ft2 | 0.01012 | 0.011318 | cmh/m2
DRINCL_R |  | Door, interior, closed, including frame & undercut |  |  |  |  | 250 | cm2/item | 0.2691 | ft2/item | 0.17501 | 0.19573 | cfm/item | 3.2024 | 3.5816 | cmh/item
WLEX_RM |  | Wall, exterior (MH) |  |  |  |  | 0.067 | cm2/m2 | 7.2118e-05 | ft2/ft2 | 4.6903e-05 | 5.2457e-05 | cfm/ft2 | 0.00085824 | 0.00095986 | cmh/m2
JTFLWL_RM |  | Floor-wall joint (MH) |  |  |  |  | 0.53 | cm2/m | 0.30045 | ft2/ft | 0.1954 | 0.21854 | cfm/ft | 3.5754 | 3.9988 | cmh/m
JTCEWL_RM |  | Ceiling-wall joint (MH) |  |  |  |  | 0.33 | cm2/m | 0.18707 | ft2/ft | 0.12166 | 0.13607 | cfm/ft | 2.2262 | 2.4898 | cmh/m
JTCR_RM |  | Wall-wall corner joint (MH) |  |  |  |  | 0.33 | cm2/m | 0.18707 | ft2/ft | 0.12166 | 0.13607 | cfm/ft | 2.2262 | 2.4898 | cmh/m
WN1_RM |  | Window (MH) |  |  |  |  | 2.3 | cm2/m | 1.3038 | ft2/ft | 0.84796 | 0.94837 | cfm/ft | 15.516 | 17.3534 | cmh/m
WN2_RM |  | Window (MH) |  |  |  |  | 2.1 | cm2/m | 1.1904 | ft2/ft | 0.77422 | 0.8659 | cfm/ft | 14.1668 | 15.8444 | cmh/m
WN3_RM |  | Window (MH) |  |  |  |  | 2.7 | cm2/m | 1.5306 | ft2/ft | 0.99543 | 1.1133 | cfm/ft | 18.2145 | 20.3714 | cmh/m
WN4_RM |  | Window (MH) |  |  |  |  | 0.9 | cm2/m | 0.51019 | ft2/ft | 0.33181 | 0.3711 | cfm/ft | 6.0715 | 6.7905 | cmh/m
DREX_RM |  | Door, exterior (MH) |  |  |  |  | 4 | cm2/item | 0.0043056 | ft2/item | 0.0028002 | 0.0031318 | cfm/item | 0.051238 | 0.057305 | cmh/item
CECS_RM |  | Crawl space ceiling (MH) (MH) |  |  |  |  | 1.33 | cm2/m2 | 0.0014316 | ft2/ft2 | 0.00093106 | 0.0010413 | cfm/ft2 | 0.017037 | 0.019054 | cmh/m2
FLAT_RM |  | Attic floor (MH) |  |  |  |  | 0.67 | cm2/m2 | 0.00072118 | ft2/ft2 | 0.00046903 | 0.00052457 | cfm/ft2 | 0.0085824 | 0.0095986 | cmh/m2
WLIN_RM |  | Wall, interior (MH) |  |  |  |  | 2 | cm2/m2 | 0.0021528 | ft2/ft2 | 0.0014001 | 0.0015659 | cfm/ft2 | 0.025619 | 0.028653 | cmh/m2
DRBACL_RM |  | Bathroom door, closed, including frame & undercut (MH) |  |  |  |  | 330 | cm2/item | 0.35521 | ft2/item | 0.23101 | 0.25837 | cfm/item | 4.2271 | 4.7277 | cmh/item
DRINCL_RM |  | Inter (bedroom) door, closed, including frame & undercut (MH) |  |  |  |  | 410 | cm2/item | 0.44132 | ft2/item | 0.28702 | 0.321 | cfm/item | 5.2519 | 5.8738 | cmh/item
DRBAOP_RM |  | Bathroom door, open, including frame & undercut (MH) |  |  |  |  | 1.3 | m2/item | 123.5 | ft2/item | 80.3195 | 89.8306 | cfm/item | 1469.7001 | 1643.7356 | cmh/item
DRINOP_RM |  | Inter (bedroom) door, open, including frame & undercut (MH) |  |  |  |  | 1.6 | m2/item | 152 | ft2/item | 98.8548 | 110.5607 | cfm/item | 1808.8617 | 2023.0592 | cmh/item

## C3 - Commercial
10 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 10 | 10 | 10 | 10 | 11 | 11 | 10 | 11 | 11 | 10.5
CALCULATIONS |  | Altit | DB | WB | Altit | Atm.Pr | Atm.Pr. | Atm.Pr. | DP | RH | V | d | W | H | Tdb | Twb
Input | ??? | feet | Tdb (F) | Twb (F) | meters | (Pa) | (in.Hg) | (psi) | F | % | ft3/lb | lb/ft3 | lbs/lb | btu/lb | R | R
Altit-H1, DB, WB |  | 0 | 95 | 75 | 0 | 101325 | 29.9213 | 14.656 | 65.9334 | 39.8692 | 14.3016 | 0.069922 | 0.014138 | 38.3964 | 554.7 | 534.7
Altit-H2 |  | 7500 | 68.3 | 57.45 | 2286 | 76714.1242 | 22.6537 | 11.0962 | 51.1213 | 55.7438 | 17.8892 | 0.0559 | 0.010908 | 28.2963 | 528 | 517.15
∆P = Press Diff (in.wg) across Surface (PI - PO) = | [5 empty] | 0.035 | Cd = | 0.65 | DP: Q = Cd * A * ( 2 * ∆P/d ) ^ 0.5; W: A = Q / ( Cd * ( 2 * ∆P/d ) ^ 0.5 )
Tdb=T-(H2-H1)* |  | 0.00356 | Base Altitude - Intermediate Calcs for DP, RH, V, W, H, T-rankine | [5 empty] | RH: Base Altitude - Intermediate Calcs for DP, RH, V, W, H, T-rankine
Twb=T-(H2-H1)* |  | 0.00234 | PWSwb | WSwb | PWSdb | VPs | VPa | a | WSdb | PWSwb | WSwb | PWSdb | VPs | VPa | a | WSdb
T = 59 - 0.00356*H |  |  | 0.43051 | 0.018823 | 0.817 | 1.6681 | 0.665 | -1.1218 | 0.036719 | 0.23422 | 0.013412 | 0.34309 | 0.7005 | 0.39045 | -1.6543 | 0.019845
0.0010764 | * cm2 = ft2 |  | 0.0001 | * cm2/m2 = ft2/ft2 |  |  | 0.56688 | * cm2/m = ft2/ft | RH: 18.2982; V: * cfm/ft2 = m3/m2; W: 1.699; H: * ft3/min = m3/hr
Appendix C3: Commercial & Institutional Building Airtightness Data (C&ISUM.lb3) | [8 empty] | DP: Converted from NIST CONTAM Library - Leakg-A + Infltr @ Alt-1 & Alt-2 in IP & SI units
National Institute of Standards & Technology - CONTAM Library
Element ID |  | Description |  |  |  |  | Leakg-A | SI units | Leakg-A | IP units | H1 cfm | H2 cfm | IP units | H1 cmh | H2 cmh | SI units
WLEXMA_CAV |  | Exter wall, masonry, mean |  |  |  |  | 4.2 | cm2/m2 | 0.00042 | ft2/ft2 | 0.00027315 | 0.0003055 | cfm/ft2 | 0.0049982 | 0.00559 | cmh/m2
WLEXMA_C+S |  | Exter wall, masonry, mean plus one std-deviation |  |  |  |  | 6.9 | cm2/m2 | 0.00069 | ft2/ft2 | 0.00044875 | 0.00050189 | cfm/ft2 | 0.0082113 | 0.0091836 | cmh/m2
WLEXMA_C-S |  | Exter wall, masonry, mean minus one std-deviation |  |  |  |  | 1.5 | cm2/m2 | 0.00015 | ft2/ft2 | 9.7554e-05 | 0.00010911 | cfm/ft2 | 0.0017851 | 0.0019964 | cmh/m2
WLEXMA_CMN |  | Exter wall, masonry, minim |  |  |  |  | 0.6 | cm2/m2 | 6e-05 | ft2/ft2 | 3.9022e-05 | 4.3642e-05 | cfm/ft2 | 0.00071402 | 0.00079858 | cmh/m2
WLEXMA_CMX |  | Exter wall, masonry, maxim |  |  |  |  | 11.4 | cm2/m2 | 0.00114 | ft2/ft2 | 0.00074141 | 0.00082921 | cfm/ft2 | 0.013566 | 0.015173 | cmh/m2
WLEXCP_CAV |  | Exter wall, concrete panel, mean |  |  |  |  | 4 | cm2/m2 | 0.0004 | ft2/ft2 | 0.00026014 | 0.00029095 | cfm/ft2 | 0.0047602 | 0.0053238 | cmh/m2
WLEXCP_C+S |  | Exter wall, concrete panel, mean plus one std-deviation |  |  |  |  | 6.9 | cm2/m2 | 0.00069 | ft2/ft2 | 0.00044875 | 0.00050189 | cfm/ft2 | 0.0082113 | 0.0091836 | cmh/m2
WLEXCP_C-S |  | Exter wall, concrete panel, mean minus one std-deviation |  |  |  |  | 1.2 | cm2/m2 | 0.00012 | ft2/ft2 | 7.8043e-05 | 8.7285e-05 | cfm/ft2 | 0.001428 | 0.0015972 | cmh/m2
WLEXCP_CMN |  | Exter wall, concrete panel, minim |  |  |  |  | 1.1 | cm2/m2 | 0.00011 | ft2/ft2 | 7.154e-05 | 8.0011e-05 | cfm/ft2 | 0.001309 | 0.0014641 | cmh/m2
WLEXCP_CMX |  | Exter wall, concrete panel, maxim |  |  |  |  | 10 | cm2/m2 | 0.001 | ft2/ft2 | 0.00065036 | 0.00072737 | cfm/ft2 | 0.0119 | 0.01331 | cmh/m2
WLEXFRMA_CAV |  | Exter wall, frame/masonry, mean |  |  |  |  | 9.1 | cm2/m2 | 0.00091 | ft2/ft2 | 0.00059183 | 0.00066191 | cfm/ft2 | 0.010829 | 0.012112 | cmh/m2
WLEXFRMA_C+S |  | Exter wall, frame/masonry, mean plus one std-deviation |  |  |  |  | 13.2 | cm2/m2 | 0.00132 | ft2/ft2 | 0.00085848 | 0.00096013 | cfm/ft2 | 0.015709 | 0.017569 | cmh/m2
WLEXFRMA_C-S |  | Exter wall, frame/masonry, mean minus one std-deviation |  |  |  |  | 4.9 | cm2/m2 | 0.00049 | ft2/ft2 | 0.00031868 | 0.00035641 | cfm/ft2 | 0.0058312 | 0.0065217 | cmh/m2
WLEXFRMA_CMN |  | Exter wall, frame/masonry, minim |  |  |  |  | 4.5 | cm2/m2 | 0.00045 | ft2/ft2 | 0.00029266 | 0.00032732 | cfm/ft2 | 0.0053552 | 0.0059893 | cmh/m2
WLEXFRMA_CMX |  | Exter wall, frame, maxim |  |  |  |  | 19.9 | cm2/m2 | 0.00199 | ft2/ft2 | 0.0012942 | 0.0014475 | cfm/ft2 | 0.023682 | 0.026486 | cmh/m2
WLEXFR_CAV |  | Exter wall, frame, mean |  |  |  |  | 8.6 | cm2/m2 | 0.00086 | ft2/ft2 | 0.00055931 | 0.00062554 | cfm/ft2 | 0.010234 | 0.011446 | cmh/m2
WLEXFR_C+S |  | Exter wall, frame, mean plus one std-deviation |  |  |  |  | 13 | cm2/m2 | 0.0013 | ft2/ft2 | 0.00084547 | 0.00094559 | cfm/ft2 | 0.015471 | 0.017302 | cmh/m2
WLEXFR_C-S |  | Exter wall, frame, mean minus one std-deviation |  |  |  |  | 4.3 | cm2/m2 | 0.00043 | ft2/ft2 | 0.00027965 | 0.00031277 | cfm/ft2 | 0.0051172 | 0.0057231 | cmh/m2
WLEXFR_CMN |  | Exter wall, frame, minim |  |  |  |  | 3.1 | cm2/m2 | 0.00031 | ft2/ft2 | 0.00020161 | 0.00022549 | cfm/ft2 | 0.0036891 | 0.004126 | cmh/m2
WLEXFR_CMX |  | Exter wall, frame, maxim |  |  |  |  | 15.6 | cm2/m2 | 0.00156 | ft2/ft2 | 0.0010146 | 0.0011347 | cfm/ft2 | 0.018565 | 0.020763 | cmh/m2
WLEXMN_CAV |  | Exter wall, manufactured, mean |  |  |  |  | 4.3 | cm2/m2 | 0.00043 | ft2/ft2 | 0.00027965 | 0.00031277 | cfm/ft2 | 0.0051172 | 0.0057231 | cmh/m2
WLEXMN_C+S |  | Exter wall, manufactured, mean plus one std-deviation |  |  |  |  | 7 | cm2/m2 | 0.0007 | ft2/ft2 | 0.00045525 | 0.00050916 | cfm/ft2 | 0.0083303 | 0.0093167 | cmh/m2
WLEXMN_C-S |  | Exter wall, manufactured, mean minus one std-deviation |  |  |  |  | 1.5 | cm2/m2 | 0.00015 | ft2/ft2 | 9.7554e-05 | 0.00010911 | cfm/ft2 | 0.0017851 | 0.0019964 | cmh/m2
WLEXMN_CMN |  | Exter wall, manufactured, minim |  |  |  |  | 2.4 | cm2/m2 | 0.00024 | ft2/ft2 | 0.00015609 | 0.00017457 | cfm/ft2 | 0.0028561 | 0.0031943 | cmh/m2
WLEXMN_CMX |  | Exter wall, manufactured, maxim |  |  |  |  | 8.7 | cm2/m2 | 0.00087 | ft2/ft2 | 0.00056581 | 0.00063281 | cfm/ft2 | 0.010353 | 0.011579 | cmh/m2
WLEXME_CAV |  | Exter wall, metal, mean |  |  |  |  | 4.6 | cm2/m2 | 0.00046 | ft2/ft2 | 0.00029917 | 0.00033459 | cfm/ft2 | 0.0054742 | 0.0061224 | cmh/m2
WLEXME_C+S |  | Exter wall, metal, mean plus one std-deviation |  |  |  |  | 7.2 | cm2/m2 | 0.00072 | ft2/ft2 | 0.00046826 | 0.00052371 | cfm/ft2 | 0.0085683 | 0.0095829 | cmh/m2
WLEXME_C-S |  | Exter wall, metal, mean minus one std-deviation |  |  |  |  | 1.9 | cm2/m2 | 0.00019 | ft2/ft2 | 0.00012357 | 0.0001382 | cfm/ft2 | 0.0022611 | 0.0025288 | cmh/m2
WLEXME_CMN |  | Exter wall, metal, minim |  |  |  |  | 2 | cm2/m2 | 0.0002 | ft2/ft2 | 0.00013007 | 0.00014547 | cfm/ft2 | 0.0023801 | 0.0026619 | cmh/m2
WLEXME_CMX |  | Exter wall, metal, maxim |  |  |  |  | 8 | cm2/m2 | 0.0008 | ft2/ft2 | 0.00052029 | 0.0005819 | cfm/ft2 | 0.0095203 | 0.010648 | cmh/m2
WLEXCW_CAV |  | Exter wall, curtain wall, mean |  |  |  |  | 2.7 | cm2/m2 | 0.00027 | ft2/ft2 | 0.0001756 | 0.00019639 | cfm/ft2 | 0.0032131 | 0.0035936 | cmh/m2
WLEXCW_C+S |  | Exter wall, curtain wall, mean plus one std-deviation |  |  |  |  | 5.6 | cm2/m2 | 0.00056 | ft2/ft2 | 0.0003642 | 0.00040733 | cfm/ft2 | 0.0066642 | 0.0074534 | cmh/m2
WLEXCW_CMN |  | Exter wall, curtain wall, minim |  |  |  |  | 0.8 | cm2/m2 | 8e-05 | ft2/ft2 | 5.2029e-05 | 5.819e-05 | cfm/ft2 | 0.00095203 | 0.0010648 | cmh/m2
WLEXCW_CMX |  | Exter wall, curtain wall, maxim |  |  |  |  | 6.9 | cm2/m2 | 0.00069 | ft2/ft2 | 0.00044875 | 0.00050189 | cfm/ft2 | 0.0082113 | 0.0091836 | cmh/m2
WLEXOF_CAV |  | Exter wall, office bldg, mean |  |  |  |  | 4.1 | cm2/m2 | 0.00041 | ft2/ft2 | 0.00026665 | 0.00029822 | cfm/ft2 | 0.0048792 | 0.0054569 | cmh/m2
WLEXOF_C+S |  | Exter wall, office bldg, mean plus one std-deviation |  |  |  |  | 7.8 | cm2/m2 | 0.00078 | ft2/ft2 | 0.00050728 | 0.00056735 | cfm/ft2 | 0.0092823 | 0.010381 | cmh/m2
WLEXOF_C-S |  | Exter wall, office bldg, mean minus one std-deviation |  |  |  |  | 0.4 | cm2/m2 | 4e-05 | ft2/ft2 | 2.6014e-05 | 2.9095e-05 | cfm/ft2 | 0.00047602 | 0.00053238 | cmh/m2
WLEXOF_CMN |  | Exter wall, office bldg, minim |  |  |  |  | 0.6 | cm2/m2 | 6e-05 | ft2/ft2 | 3.9022e-05 | 4.3642e-05 | cfm/ft2 | 0.00071402 | 0.00079858 | cmh/m2
WLEXOF_CMX |  | Exter wall, office bldg, maxim |  |  |  |  | 19.9 | cm2/m2 | 0.00199 | ft2/ft2 | 0.0012942 | 0.0014475 | cfm/ft2 | 0.023682 | 0.026486 | cmh/m2
WLEXSC_IAV |  | Exter wall, school, mean |  |  |  |  | 3.1 | cm2/m2 | 0.00031 | ft2/ft2 | 0.00020161 | 0.00022549 | cfm/ft2 | 0.0036891 | 0.004126 | cmh/m2
WLEXSC_I+S |  | Exter wall, school, mean plus one std-deviation |  |  |  |  | 5.1 | cm2/m2 | 0.00051 | ft2/ft2 | 0.00033168 | 0.00037096 | cfm/ft2 | 0.0060692 | 0.0067879 | cmh/m2
WLEXSC_I-S |  | Exter wall, school, mean minus one std-deviation |  |  |  |  | 1 | cm2/m2 | 0.0001 | ft2/ft2 | 6.5036e-05 | 7.2737e-05 | cfm/ft2 | 0.00119 | 0.001331 | cmh/m2
WLEXSC_IMN |  | Exter wall, school, minim |  |  |  |  | 0.4 | cm2/m2 | 4e-05 | ft2/ft2 | 2.6014e-05 | 2.9095e-05 | cfm/ft2 | 0.00047602 | 0.00053238 | cmh/m2
WLEXSC_IMX |  | Exter wall, school, maxim |  |  |  |  | 8.6 | cm2/m2 | 0.00086 | ft2/ft2 | 0.00055931 | 0.00062554 | cfm/ft2 | 0.010234 | 0.011446 | cmh/m2
WLEXID_NAV |  | Exter wall, industrial bldg, mean |  |  |  |  | 3.8 | cm2/m2 | 0.00038 | ft2/ft2 | 0.00024714 | 0.0002764 | cfm/ft2 | 0.0045222 | 0.0050576 | cmh/m2
WLEXID_N+S |  | Exter wall, industrial bldg, mean plus one std-deviation |  |  |  |  | 7.9 | cm2/m2 | 0.00079 | ft2/ft2 | 0.00051378 | 0.00057462 | cfm/ft2 | 0.0094013 | 0.010515 | cmh/m2
WLEXID_NMN |  | Exter wall, industrial bldg, minim |  |  |  |  | 0.4 | cm2/m2 | 4e-05 | ft2/ft2 | 2.6014e-05 | 2.9095e-05 | cfm/ft2 | 0.00047602 | 0.00053238 | cmh/m2
WLEXID_NMX |  | Exter wall, industrial bldg, maxim |  |  |  |  | 15.6 | cm2/m2 | 0.00156 | ft2/ft2 | 0.0010146 | 0.0011347 | cfm/ft2 | 0.018565 | 0.020763 | cmh/m2
WLEXRE_CAV |  | Exter wall, retail, mean |  |  |  |  | 6.9 | cm2/m2 | 0.00069 | ft2/ft2 | 0.00044875 | 0.00050189 | cfm/ft2 | 0.0082113 | 0.0091836 | cmh/m2
WLEXRE_C+S |  | Exter wall, retail, mean plus one std-deviation |  |  |  |  | 10.5 | cm2/m2 | 0.00105 | ft2/ft2 | 0.00068288 | 0.00076374 | cfm/ft2 | 0.012495 | 0.013975 | cmh/m2
WLEXRE_C-S |  | Exter wall, retail, mean minus one std-deviation |  |  |  |  | 3.3 | cm2/m2 | 0.00033 | ft2/ft2 | 0.00021462 | 0.00024003 | cfm/ft2 | 0.0039271 | 0.0043922 | cmh/m2
WLEXRE_CMN |  | Exter wall, retail, minim |  |  |  |  | 0.7 | cm2/m2 | 7e-05 | ft2/ft2 | 4.5525e-05 | 5.0916e-05 | cfm/ft2 | 0.00083303 | 0.00093167 | cmh/m2
WLEXRE_CMX |  | Exter wall, retail, maxim |  |  |  |  | 12 | cm2/m2 | 0.0012 | ft2/ft2 | 0.00078043 | 0.00087285 | cfm/ft2 | 0.01428 | 0.015972 | cmh/m2
WLEXRS_CAV |  | Exter wall, restaurant, mean |  |  |  |  | 3.8 | cm2/m2 | 0.00038 | ft2/ft2 | 0.00024714 | 0.0002764 | cfm/ft2 | 0.0045222 | 0.0050576 | cmh/m2
WLEXRS_C+S |  | Exter wall, restaurant, mean plus one std-deviation |  |  |  |  | 5.2 | cm2/m2 | 0.00052 | ft2/ft2 | 0.00033819 | 0.00037823 | cfm/ft2 | 0.0061882 | 0.006921 | cmh/m2
WLEXRS_C-S |  | Exter wall, restaurant, mean minus one std-deviation |  |  |  |  | 2.3 | cm2/m2 | 0.00023 | ft2/ft2 | 0.00014958 | 0.0001673 | cfm/ft2 | 0.0027371 | 0.0030612 | cmh/m2
WLEXRS_CMN |  | Exter wall, restaurant, minim |  |  |  |  | 1.4 | cm2/m2 | 0.00014 | ft2/ft2 | 9.105e-05 | 0.00010183 | cfm/ft2 | 0.0016661 | 0.0018633 | cmh/m2
WLEXRS_CMX |  | Exter wall, restaurant, maxim |  |  |  |  | 5.5 | cm2/m2 | 0.00055 | ft2/ft2 | 0.0003577 | 0.00040006 | cfm/ft2 | 0.0065452 | 0.0073203 | cmh/m2
WLEXAS_NAV |  | Exter wall, assembly, mean |  |  |  |  | 3.7 | cm2/m2 | 0.00037 | ft2/ft2 | 0.00024063 | 0.00026913 | cfm/ft2 | 0.0044032 | 0.0049246 | cmh/m2
WLEXAS_N+S |  | Exter wall, assembly, mean plus one std-deviation |  |  |  |  | 5.8 | cm2/m2 | 0.00058 | ft2/ft2 | 0.00037721 | 0.00042188 | cfm/ft2 | 0.0069022 | 0.0077196 | cmh/m2
WLEXAS_N-S |  | Exter wall, assembly, mean minus one std-deviation |  |  |  |  | 1.5 | cm2/m2 | 0.00015 | ft2/ft2 | 9.7554e-05 | 0.00010911 | cfm/ft2 | 0.0017851 | 0.0019964 | cmh/m2
WLEXAS_NMN |  | Exter wall, assembly, minim |  |  |  |  | 1.8 | cm2/m2 | 0.00018 | ft2/ft2 | 0.00011706 | 0.00013093 | cfm/ft2 | 0.0021421 | 0.0023957 | cmh/m2
WLEXAS_NMX |  | Exter wall, assembly, maxim |  |  |  |  | 6.3 | cm2/m2 | 0.00063 | ft2/ft2 | 0.00040973 | 0.00045825 | cfm/ft2 | 0.0074973 | 0.008385 | cmh/m2
WLEXHC_IAV |  | Exter wall, healthcare, mean |  |  |  |  | 5.6 | cm2/m2 | 0.00056 | ft2/ft2 | 0.0003642 | 0.00040733 | cfm/ft2 | 0.0066642 | 0.0074534 | cmh/m2
WLEXHC_I+S |  | Exter wall, healthcare, mean plus one std-deviation |  |  |  |  | 7.5 | cm2/m2 | 0.00075 | ft2/ft2 | 0.00048777 | 0.00054553 | cfm/ft2 | 0.0089253 | 0.0099822 | cmh/m2
WLEXHC_I-S |  | Exter wall, healthcare, mean minus one std-deviation |  |  |  |  | 3.7 | cm2/m2 | 0.00037 | ft2/ft2 | 0.00024063 | 0.00026913 | cfm/ft2 | 0.0044032 | 0.0049246 | cmh/m2
WLEXHC_IMN |  | Exter wall, healthcare, minim |  |  |  |  | 3.7 | cm2/m2 | 0.00037 | ft2/ft2 | 0.00024063 | 0.00026913 | cfm/ft2 | 0.0044032 | 0.0049246 | cmh/m2
WLEXHC_IMX |  | Exter wall, healthcare, maxim |  |  |  |  | 7.6 | cm2/m2 | 0.00076 | ft2/ft2 | 0.00049427 | 0.0005528 | cfm/ft2 | 0.0090443 | 0.010115 | cmh/m2
WLEXSP_CAV |  | Exter wall, sports facility, mean |  |  |  |  | 7.4 | cm2/m2 | 0.00074 | ft2/ft2 | 0.00048127 | 0.00053826 | cfm/ft2 | 0.0088063 | 0.0098491 | cmh/m2
WLEXSP_C+S |  | Exter wall, sports facility, mean plus one std-deviation |  |  |  |  | 10.1 | cm2/m2 | 0.00101 | ft2/ft2 | 0.00065686 | 0.00073465 | cfm/ft2 | 0.012019 | 0.013443 | cmh/m2
WLEXSP_C-S |  | Exter wall, sports facility, mean minus one std-deviation |  |  |  |  | 4.8 | cm2/m2 | 0.00048 | ft2/ft2 | 0.00031217 | 0.00034914 | cfm/ft2 | 0.0057122 | 0.0063886 | cmh/m2
WLEXSP_CMN |  | Exter wall, sports facility, minim |  |  |  |  | 3.7 | cm2/m2 | 0.00037 | ft2/ft2 | 0.00024063 | 0.00026913 | cfm/ft2 | 0.0044032 | 0.0049246 | cmh/m2
WLEXSP_CMX |  | Exter wall, sports facility, maxim |  |  |  |  | 9.8 | cm2/m2 | 0.00098 | ft2/ft2 | 0.00063735 | 0.00071283 | cfm/ft2 | 0.011662 | 0.013043 | cmh/m2

## C4 - Miscell-Commercial
10 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 10 | 10 | 10 | 10 | 11 | 11 | 10 | 11 | 11 | 10.5
CALCULATIONS |  | Altit | DB | WB | Altit | Atm.Pr | Atm.Pr. | Atm.Pr. | DP | RH | V | d | W | H | Tdb | Twb
Input | ??? | feet | Tdb (F) | Twb (F) | meters | (Pa) | (in.Hg) | (psi) | F | % | ft3/lb | lb/ft3 | lbs/lb | btu/lb | R | R
Altit-H1, DB, WB |  | 0 | 95 | 75 | 0 | 101325 | 29.9213 | 14.656 | 65.9334 | 39.8692 | 14.3016 | 0.069922 | 0.014138 | 38.3964 | 554.7 | 534.7
Altit-H2 |  | 7500 | 68.3 | 57.45 | 2286 | 76714.1242 | 22.6537 | 11.0962 | 51.1213 | 55.7438 | 17.8892 | 0.0559 | 0.010908 | 28.2963 | 528 | 517.15
∆P = Press Diff (in.wg) across Surface (PI - PO) = | [5 empty] | 0.035 | Cd = | 0.65 | DP: Q = Cd * A * ( 2 * ∆P/d ) ^ 0.5; W: A = Q / ( Cd * ( 2 * ∆P/d ) ^ 0.5 )
Tdb=T-(H2-H1)* |  | 0.00356 | Base Altitude - Intermediate Calcs for DP, RH, V, W, H, T-rankine | [5 empty] | RH: Base Altitude - Intermediate Calcs for DP, RH, V, W, H, T-rankine
Twb=T-(H2-H1)* |  | 0.00234 | PWSwb | WSwb | PWSdb | VPs | VPa | a | WSdb | PWSwb | WSwb | PWSdb | VPs | VPa | a | WSdb
T = 59 - 0.00356*H |  |  | 0.43051 | 0.018823 | 0.817 | 1.6681 | 0.665 | -1.1218 | 0.036719 | 0.23422 | 0.013412 | 0.34309 | 0.7005 | 0.39045 | -1.6543 | 0.019845
0.0010764 | * cm2 = ft2 |  | 0.0001 | * cm2/m2 = ft2/ft2 |  |  | 0.56688 | * cm2/m = ft2/ft | RH: 18.2982; V: * cfm/ft2 = m3/m2; W: 1.699; H: * ft3/min = m3/hr
Appendix C4 Miscell Commerc'l & Institut'l Bldg Airtightness Data (C&IMISC4.lb3) | [8 empty] | DP: Converted from NIST CONTAM Library - Leakg-A + Infltr @ Alt-1 & Alt-2 in IP & SI units
National Institute of Standards & Technology - CONTAM Library
Element ID |  | Description |  |  |  |  | Leakg-A | SI units | Leakg-A | IP units | H1 cfm | H2 cfm | IP units | H1 cmh | H2 cmh | SI units
WLEXPC6A_C |  | Exterior Wall: Precast concrete panel, Building A |  |  |  |  | 2.19 | cm2/m2 | 0.000219 | ft2/ft2 | 0.00014243 | 0.00015929 | cfm/ft2 | 0.0026062 | 0.0029148 | cmh/m2
WNIO6A_CMN |  | Inoperable window, Building A, minim |  |  |  |  | 0.58 | cm2/m2 | 5.8e-05 | ft2/ft2 | 3.7721e-05 | 4.2188e-05 | cfm/ft2 | 0.00069022 | 0.00077196 | cmh/m2
WNIO6A_CMX |  | Inoperable window, Building A, maxim |  |  |  |  | 1.73 | cm2/m2 | 0.000173 | ft2/ft2 | 0.00011251 | 0.00012584 | cfm/ft2 | 0.0020588 | 0.0023026 | cmh/m2
WLEXTV6AA_C |  | Exterior Wall: Tile veneer, Building AA |  |  |  |  | 1.34 | cm2/m2 | 0.000134 | ft2/ft2 | 8.7148e-05 | 9.7468e-05 | cfm/ft2 | 0.0015947 | 0.0017835 | cmh/m2
WNIO6AA_CAV |  | Inoperable window, Building AA, typical |  |  |  |  | 0.58 | cm2/m2 | 5.8e-05 | ft2/ft2 | 3.7721e-05 | 4.2188e-05 | cfm/ft2 | 0.00069022 | 0.00077196 | cmh/m2
WLEXPC6C_C |  | Exterior Wall: Precast concrete panel, Building C |  |  |  |  | 1.96 | cm2/m2 | 0.000196 | ft2/ft2 | 0.00012747 | 0.00014257 | cfm/ft2 | 0.0023325 | 0.0026087 | cmh/m2
WNOO6C_CMN |  | Operable window, Building C, minim |  |  |  |  | 1.73 | cm2/m2 | 0.000173 | ft2/ft2 | 0.00011251 | 0.00012584 | cfm/ft2 | 0.0020588 | 0.0023026 | cmh/m2
WNOO6C_CMX |  | Operable window, Building C, maxim |  |  |  |  | 3.46 | cm2/m2 | 0.000346 | ft2/ft2 | 0.00022502 | 0.00025167 | cfm/ft2 | 0.0041175 | 0.0046051 | cmh/m2
WLEXBR6H_C |  | Exterior Wall: Brick veneer, Building H |  |  |  |  | 0.62 | cm2/m2 | 6.2e-05 | ft2/ft2 | 4.0322e-05 | 4.5097e-05 | cfm/ft2 | 0.00073783 | 0.0008252 | cmh/m2
WLEXBR6N_C |  | Exterior Wall: Brick veneer, Building N |  |  |  |  | 2.35 | cm2/m2 | 0.000235 | ft2/ft2 | 0.00015283 | 0.00017093 | cfm/ft2 | 0.0027966 | 0.0031278 | cmh/m2
WNIO6N_CAV |  | Inoperable window, Building N, typical |  |  |  |  | 0.86 | cm2/m2 | 8.6e-05 | ft2/ft2 | 5.5931e-05 | 6.2554e-05 | cfm/ft2 | 0.0010234 | 0.0011446 | cmh/m2
WLEXBR6P_C |  | Exterior Wall: Brick veneer, Building P |  |  |  |  | 1.14 | cm2/m2 | 0.000114 | ft2/ft2 | 7.4141e-05 | 8.2921e-05 | cfm/ft2 | 0.0013566 | 0.0015173 | cmh/m2
WLEXPC6S_C |  | Exterior Wall: Precast concrete panel, Building S |  |  |  |  | 3.01 | cm2/m2 | 0.000301 | ft2/ft2 | 0.00019576 | 0.00021894 | cfm/ft2 | 0.003582 | 0.0040062 | cmh/m2
WLEXPC7O_C |  | Exterior Wall: Precast concrete panel, Building O |  |  |  |  | 6.88 | cm2/m2 | 0.000688 | ft2/ft2 | 0.00044745 | 0.00050043 | cfm/ft2 | 0.0081875 | 0.009157 | cmh/m2
WLEXCW8A_C |  | Exterior Wall: Glass and metal curtain wall, Building A |  |  |  |  | 5.07 | cm2/m2 | 0.000507 | ft2/ft2 | 0.00032973 | 0.00036878 | cfm/ft2 | 0.0060335 | 0.006748 | cmh/m2
WLEXPC8B_C |  | Exterior Wall: Precast concrete panel, Building B |  |  |  |  | 2.51 | cm2/m2 | 0.000251 | ft2/ft2 | 0.00016324 | 0.00018257 | cfm/ft2 | 0.002987 | 0.0033407 | cmh/m2
WLEXPC9A_C |  | Exterior Wall: Precast concrete panel, Building A |  |  |  |  | 3.59 | cm2/m2 | 0.000359 | ft2/ft2 | 0.00023348 | 0.00026113 | cfm/ft2 | 0.0042722 | 0.0047781 | cmh/m2
WLEXPC9B_C |  | Exterior Wall: Precast concrete panel, Building B |  |  |  |  | 1.79 | cm2/m2 | 0.000179 | ft2/ft2 | 0.00011641 | 0.0001302 | cfm/ft2 | 0.0021302 | 0.0023824 | cmh/m2
WLEXPC9C_C |  | Exterior Wall: Precast concrete panel, Building C |  |  |  |  | 1.79 | cm2/m2 | 0.000179 | ft2/ft2 | 0.00011641 | 0.0001302 | cfm/ft2 | 0.0021302 | 0.0023824 | cmh/m2
WLEXCW9D_C |  | Exterior Wall: Curtain wall, Building D |  |  |  |  | 2.03 | cm2/m2 | 0.000203 | ft2/ft2 | 0.00013202 | 0.00014766 | cfm/ft2 | 0.0024158 | 0.0027018 | cmh/m2
WLEXCW9E_C |  | Exterior Wall: Curtain wall, Building E |  |  |  |  | 1.14 | cm2/m2 | 0.000114 | ft2/ft2 | 7.4141e-05 | 8.2921e-05 | cfm/ft2 | 0.0013566 | 0.0015173 | cmh/m2
WLEXPC9F_C |  | Exterior Wall: Precast concrete panel, Building F |  |  |  |  | 1.14 | cm2/m2 | 0.000114 | ft2/ft2 | 7.4141e-05 | 8.2921e-05 | cfm/ft2 | 0.0013566 | 0.0015173 | cmh/m2
WLEXPC9G_C |  | Exterior Wall: Precast concrete panel, Building G |  |  |  |  | 1.67 | cm2/m2 | 0.000167 | ft2/ft2 | 0.00010861 | 0.00012147 | cfm/ft2 | 0.0019874 | 0.0022227 | cmh/m2
WLEXCW9H_C |  | Exterior Wall: Curtain wall, Building H |  |  |  |  | 0.78 | cm2/m2 | 7.8e-05 | ft2/ft2 | 5.0728e-05 | 5.6735e-05 | cfm/ft2 | 0.00092823 | 0.0010381 | cmh/m2
WLEX10_NAV |  | Exterior Wall: Average |  |  |  |  | 0.96 | cm2/m2 | 9.6e-05 | ft2/ft2 | 6.2435e-05 | 6.9828e-05 | cfm/ft2 | 0.0011424 | 0.0012777 | cmh/m2
WLEX10_NMN |  | Exterior Wall: Minim |  |  |  |  | 0.48 | cm2/m2 | 4.8e-05 | ft2/ft2 | 3.1217e-05 | 3.4914e-05 | cfm/ft2 | 0.00057122 | 0.00063886 | cmh/m2
WLEX10_NMX |  | Exterior Wall: Maxim |  |  |  |  | 2.4 | cm2/m2 | 0.00024 | ft2/ft2 | 0.00015609 | 0.00017457 | cfm/ft2 | 0.0028561 | 0.0031943 | cmh/m2
WLEXSC11_NAV |  | Exterior Wall: School, average |  |  |  |  | 1.44 | cm2/m2 | 0.000144 | ft2/ft2 | 9.3652e-05 | 0.00010474 | cfm/ft2 | 0.0017137 | 0.0019166 | cmh/m2
WLEXSC11_NMN |  | Exterior Wall: School, minim |  |  |  |  | 0.48 | cm2/m2 | 4.8e-05 | ft2/ft2 | 3.1217e-05 | 3.4914e-05 | cfm/ft2 | 0.00057122 | 0.00063886 | cmh/m2
WLEXSC11_NMX |  | Exterior Wall: School, maxim |  |  |  |  | 1.6 | cm2/m2 | 0.00016 | ft2/ft2 | 0.00010406 | 0.00011638 | cfm/ft2 | 0.0019041 | 0.0021295 | cmh/m2
WLEXSC12_NAV |  | Exterior Wall: School, average |  |  |  |  | 4.48 | cm2/m2 | 0.000448 | ft2/ft2 | 0.00029136 | 0.00032586 | cfm/ft2 | 0.0053314 | 0.0059627 | cmh/m2
WLEXSC12_NMN |  | Exterior Wall: School, minim |  |  |  |  | 3.2 | cm2/m2 | 0.00032 | ft2/ft2 | 0.00020812 | 0.00023276 | cfm/ft2 | 0.0038081 | 0.0042591 | cmh/m2
WLEXSC12_NMX |  | Exterior Wall: School, maxim |  |  |  |  | 4.8 | cm2/m2 | 0.00048 | ft2/ft2 | 0.00031217 | 0.00034914 | cfm/ft2 | 0.0057122 | 0.0063886 | cmh/m2
WLEXSC13_CAV |  | Exterior Wall: Retail stores/shopping malls, average |  |  |  |  | 7.84 | cm2/m2 | 0.000784 | ft2/ft2 | 0.00050988 | 0.00057026 | cfm/ft2 | 0.0093299 | 0.010435 | cmh/m2
WLEXSC13_CMN |  | Exterior Wall: Retail stores/shopping malls, minim |  |  |  |  | 4 | cm2/m2 | 0.0004 | ft2/ft2 | 0.00026014 | 0.00029095 | cfm/ft2 | 0.0047602 | 0.0053238 | cmh/m2
WLEXSC13_CMX |  | Exterior Wall: Retail stores/shopping malls, maxim |  |  |  |  | 11.2 | cm2/m2 | 0.00112 | ft2/ft2 | 0.0007284 | 0.00081466 | cfm/ft2 | 0.013328 | 0.014907 | cmh/m2
WLELCC14A_C |  | Elevator shaft wall, cast-in-place concrete, 17 story office building |  |  |  |  | 5.55 | cm2/m2 | 0.000555 | ft2/ft2 | 0.00036095 | 0.00040369 | cfm/ft2 | 0.0066047 | 0.0073868 | cmh/m2
WLELCC14B_C |  | Elevator shaft wall, cast-in-place concrete, 14 story office building |  |  |  |  | 2.25 | cm2/m2 | 0.000225 | ft2/ft2 | 0.00014633 | 0.00016366 | cfm/ft2 | 0.0026776 | 0.0029947 | cmh/m2
WLELCC14C_C |  | Elevator shaft wall, cast-in-place concrete, 12 story office building |  |  |  |  | 1.72 | cm2/m2 | 0.000172 | ft2/ft2 | 0.00011186 | 0.00012511 | cfm/ft2 | 0.0020469 | 0.0022893 | cmh/m2
WLELCOBL14D_C |  | Elevator shaft wall, concrete block, 6 story office building |  |  |  |  | 5.55 | cm2/m2 | 0.000555 | ft2/ft2 | 0.00036095 | 0.00040369 | cfm/ft2 | 0.0066047 | 0.0073868 | cmh/m2
WLELCC14E_C |  | Elevator shaft wall, cast-in-place concrete, 16 story office building |  |  |  |  | 0.75 | cm2/m2 | 7.5e-05 | ft2/ft2 | 4.8777e-05 | 5.4553e-05 | cfm/ft2 | 0.00089253 | 0.00099822 | cmh/m2
WLELTIBL14F_C |  | Elevator shaft wall, clay tile block, 10 story office building |  |  |  |  | 6.15 | cm2/m2 | 0.000615 | ft2/ft2 | 0.00039997 | 0.00044733 | cfm/ft2 | 0.0073187 | 0.0081854 | cmh/m2
WLELCC14G_C |  | Elevator shaft wall, cast-in-place concrete, 14 story office building |  |  |  |  | 2.25 | cm2/m2 | 0.000225 | ft2/ft2 | 0.00014633 | 0.00016366 | cfm/ft2 | 0.0026776 | 0.0029947 | cmh/m2
WLSRCC14A_C |  | Stair shaft wall, cast-in-place concrete, 19 story office building |  |  |  |  | 0.45 | cm2/m2 | 4.5e-05 | ft2/ft2 | 2.9266e-05 | 3.2732e-05 | cfm/ft2 | 0.00053552 | 0.00059893 | cmh/m2
WLSRCC14B_C |  | Stair shaft wall, cast-in-place concrete, 23 story office building |  |  |  |  | 0.07 | cm2/m2 | 7e-06 | ft2/ft2 | 4.5525e-06 | 5.0916e-06 | cfm/ft2 | 8.3303e-05 | 9.3167e-05 | cmh/m2
WLSRCC14C_C |  | Stair shaft wall, cast-in-place concrete, 28 story office building |  |  |  |  | 0.15 | cm2/m2 | 1.5e-05 | ft2/ft2 | 9.7554e-06 | 1.0911e-05 | cfm/ft2 | 0.00017851 | 0.00019964 | cmh/m2
WLSRCC14D_C |  | Stair shaft wall, cast-in-place concrete, 23 story office building |  |  |  |  | 0.41 | cm2/m2 | 4.1e-05 | ft2/ft2 | 2.6665e-05 | 2.9822e-05 | cfm/ft2 | 0.00048792 | 0.00054569 | cmh/m2
WLSRCC14E_C |  | Stair shaft wall, cast-in-place concrete, 15 story office building |  |  |  |  | 0.3 | cm2/m2 | 3e-05 | ft2/ft2 | 1.9511e-05 | 2.1821e-05 | cfm/ft2 | 0.00035701 | 0.00039929 | cmh/m2
WLSRCC14F_C |  | Stair shaft wall, cast-in-place concrete, 17 story office building |  |  |  |  | 1.42 | cm2/m2 | 0.000142 | ft2/ft2 | 9.2351e-05 | 0.00010329 | cfm/ft2 | 0.0016899 | 0.00189 | cmh/m2
WLSRTIBL14G_C |  | Stair shaft wall, clay tile block, 11 story office building |  |  |  |  | 0.67 | cm2/m2 | 6.7e-05 | ft2/ft2 | 4.3574e-05 | 4.8734e-05 | cfm/ft2 | 0.00079733 | 0.00089174 | cmh/m2
WLSRCC14H_C |  | Stair shaft wall, cast-in-place concrete, 12 story office building |  |  |  |  | 0.37 | cm2/m2 | 3.7e-05 | ft2/ft2 | 2.4063e-05 | 2.6913e-05 | cfm/ft2 | 0.00044032 | 0.00049246 | cmh/m2
DREL14_CMN |  | Elevator doors, 7 office buildings, minim |  |  |  |  | 187.5 | cm2/door | 0.01875 | ft2/ft2 | 0.012194 | 0.013638 | cfm/ft2 | 0.22313 | 0.24956 | cmh/m2
DREL14_CMX |  | Elevator doors, 7 office buildings, maxim |  |  |  |  | 262.5 | cm2/door | 0.02625 | ft2/ft2 | 0.017072 | 0.019094 | cfm/ft2 | 0.31239 | 0.34938 | cmh/m2
DRSR14_CMN |  | Stair shaft doors, 8 office buildings, minim |  |  |  |  | 75 | cm2/door | 0.0075 | ft2/ft2 | 0.0048777 | 0.0054553 | cfm/ft2 | 0.089253 | 0.099822 | cmh/m2
DRSR14_CMX |  | Stair shaft doors, 8 office buildings, maxim |  |  |  |  | 187.5 | cm2/door | 0.01875 | ft2/ft2 | 0.012194 | 0.013638 | cfm/ft2 | 0.22313 | 0.24956 | cmh/m2
FLCO15_CMN |  | Floor: Office building, reinforced concrete, minim |  |  |  |  | 0.18 | cm2/m2 | 1.8e-05 | ft2/ft2 | 1.1706e-05 | 1.3093e-05 | cfm/ft2 | 0.00021421 | 0.00023957 | cmh/m2
FLCO15_CMX |  | Floor: Office building, reinforced concrete, maxim |  |  |  |  | 0.35 | cm2/m2 | 3.5e-05 | ft2/ft2 | 2.2763e-05 | 2.5458e-05 | cfm/ft2 | 0.00041651 | 0.00046584 | cmh/m2
WLEX16A_R |  | Exterior Wall: Individual apartment (#405) in high-rise building |  |  |  |  | 1.87 | cm2/m2 | 0.000187 | ft2/ft2 | 0.00012162 | 0.00013602 | cfm/ft2 | 0.0022254 | 0.0024889 | cmh/m2
WLEX16B_R |  | Exterior Wall: Individual apartment (#509) in high-rise building |  |  |  |  | 2.36 | cm2/m2 | 0.000236 | ft2/ft2 | 0.00015349 | 0.00017166 | cfm/ft2 | 0.0028085 | 0.0031411 | cmh/m2
WLEX16C_R |  | Exterior Wall: Individual apartment (#609) in high-rise building |  |  |  |  | 2.33 | cm2/m2 | 0.000233 | ft2/ft2 | 0.00015153 | 0.00016948 | cfm/ft2 | 0.0027728 | 0.0031011 | cmh/m2
WLEX16D_R |  | Exterior Wall: Individual apartment (#1009) in high-rise building |  |  |  |  | 1.57 | cm2/m2 | 0.000157 | ft2/ft2 | 0.00010211 | 0.0001142 | cfm/ft2 | 0.0018684 | 0.0020896 | cmh/m2
WLEXBRBL17_R |  | Exterior Wall: 5-story apartment building, brick and block backup |  |  |  |  | 2.55 | cm2/m2 | 0.000255 | ft2/ft2 | 0.00016584 | 0.00018548 | cfm/ft2 | 0.0030346 | 0.0033939 | cmh/m2
FLCEAP17_RMN |  | Floor/ceiling interface: 5-story apartment building, minim |  |  |  |  | 0.11 | cm2/m2 | 1.1e-05 | ft2/ft2 | 7.154e-06 | 8.0011e-06 | cfm/ft2 | 0.0001309 | 0.00014641 | cmh/m2
FLCEAP17_RMX |  | Floor/ceiling interface: 5-story apartment building, maxim |  |  |  |  | 0.43 | cm2/m2 | 4.3e-05 | ft2/ft2 | 2.7965e-05 | 3.1277e-05 | cfm/ft2 | 0.00051172 | 0.00057231 | cmh/m2
FLCEAP17_RAV |  | Floor/ceiling interface: 5-story apartment building, average |  |  |  |  | 0.32 | cm2/m2 | 3.2e-05 | ft2/ft2 | 2.0812e-05 | 2.3276e-05 | cfm/ft2 | 0.00038081 | 0.00042591 | cmh/m2
WLINAP17_RMN |  | Interior partition: 5-story apartment building, minim |  |  |  |  | 0.37 | cm2/m2 | 3.7e-05 | ft2/ft2 | 2.4063e-05 | 2.6913e-05 | cfm/ft2 | 0.00044032 | 0.00049246 | cmh/m2
WLINAP17_RMX |  | Interior partition: 5-story apartment building, maxim |  |  |  |  | 2.25 | cm2/m2 | 0.000225 | ft2/ft2 | 0.00014633 | 0.00016366 | cfm/ft2 | 0.0026776 | 0.0029947 | cmh/m2
WLINAP17_RAV |  | Interior partition: 5-story apartment building, average |  |  |  |  | 1.12 | cm2/m2 | 0.000112 | ft2/ft2 | 7.284e-05 | 8.1466e-05 | cfm/ft2 | 0.0013328 | 0.0014907 | cmh/m2
WLEXAP18_R |  | Exterior Wall: Multi-story apartment building |  |  |  |  | 1.46 | cm2/m2 | 0.000146 | ft2/ft2 | 9.4953e-05 | 0.0001062 | cfm/ft2 | 0.0017375 | 0.0019432 | cmh/m2
WLEXAP19D_R |  | Exterior Wall: High-story apartment building D |  |  |  |  | 1.65 | cm2/m2 | 0.000165 | ft2/ft2 | 0.00010731 | 0.00012002 | cfm/ft2 | 0.0019636 | 0.0021961 | cmh/m2
WLEXAP19V_R |  | Exterior Wall: High-story apartment building V |  |  |  |  | 2.62 | cm2/m2 | 0.000262 | ft2/ft2 | 0.00017039 | 0.00019057 | cfm/ft2 | 0.0031179 | 0.0034871 | cmh/m2