| 1/7/2009 - | Credit Interpretation Request We are trying to determine the correct baseline HVAC system type for a new 9 story, 400,000 ft2 hospital in San Francisco. Per 90.1-2004 section G3.1.1 exception C, the baseline should be System Type 3 (packaged single zone systems with DX cooling) in ".any zones having special pressurization relationships, cross contamination requirements, or code required minimum circulation rates." This exception is vague but appears to require System 3 in almost all hospital zones since almost all hospital zones have "special pressurization relationships, cross contamination requirements, or code required minimum circulation rates." We are not aware of any large, multi-story hospitals in the U.S. that use packaged single zone systems. Such systems are simply not practical or even possible for most zones in a large hospital. For example, it would probably be impossible to find enough roof or shaft space to serve a 9 story hospital with rooftop packaged single zone units. A few exceptional hospitals are using variable air volume (VAV) reheat in some zones with special pressurization requirements but the majority of hospitals being built today use constant volume (CV) reheat in such zones. The 90.1 baseline is intended to represent the industry standard of care and constant volume reheat (not packaged single zone) is the current standard of care where pressurization is required. Constant volume is the industry standard because it is simpler and considerably less expensive and less maintenance than variable volume. Constant volume systems in hospitals either have no terminal units or have standard CV terminal units on the supply side but not on the return/exhaust side. VAV systems, on the other hand, require terminal units on both the supply and return/exhaust sides. Furthermore, terminal units in VAV systems in California are typically not standard VAV terminal units (e.g. butterfly damper type) but are special airflow control devices (e.g. Phoenix valves) due to the local oversight agency's (OSHPD's) stringent room relative pressure requirements and lint issues for standard VAV terminals on the exhaust side. Such control devices are considerably more expensive than standard VAV terminal units. Therefore we request confirmation that the following clarification (for hospitals only) of 90.1-2004 section G3.1.1 exception C provides a suitable baseline in accordance with the intent of LEED®.: (c) If the baseline HVAC system type is 5, 6, 7, or 8, and if packaged single zone are impractical or impossible, then use a separate constant volume reheat system conforming with the requirements of System 7 for all zones having special pressurization relationships, cross-contamination requirements, or code required minimum circulation rates. Where constant volume reheat is to be used in the baseline, as described above, we propose to use the constant volume baseline fan motor brake horsepower equation in 90.1-2007 Table G3.1.2.9 (bhp = CFMs · 0.00094 + A). Supporting information: - Per 2007 California Mechanical Code section 407.5.1, "variable air volume systems subjecting the patient to a fluctuating air movement are not acceptable for airborne infection isolation rooms, protective environment rooms or those critically sensitive areas listed in Table 315." Table 315 lists: Operating room, Cystoscopy, Cardiac cath lab, Delivery room, Recovery room, Newborn nursery, Intensive-care newborn nursery, Intensive care. - 90.1-2004 (section 6.5.2.1, exception b) allows constant volume reheat in "Zones where special pressurization relationships, cross-contamination requirements, or code-required minimum circulation rates are such that variable air volume systems are impractical." - Constant volume airflows are required for certain rooms, regardless of pressurization: 2007 CMC for OSHPD building requires that "Ventilation shall not be reduced in rooms specifically used for airborne infection control, such as waiting rooms, triage rooms, corridors, reception areas, areas adjacent to waiting areas, airborne infection isolation rooms, negative pressure exam room, negative pressure x-ray treatment rooms, and protective environment rooms." - Our proposed rule for modeling the baseline system is based on Appendix 1 of the Green Guide for Health Care (version 2.2). This Guide has broad industry participation and will certainly influence the modeling rules in the upcoming LEED for Healthcare Rating System. - Examples of recent hospitals using constant volume reheat in zones with pressurization requirements: Every Kaiser hospital (including Kaiser Santa Clara, Kaiser Vallejo - Replacement Hospital, and Kaiser Vacaville) and Community Hospital of Monterey Peninsula |
| --- | --- |
| 2/20/2009 - | Ruling It appears that the applicant is requesting the use of a constant volume baseline HVAC system. As is noted in the request, several rooms in a hospital have special pressurization and/or cross-contamination requirements that can not be adequately met by a VAV system. These spaces, however, satisfy the requirements of Exception (c) to Section G3.1.1 of ASHRAE 90.1-2004 and the baseline HVAC system may be modeled as System 3 – packaged single zone air conditioner (PSZ). The description of System 3 in Table G3.1.1B indicates that the fan control is “constant volume.” Therefore, it appears that the system requirements outlined in Section G3.1.1 adequately address the design conditions and allows for the use of constant volume systems for the spaces in question. In addition, widely-available building simulation programs (such as DOE-2.2) do allow dehumidification control with PSZ systems. Thus, the PSZ system can modeled as a constant air-volume system that overcools and reheats to meet required humidity levels. |