## ASHRAE 90.1-2007
ASHRAE 90.1-2007 Baseline Fan Power Calculator
Residential Fans (Systems 1 - 2)
| AHU name | Supply cfm (CFMS) |  |  |  | Pfan (watts) | W/cfm
[6 empty] | 0 | #DIV/0!
[6 empty] | 0 | #DIV/0!
[6 empty] | 0 | #DIV/0!
[6 empty] | 0 | #DIV/0!
[6 empty] | 0 | #DIV/0!
Nonresidential Constant Volume Fans (Systems 3 - 4)
| AHU name | Supply cfm (CFMS) |  |  |  | Table 6.5.3.1.1B Pressure Drop Adjustment (PD) | A | bhp | Lookup Table Row | Table 10.8 Fan Motor Efficiency | Pfan (watts) | W/cfm
[7 empty] | 0 | 0 | 20 | 82.5% | 0 | #DIV/0!
[7 empty] | 0 | 0 | 20 | 82.5% | 0 | #DIV/0!
[7 empty] | 0 | 0 | 20 | 82.5% | 0 | #DIV/0!
[7 empty] | 0 | 0 | 20 | 82.5% | 0 | #DIV/0!
[7 empty] | 0 | 0 | 20 | 82.5% | 0 | #DIV/0!
Nonresidential Variable Volume Fans (Systems 5 - 8)
| AHU name | Supply cfm (CFMS) | Outside Air Ratio | Fresh air CFM | Return air CFM | Table 6.5.3.1.1B Pressure Drop Adjustment (PD) | A | bhp | Lookup Table Row | Table 10.8 Fan Motor Efficiency | Pfan (watts) | W/cfm | kW/cfm
| W&S 1 | 24247 | 0.494 | 11978.018 | 12268.982 | 1.4 | 4.0946 | 35.6157 | 9 | 93% | 28569.1363 | 1.1783 | 0.0011783
| W 2 | 7386 | 0.468 | 3456.648 | 3929.352 | 0.9 | 1.6092 | 11.211 | 13 | 91% | 9190.5153 | 1.2443 | 0.0012443
| W 3 | 5980 | 0.573 | 3426.54 | 2553.46 | 1.4 | 2.0266 | 9.8006 | 14 | 89.5% | 8169.015 | 1.3661 | 0.0013661
| W 4 | 6363 | 0.461 | 2933.343 | 3429.657 | 1.4 | 2.1564 | 10.4283 | 13 | 91% | 8548.9362 | 1.3435 | 0.0013435
| Bas | 23726 | 0.207 | 4911.282 | 18814.718 | 1.4 | 8.0408 | 38.8846 | 9 | 93% | 31191.2747 | 1.3146 | 0.0013146
| N 1 | 6177 | 0.512 | 3162.624 | 3014.376 | 1.4 | 2.0934 | 10.1235 | 13 | 91% | 8299.038 | 1.3435 | 0.0013435
| N 2 | 4640 | 0.259 | 1201.76 | 3438.24 | 1.4 | 1.5725 | 7.6045 | 14 | 89.5% | 6338.4999 | 1.3661 | 0.0013661
| N 3 | 6197 | 0.559 | 3464.123 | 2732.877 | 1.4 | 2.1002 | 10.1563 | 13 | 91% | 8325.9088 | 1.3435 | 0.0013435
| N 4 | 6381 | 0.605 | 3860.505 | 2520.495 | 1.4 | 2.1625 | 10.4578 | 13 | 91% | 8573.1199 | 1.3435 | 0.0013435
| GF | 9479 | 0.178 | 1687.262 | 7791.738 | 1.4 | 3.2124 | 15.5351 | 12 | 91% | 12735.4025 | 1.3435 | 0.0013435
| S 2 | 18526 | 0.686 | 12708.836 | 5817.164 | 1.4 | 6.2785 | 30.3623 | 9 | 93% | 24355.1191 | 1.3146 | 0.0013146
Table 6.5.3.1.1B Fan Power Limitation Pressure Drop Adjustment
| Device | [6 empty] | Adjustment
Credits
| Fully ducted return and/or exhaust air systems | [6 empty] | 0.5 in. w.c.
| Return and/or exhaust airflow control devices | [6 empty] | 0.5 in. w.c.
| Exhaust filters, scrubbers, or other exhaust treatment | [6 empty] | The pressure drop of device calculated at fan system design condition
| Particulate Filtration Credit: MERV 9-12 | [6 empty] | 0.5 in. w.c.
| Particulate Filtration Credit: MERV 13-15 | [6 empty] | 0.9 in. w.c.
| Particulate Filtration Credit: MERV 16 and greater and electronically enhanced filters | [6 empty] | Pressure drop calculated at 2x clean filter pressure drop at fan system design condition
| Carbon and other gas-phase air cleaners | [6 empty] | Clean filter pressure drop at fan system design condition
| Heat recovery device | [6 empty] | Pressure drop of device at fan system design condition
| Evaporative humidifier/cooler in series with another cooling coil | [6 empty] | Pressure drop of device at fan system design condition
| Sound attenuation section | [6 empty] | 0.15 in. w.c.
Deductions
| Fume Hood Exhaust Exception (required if 6.5.3.1.1 Exception [c] is taken) | [6 empty] | -1.0 in. w.c.

## Motor Efficiency Table (hidden)
Row | Motor Horsepower | Minimum Nominal Full-Load Efficiency
1 | 999999 | 95
2 | 200 | 95
3 | 150 | 95
4 | 125 | 94.5
5 | 100 | 94.5
6 | 75 | 94.1
7 | 60 | 93.6
8 | 50 | 93
9 | 40 | 93
10 | 30 | 92.4
11 | 25 | 92.4
12 | 20 | 91
13 | 15 | 91
14 | 10 | 89.5
15 | 7.5 | 89.5
16 | 5 | 87.5
17 | 3 | 87.5
18 | 2 | 84
19 | 1.5 | 84
20 | 1 | 82.5