## VSD
[10 empty] | Make & Model: | VSD Chiller
[5 empty] | Color Code: | [7 empty] | Reset Temp (F)
[5 empty] | Cells without a fill color are data requested from the manufacturer |  |  |  | gpm/ton |  | Flow (gpm) | Head (ft) | Max | Min
[5 empty] | Calculated values |  |  |  | 2.2375 | Condenser | 1163.5 | 15.7 | 75 | 55
[5 empty] | Calculated values to be used for obtaining requested data |  |  | DT: | 17.1783 | Evaporator | 726.5 | 11.6 | 48 | 42
[5 empty] | Points to be used for obtaining requested data | [5 empty] | Min Capacity: | 50 | (tons) With Hot-Gas bypass
[5 empty] | Ref Points | [5 empty] | Min Capacity: | 75 | (tons) Without Hot-Gas bypass
[5 empty] | CapNom | [5 empty] | MIN-RATIO: | 0.096154
[5 empty] | EIRnom | [5 empty] | HGB-RATIO: | 0.14423
|  |  | Info From Manufacturer | [5 empty] | eQuest Detailed Interface Input (Opt 1) | [11 empty] | eQuest INP File Input (Opt 2)
[9 empty] | CAP-fCHWT&ECT |  |  |  | EIR-fCHWT&ECT |  |  |  | EIR-fPLR&dT
|  |  | Full Load Ratio | [5 empty] | Indep-1 (X) | Indep-2 (Y) | Depend (Z) |  | Indep-1 (X) | Indep-2 (Y) | Depend (Z) | (For Ref) | Indep-1 (X) | Indep-2 (Y) | Depend (Z) |  | "VSD Chiller-CAP-fCHWT&ECT" = CURVE-FIT
| CHWS (F) | ECT (F) | CapOp (tons)* | kW/ton | EIRop | Cap (Mbtu/h) | COP |  | CHWS (F) | ECT (F) | CAPFT |  | CHWS (F) | ECT (F) | EIRFT | Q/(Qref*CAPFT) | PLR | dT | EIRFPLR |  | TYPE = BI-QUADRATIC-T
| 42 | 75 | 520 | 0.518 | 0.14728 | 6.24 | 6.7896 |  | 42 | 75 | 1.000 |  | 42 | 75 | 1.000 | 1 | 1.00 | 33 | 1.000 |  | INPUT-TYPE = DATA
| 42 | 71 | 535 | 0.474 | 0.13477 | 6.42 | 7.4198 |  | 42 | 71 | 1.029 |  | 42 | 71 | 0.915 | 0.8 | 0.80 | 33 | 0.680 |  | INDEPENDENT-1 = ( 42, 42, 42, 42, 42, 42, 45, 45, 45, 45,
| 42 | 67 | 550 | 0.343 | 0.097526 | 6.6 | 10.2536 |  | 42 | 67 | 1.058 |  | 42 | 67 | 0.662 | 0.6 | 0.60 | 33 | 0.430 |  | 45, 45, 45, 45, 48, 48, 48, 48, 48, 48 )
| 42 | 63 | 560 | 0.337 | 0.09582 | 6.72 | 10.4362 |  | 42 | 63 | 1.077 |  | 42 | 63 | 0.651 | 0.4 | 0.40 | 33 | 0.236 |  | INDEPENDENT-2 = ( 75, 71, 67, 63, 59, 55, 75, 72, 69, 66,
| 42 | 59 | 575 | 0.342 | 0.097242 | 6.9 | 10.2836 |  | 42 | 59 | 1.106 |  | 42 | 59 | 0.660 | 0.15 | 0.15 | 33 | 0.097 |  | 63, 60, 57, 55, 75, 71, 67, 63, 59, 55 )
| 42 | 55 | 575 | 0.344 | 0.097811 | 6.9 | 10.2238 |  | 42 | 55 | 1.106 |  | 42 | 55 | 0.664 | 0.99979 | 1.00 | 15 | 1.000 | Pwr ratio should be relative to Pwr at PLR=1 for this dT! | DEPENDENT = ( 1.000, 1.029, 1.058, 1.077, 1.106,
| 45 | 75 | 555 | 0.492 | 0.13989 | 6.66 | 7.1484 |  | 45 | 75 | 1.067 |  | 45 | 75 | 0.950 | 0.89981 | 0.90 | 15 | 0.837 |  | 1.106, 1.067, 1.087, 1.106, 1.106,
| 45 | 72 | 565 | 0.459 | 0.13051 | 6.78 | 7.6623 |  | 45 | 72 | 1.087 |  | 45 | 72 | 0.886 | 0.79983 | 0.80 | 15 | 0.699 |  | 1.106, 1.106, 1.106, 1.106, 1.106,
| 45 | 69 | 575 | 0.433 | 0.12312 | 6.9 | 8.1224 |  | 45 | 69 | 1.106 |  | 45 | 69 | 0.836 | 0.69985 | 0.70 | 15 | 0.578 |  | 1.106, 1.106, 1.106, 1.106, 1.106 )
| 45 | 66 | 575 | 0.405 | 0.11516 | 6.9 | 8.6839 |  | 45 | 66 | 1.106 |  | 45 | 66 | 0.782 | 0.59987 | 0.60 | 15 | 0.467 |  | ..
| 45 | 63 | 575 | 0.381 | 0.10833 | 6.9 | 9.231 |  | 45 | 63 | 1.106 |  | 45 | 63 | 0.736 | 0.4999 | 0.50 | 15 | 0.368 |  | "VSD Chiller-EIR-fCHWT&ECT" = CURVE-FIT
| 45 | 60 | 575 | 0.356 | 0.10122 | 6.9 | 9.8792 |  | 45 | 60 | 1.106 |  | 45 | 60 | 0.687 | 0.39992 | 0.40 | 15 | 0.280 |  | TYPE = BI-QUADRATIC-T
| 45 | 57 | 575 | 0.332 | 0.094399 | 6.9 | 10.5934 |  | 45 | 57 | 1.106 |  | 45 | 57 | 0.641 | 0.29994 | 0.30 | 15 | 0.205 |  | INPUT-TYPE = DATA
| 45 | 55 | 575 | 0.317 | 0.090134 | 6.9 | 11.0946 |  | 45 | 55 | 1.106 |  | 45 | 55 | 0.612 | 0.19996 | 0.20 | 15 | 0.145 |  | INDEPENDENT-1 = ( 42, 42, 42, 42, 42, 42, 45, 45, 45, 45,
| 48 | 75 | 575 | 0.459 | 0.13051 | 6.9 | 7.6623 |  | 48 | 75 | 1.106 |  | 48 | 75 | 0.886 | 0.099979 | 0.10 | 15 | 0.094 |  | 45, 45, 45, 45, 48, 48, 48, 48, 48, 48 )
| 48 | 71 | 575 | 0.421 | 0.1197 | 6.9 | 8.3539 |  | 48 | 71 | 1.106 |  | 48 | 71 | 0.813 | 0.99979 | 1.00 | 7 | 1.000 | Pwr ratio should be relative to Pwr at PLR=1 for this dT! | INDEPENDENT-2 = ( 75, 71, 67, 63, 59, 55, 75, 72, 69, 66,
| 48 | 67 | 575 | 0.386 | 0.10975 | 6.9 | 9.1114 |  | 48 | 67 | 1.106 |  | 48 | 67 | 0.745 | 0.69985 | 0.70 | 7 | 0.578 |  | 63, 60, 57, 55, 75, 71, 67, 63, 59, 55 )
| 48 | 63 | 575 | 0.352 | 0.10009 | 6.9 | 9.9915 |  | 48 | 63 | 1.106 |  | 48 | 63 | 0.680 | 0.4999 | 0.50 | 7 | 0.366 |  | DEPENDENT = ( 1.000, 0.915, 0.662, 0.651, 0.660,
| 48 | 59 | 575 | 0.32 | 0.090987 | 6.9 | 10.9906 |  | 48 | 59 | 1.106 |  | 48 | 59 | 0.618 | [5 empty] | 0.664, 0.950, 0.886, 0.836, 0.782,
| 48 | 55 | 575 | 0.288 | 0.081888 | 0.081888 | 12.2118 |  | 48 | 55 | 1.106 |  | 48 | 55 | 0.556 | [5 empty] | 0.736, 0.687, 0.641, 0.612, 0.886,
|  |  | *Note to Chiller Manufacturer's Rep., Please allow program to size | [17 empty] | 0.813, 0.745, 0.680, 0.618, 0.556 )
|  |  | (don't input kW into your program) | [17 empty] | ..
"VSD Chiller-EIR-fPLR&dT" = CURVE-FIT
|  |  | Part Load Ratio | [17 empty] | TYPE = BI-QUADRATIC-RATIO&DT
% Hourly Capacity (PLR) |  |  | Qchiller (tons) | PwrPLR (kW) | [16 empty] | INPUT-TYPE = DATA
100% | 42 | 75 | 520 | 269.36 | PwrOp | [15 empty] | INDEPENDENT-1 = ( 1.00, 0.80, 0.60, 0.40, 0.15
80% | 42 | 75 | 416 | 183.04 | [5 empty] | CAPFT = ( CapOp / CapNom ) | [10 empty] | 1.00, 0.90, 0.80, 0.70, 0.60,
60% | 42 | 75 | 312 | 115.752 | [5 empty] | EIRFT = EIRop / EIRnom | [10 empty] | 0.50, 0.40, 0.30, 0.20, 0.10,
40% | 42 | 75 | 208 | 63.44 | [5 empty] | PLR = Current chiller load/Max capacity with equal CHWS & ECT temperatures (Given to Manufacturer) | [10 empty] | 1.00, 0.70, 0.50 )
15% | 42 | 75 | 78 | 26.052 | [5 empty] | EIRfPLR = PwrPLR / PwrOp | [10 empty] | INDEPENDENT-2 = ( 33, 33, 33, 33, 33
100% | 45 | 60 | 575 | 204.7 | PwrOp |  |  |  |  | CapNom: | 520 | tons | [8 empty] | 15, 15, 15, 15, 15,
90% | 45 | 60 | 517.5 | 171.2925 | [5 empty] | EIRnom: | 0.14728 | [9 empty] | 15, 15, 15, 15, 15,
80% | 45 | 60 | 460 | 143.06 |  |  |  |  | CapOp: | Chiller capacity at specified temperature conditions | [10 empty] | 7, 7, 7 )
70% | 45 | 60 | 402.5 | 118.335 |  |  |  |  | CapNom: | Reference capacity, which can be selected based on either design capacity or ARI-rated capacity, but must be equal to the nominal capcity defined for the chiller | [10 empty] | DEPENDENT = ( 1.000, 0.680, 0.430, 0.236, 0.097,
60% | 45 | 60 | 345 | 95.565 | [16 empty] | 1.000, 0.837, 0.699, 0.578, 0.467,
50% | 45 | 60 | 287.5 | 75.325 | [16 empty] | 0.368, 0.280, 0.205, 0.145, 0.094,
40% | 45 | 60 | 230 | 57.27 | [16 empty] | 1.000, 0.578, 0.366 )
30% | 45 | 60 | 172.5 | 41.9175 | [16 empty] | ..
20% | 45 | 60 | 115 | 29.67
10% | 45 | 60 | 57.5 | 19.32
100% | 48 | 55 | 575 | 165.6 | PwrOp
70% | 48 | 55 | 402.5 | 95.795
50% | 48 | 55 | 287.5 | 60.6625
30% | 48 | 55 | 172.5 | Head pressure too low.
10% | 48 | 55 | 57.5 | Head pressure too low.
*Note to Chiller Manufacturer's Rep., Please allow program to size
(don't input capacity and kW into your program)

## Constant Speed
[10 empty] | Make & Model: | Constant Speed
[5 empty] | Color Code: | [7 empty] | Reset Temp (F)
[5 empty] | Cells without a fill color are data requested from the manufacturer |  |  |  | gpm/ton |  | Flow (gpm) | Head (ft) | Max | Min
[5 empty] | Calculated values |  |  |  | 2.1953 | Condenser | 1163.5 | 15.7 | 75 | 55
[5 empty] | Calculated values to be used for obtaining requested data |  |  | DT: | 17.5086 | Evaporator | 726.5 | 11.6 | 48 | 42
[5 empty] | Points to be used for obtaining requested data | [5 empty] | Min Capacity: | 50 | (tons) With Hot-Gas bypass
[5 empty] | Ref Points | [5 empty] | Min Capacity: | 75 | (tons) Without Hot-Gas bypass
[5 empty] | CapNom | [5 empty] | MIN-RATIO: | 0.09434
[5 empty] | EIRnom | [5 empty] | HGB-RATIO: | 0.14151
|  |  | Info From Manufacturer | [5 empty] | eQuest Detailed Interface Input (Opt 1) | [10 empty] | eQuest INP File Input (Opt 2)
[9 empty] | CAP-fCHWT&ECT |  |  |  | EIR-fCHWT&ECT |  |  | EIR-fPLR&dT
|  |  | Full Load Ratio | [5 empty] | Indep-1 (X) | Indep-2 (Y) | Depend (Z) |  | Indep-1 (X) | Indep-2 (Y) | Depend (Z) | Indep-1 (X) | Indep-2 (Y) | Depend (Z) |  | "Constant Speed-CAP-fCHWT&ECT" = CURVE-FIT
| CHWS (F) | ECT (F) | CapOp (tons)* | kW/ton | EIRop | Cap (Mbtu/h) | COP |  | CHWS (F) | ECT (F) | CAPFT |  | CHWS (F) | ECT (F) | EIRFT | PLR | dT | EIRFPLR |  | TYPE = BI-QUADRATIC-T
| 42 | 75 | 530 | 0.535 | 0.15212 | 6.36 | 6.5738 |  | 42 | 75 | 1.000 |  | 42 | 75 | 1.000 | 1.00 | 33 | 1.000 |  | INPUT-TYPE = DATA
| 42 | 71 | 545 | 0.52 | 0.14785 | 6.54 | 6.7635 |  | 42 | 71 | 1.028 |  | 42 | 71 | 0.972 | 0.80 | 33 | 0.769 |  | INDEPENDENT-1 = ( 42, 42, 42, 42, 42, 42, 45, 45, 45, 45,
| 42 | 67 | 565 | 0.501 | 0.14245 | 6.78 | 7.02 |  | 42 | 67 | 1.066 |  | 42 | 67 | 0.936 | 0.60 | 33 | 0.640 |  | 45, 45, 45, 45, 48, 48, 48, 48, 48, 48 )
| 42 | 63 | 555 | 0.471 | 0.13392 | 6.66 | 7.4671 |  | 42 | 63 | 1.047 |  | 42 | 63 | 0.880 | 0.40 | 33 | 0.507 |  | INDEPENDENT-2 = ( 75, 71, 67, 63, 59, 55, 75, 72, 69, 66,
| 42 | 59 | 535 | 0.44 | 0.12511 | 6.42 | 7.9932 |  | 42 | 59 | 1.009 |  | 42 | 59 | 0.822 | 0.15 | 33 | 0.307 |  | 63, 60, 57, 55, 75, 71, 67, 63, 59, 55 )
| 42 | 55 | 505 | 0.415 | 0.118 | 6.06 | 8.4747 |  | 42 | 55 | 0.953 |  | 42 | 55 | 0.776 | 1.00 | 15 | 1.000 | Pwr ratio should be relative to Pwr at PLR=1 for this dT! | DEPENDENT = ( 1.000, 1.028, 1.066, 1.047, 1.009,
| 45 | 75 | 550 | 0.516 | 0.14672 | 6.6 | 6.8159 |  | 45 | 75 | 1.038 |  | 45 | 75 | 0.964 | 0.90 | 15 | 0.881 |  | 0.953, 1.038, 1.066, 1.094, 1.028,
| 45 | 72 | 565 | 0.502 | 0.14274 | 6.78 | 7.006 |  | 45 | 72 | 1.066 |  | 45 | 72 | 0.938 | 0.80 | 15 | 0.796 |  | 1.047, 1.009, 0.962, 0.925, 1.085,
| 45 | 69 | 580 | 0.491 | 0.13961 | 6.96 | 7.1629 |  | 45 | 69 | 1.094 |  | 45 | 69 | 0.918 | 0.70 | 15 | 0.715 |  | 1.009, 1.047, 1.038, 0.972, 0.887 )
| 45 | 66 | 545 | 0.452 | 0.12852 | 6.54 | 7.781 |  | 45 | 66 | 1.028 |  | 45 | 66 | 0.845 | 0.60 | 15 | 0.640 |  | ..
| 45 | 63 | 555 | 0.445 | 0.12653 | 6.66 | 7.9034 |  | 45 | 63 | 1.047 |  | 45 | 63 | 0.832 | 0.50 | 15 | 0.562 |  | "Constant Speed-EIR-fCHWT&ECT" = CURVE-FIT
| 45 | 60 | 535 | 0.425 | 0.12084 | 6.42 | 8.2753 |  | 45 | 60 | 1.009 |  | 45 | 60 | 0.794 | 0.40 | 15 | 0.488 |  | TYPE = BI-QUADRATIC-T
| 45 | 57 | 510 | 0.41 | 0.11658 | 6.12 | 8.578 |  | 45 | 57 | 0.962 |  | 45 | 57 | 0.766 | 0.30 | 15 | 0.417 |  | INPUT-TYPE = DATA
| 45 | 55 | 490 | 0.399 | 0.11345 | 5.88 | 8.8145 |  | 45 | 55 | 0.925 |  | 45 | 55 | 0.746 | 0.20 | 15 | 0.349 |  | INDEPENDENT-1 = ( 42, 42, 42, 42, 42, 42, 45, 45, 45, 45,
| 48 | 75 | 575 | 0.495 | 0.14074 | 6.9 | 7.105 |  | 48 | 75 | 1.085 |  | 48 | 75 | 0.925 | 0.10 | 15 | 0.268 |  | 45, 45, 45, 45, 48, 48, 48, 48, 48, 48 )
| 48 | 71 | 535 | 0.464 | 0.13193 | 6.42 | 7.5797 |  | 48 | 71 | 1.009 |  | 48 | 71 | 0.867 | 1.00 | 7 | 1.000 | Pwr ratio should be relative to Pwr at PLR=1 for this dT! | INDEPENDENT-2 = ( 75, 71, 67, 63, 59, 55, 75, 72, 69, 66,
| 48 | 67 | 555 | 0.446 | 0.12681 | 6.66 | 7.8856 |  | 48 | 67 | 1.047 |  | 48 | 67 | 0.834 |  |  |  |  | 63, 60, 57, 55, 75, 71, 67, 63, 59, 55 )
| 48 | 63 | 550 | 0.425 | 0.12084 | 6.6 | 8.2753 |  | 48 | 63 | 1.038 |  | 48 | 63 | 0.794 |  |  |  |  | DEPENDENT = ( 1.000, 0.972, 0.936, 0.880, 0.822,
| 48 | 59 | 515 | 0.404 | 0.11487 | 6.18 | 8.7054 |  | 48 | 59 | 0.972 |  | 48 | 59 | 0.755 |  |  |  |  | 0.776, 0.964, 0.938, 0.918, 0.845,
| 48 | 55 | 470 | 0.388 | 0.11032 | 5.64 | 9.0644 |  | 48 | 55 | 0.887 |  | 48 | 55 | 0.725 |  |  |  |  | 0.832, 0.794, 0.766, 0.746, 0.925,
|  |  | *Note to Chiller Manufacturer's Rep., Please allow program to size | [16 empty] | 0.867, 0.834, 0.794, 0.755, 0.725 )
|  |  | (don't input kW into your program) | [16 empty] | ..
"Constant Speed-EIR-fPLR&dT" = CURVE-FIT
|  |  | Part Load Ratio | [16 empty] | TYPE = BI-QUADRATIC-RATIO&DT
% Hourly Capacity (PLR) |  |  | Qchiller (tons) | PwrPLR (kW) | [15 empty] | INPUT-TYPE = DATA
100% | 42 | 75 | 530 | 283.55 | PwrOp | [14 empty] | INDEPENDENT-1 = ( 1.00, 0.80, 0.60, 0.40, 0.15
80% | 42 | 75 | 424 | 217.936 | [5 empty] | CAPFT = ( CapOp / CapNom ) | [9 empty] | 1.00, 0.90, 0.80, 0.70, 0.60,
60% | 42 | 75 | 318 | 181.578 | [5 empty] | EIRFT = EIRop / EIRnom | [9 empty] | 0.50, 0.40, 0.30, 0.20, 0.10,
40% | 42 | 75 | 212 | 143.736 | [5 empty] | PLR = Current chiller load/Max capacity with equal CHWS & ECT temperatures (Given to Manufacturer) | [9 empty] | 1.00 )
15% | 42 | 75 | 79.5 | 86.973 | [5 empty] | EIRfPLR = PwrPLR / PwrOp | [9 empty] | INDEPENDENT-2 = ( 33, 33, 33, 33, 33
100% | 45 | 60 | 535 | 227.375 | PwrOp |  |  |  |  | CapNom: | 530 | tons | [7 empty] | 15, 15, 15, 15, 15,
90% | 45 | 60 | 481.5 | 200.304 | [5 empty] | EIRnom: | 0.15212 | [8 empty] | 15, 15, 15, 15, 15,
80% | 45 | 60 | 428 | 181.044 |  |  |  |  | CapOp: | Chiller capacity at specified temperature conditions | [9 empty] | 7 )
70% | 45 | 60 | 374.5 | 162.533 |  |  |  |  | CapNom: | Reference capacity, which can be selected based on either design capacity or ARI-rated capacity, but must be equal to the nominal capcity defined for the chiller | [9 empty] | DEPENDENT = ( 1.000, 0.769, 0.640, 0.507, 0.307,
60% | 45 | 60 | 321 | 145.413 | [15 empty] | 1.000, 0.881, 0.796, 0.715, 0.640,
50% | 45 | 60 | 267.5 | 127.865 | [15 empty] | 0.562, 0.488, 0.417, 0.349, 0.268,
40% | 45 | 60 | 214 | 111.066 | [15 empty] | 1.000 )
30% | 45 | 60 | 160.5 | 94.8555 | [15 empty] | ..
20% | 45 | 60 | 107 | 79.394
10% | 45 | 60 | 53.5 | 60.883
100% | 48 | 55 | 470 | 182.36 | PwrOp
70% | 48 | 55 | 329 | Head pressure too low.
50% | 48 | 55 | 235 | Head pressure too low.
30% | 48 | 55 | 141 | Head pressure too low.
10% | 48 | 55 | 47 | Head pressure too low.
*Note to Chiller Manufacturer's Rep., Please allow program to size
(don't input capacity and kW into your program)