## Humidity calculations
C:\Users\plapierre\Desktop\ICM\2016-229-61-SIM-PREL-PROP-R00 - Baseline Design
Simulated: 2017-Jun-27 08:51:55
CSV Written: 2017-Jun-27 08:51:55
eQUEST 3.65.7163
[10 empty] | GLOBAL |  | SYSTEM
|  |  | Day | Var 17 | Var 18 | Var 19 |  | Var 39 |  | Var 4 | Var 10 | Var 4 | Var 127 |  | Var 11 | Var 28 | Var 35 | Var 36
Month | Day | Hour | Type | Total system supply air flow rate (cfm) | Total system hot supply air flow rate (cfm) | Total system cold supply air flow rate (cfm) |  | Ratio of outside air to total supply air | Outside air | Outside dry-bulb temp (F) | Humidity ratio (lb H20/lb air) | Return air temp on downstream side of ret fan and plenums (deg F) | Air stream temperature rise across the return fan (Deg F) | Return air temp for humidity check | Humidification heat output (Btu/hr) | CONS(2) | Return air humidity ratio (lb H20/lb dry air) | Mix air humidity ratio (lb H20/lb dry air) | Mix air humidity (calculated by eQUEST) | Error vs eQUEST | Mix air humidity (real value) | Error vs eQUEST
1 | 1 | 1 | 7 | 111321 | 52651.7 | 58668.9 |  | 0.61361 | 35999.9997 | 44 | 0.0057 | 73.8576 | 2.6307 | 71.2269 | 0 | 5454.78 | 0.0061296 | 0.005866 | 0.005866 | 0.0001091% | 0.0059906 | 2.125%
1 | 1 | 2 | 7 | 111309 | 50620.8 | 60688 |  | 0.5932 | 36000.0002 | 47 | 0.0059 | 73.0824 | 2.9984 | 70.084 | 0 | 4735.37 | 0.0063948 | 0.0061013 | 0.0061013 | -4.956e-06% | 0.0062348 | 2.188%
1 | 1 | 3 | 7 | 111309 | 50546.9 | 60761.8 |  | 0.59248 | 36000.0297 | 49 | 0.0064 | 73.3089 | 3.0069 | 70.302 | 0 | 4720 | 0.0068964 | 0.0066023 | 0.0066023 | 9.31e-05% | 0.0067359 | 2.023%
1 | 1 | 4 | 7 | 111309 | 50474.4 | 60834.5 |  | 0.59177 | 35999.9712 | 49 | 0.0064 | 73.3477 | 3.0116 | 70.3361 | 0 | 4708.36 | 0.0068976 | 0.0066032 | 0.0066032 | -5.82e-05% | 0.0067367 | 2.022%
1 | 1 | 5 | 7 | 111309 | 50584.9 | 60724.1 |  | 0.59284 | 35999.9791 | 49 | 0.0064 | 73.3463 | 3.0118 | 70.3345 | 0 | 4707.99 | 0.0068977 | 0.0066026 | 0.0066026 | -4.586e-05% | 0.0067367 | 2.031%
1 | 1 | 6 | 7 | 111309 | 50730.2 | 60578.9 |  | 0.59427 | 36000.0412 | 48 | 0.0067 | 73.3172 | 3.0118 | 70.3054 | 0 | 4708.13 | 0.0071977 | 0.0069019 | 0.0069019 | 7.533e-05% | 0.0070367 | 1.953%
1 | 1 | 7 | 7 | 111309 | 55302.8 | 56005.7 |  | 0.64279 | 36000.0159 | 46 | 0.0052 | 73.757 | 3.0093 | 70.7477 | 0 | 4709.42 | 0.005697 | 0.0053775 | 0.0053775 | -3.556e-05% | 0.0055362 | 2.951%
1 | 1 | 8 | 7 | 111327 | 61940.2 | 49387.2 | #REF! | 0.72893 | 36000.0092 | 43 | 0.0032 | 74.8892 | 2.993 | 71.8962 | -724834 | 4747.38 | 0.0055287 | 0.0038312 | 0.0038312 | -0.0001759% | 0.0047756 | 24.65%
1 | 1 | 9 | 7 | 111327 | 60483.9 | 50843.6 | #REF! | 0.70805 | 36000.0144 | 41 | 0.0033 | 75.6604 | 2.9825 | 72.6779 | -723227 | 4777.45 | 0.0056744 | 0.0039932 | 0.0039932 | 9.173e-05% | 0.0049066 | 22.87%
1 | 1 | 10 | 7 | 111327 | 59444.2 | 51883.3 | #REF! | 0.69387 | 36000.0578 | 42 | 0.0035 | 75.8523 | 2.9821 | 72.8702 | -646822 | 4776.74 | 0.0057108 | 0.0041768 | 0.0041768 | 5.536e-06% | 0.0049959 | 19.61%
1 | 1 | 11 | 7 | 111327 | 58329 | 52998.5 | #REF! | 0.67927 | 36000.0261 | 43 | 0.0032 | 76.0327 | 2.9866 | 73.0461 | -751811 | 4768 | 0.0057453 | 0.0040164 | 0.0040164 | 1.889e-05% | 0.0049222 | 22.55%
1 | 1 | 12 | 7 | 111327 | 57711.2 | 53616.2 | #REF! | 0.67144 | 36000.0077 | 42 | 0.0032 | 76.1497 | 2.9912 | 73.1585 | -750276 | 4761.93 | 0.0057681 | 0.0040438 | 0.0040438 | -0.0001465% | 0.0049377 | 22.1%
1 | 1 | 13 | 7 | 111327 | 58894.9 | 52432.5 | #REF! | 0.6866 | 35999.9972 | 42 | 0.0032 | 76.0995 | 2.9902 | 73.1093 | -763858 | 4763.36 | 0.0057583 | 0.0040018 | 0.0040018 | 5.07e-05% | 0.004931 | 23.22%
1 | 1 | 14 | 7 | 111327 | 58823.2 | 52504.3 | #REF! | 0.68566 | 35999.9933 | 41 | 0.003 | 76.0007 | 2.9784 | 73.0223 | -826702 | 4782.65 | 0.0057196 | 0.0038549 | 0.0038549 | 5.005e-05% | 0.0048401 | 25.56%
1 | 1 | 15 | 7 | 111327 | 57836.5 | 53491 | #REF! | 0.67301 | 36000.0314 | 40 | 0.003 | 76.0314 | 2.9758 | 73.0556 | -814780 | 4788.13 | 0.0057255 | 0.0038912 | 0.0038912 | 4.109e-05% | 0.0048442 | 24.49%
1 | 1 | 16 | 7 | 111327 | 54868.9 | 56458.5 | #REF! | 0.63764 | 35999.9721 | 37 | 0.0025 | 76.2032 | 2.9749 | 73.2283 | -957148 | 4789.16 | 0.005759 | 0.0036809 | 0.0036809 | 1.772e-05% | 0.0047051 | 27.82%
1 | 1 | 17 | 7 | 111327 | 53421.8 | 57905.7 | #REF! | 0.6217 | 36000.0316 | 35 | 0.0021 | 76.4045 | 2.9632 | 73.4413 | -1080500 | 4809.88 | 0.0057786 | 0.0034916 | 0.0034916 | -0.0001193% | 0.0045891 | 31.43%
1 | 1 | 18 | 7 | 111327 | 52582.1 | 58745.4 | #REF! | 0.61281 | 36000.0036 | 34 | 0.0022 | 76.5241 | 2.9617 | 73.5624 | -1040400 | 4814.04 | 0.0058019 | 0.0035946 | 0.0035946 | 0.0001012% | 0.0046371 | 29%
1 | 1 | 19 | 7 | 111327 | 50745.4 | 60582.1 | #REF! | 0.59423 | 36000.0042 | 32 | 0.0022 | 76.6544 | 2.9512 | 73.7031 | -1018820 | 4830.16 | 0.0058076 | 0.0036638 | 0.0036638 | 4.322e-05% | 0.004641 | 26.67%
1 | 1 | 20 | 7 | 111327 | 49378.3 | 61949.1 | #REF! | 0.58112 | 35999.9849 | 30 | 0.0022 | 76.808 | 2.9501 | 73.858 | -1026190 | 4831.53 | 0.0058373 | 0.0037236 | 0.0037236 | 0.0001765% | 0.0046611 | 25.18%
1 | 1 | 21 | 7 | 111327 | 48569.7 | 62757.7 | #REF! | 0.57363 | 35999.9505 | 29 | 0.0018 | 76.8971 | 2.9387 | 73.9584 | -1144070 | 4849.68 | 0.0058349 | 0.0035203 | 0.0035203 | -0.0001237% | 0.0045301 | 28.68%
1 | 1 | 22 | 7 | 111327 | 45450.7 | 65876.8 | #REF! | 0.54648 | 36000.0243 | 24 | 0.0012 | 77.0801 | 2.9382 | 74.1419 | -1285770 | 4852.3 | 0.0058706 | 0.0033183 | 0.0033183 | -0.0001042% | 0.0043603 | 31.4%
1 | 1 | 23 | 7 | 111327 | 45835.2 | 65492.2 | #REF! | 0.54968 | 36000.0145 | 21 | 0.0011 | 77.1879 | 2.9242 | 74.2637 | -1332330 | 4877.31 | 0.0058724 | 0.0032491 | 0.0032491 | -0.0001366% | 0.0043291 | 33.24%
1 | 1 | 24 | 7 | 111327 | 46137.8 | 65189.7 | #REF! | 0.55224 | 36000.034 | 19 | 0.0011 | 77.1488 | 2.9183 | 74.2305 | -1339300 | 4887.79 | 0.0058646 | 0.0032334 | 0.0032334 | 0.0001408% | 0.0043239 | 33.72%
1 | 2 | 1 | 8 | 111315 | 42489.2 | 68825.8 | #REF! | 0.52306 | 36000.0229 | 18 | 0.001 | 76.4999 | 2.9142 | 73.5857 | -1263010 | 4895.4 | 0.005739 | 0.0032602 | 0.0032602 | -6.939e-05% | 0.0042064 | 29.02%
1 | 2 | 2 | 8 | 111309 | 41729.6 | 69579.2 | #REF! | 0.5174 | 35999.9998 | 17 | 0.001 | 75.9396 | 2.9059 | 73.0337 | -1216150 | 4909.35 | 0.005613 | 0.0032262 | 0.0032262 | -5.822e-05% | 0.004121 | 27.73%
1 | 2 | 3 | 8 | 111309 | 42019.8 | 69289 |  | 0.51956 | 36000.0007 | 17 | 0.001 | 75.9844 | 2.903 | 73.0814 | -1225160 | 4914.61 | 0.0056213 | 0.0032202 | 0.0032202 | 0.0001089% | 0.0041267 | 28.15%
1 | 2 | 4 | 8 | 111309 | 42001 | 69307.8 |  | 0.51942 | 35999.9961 | 17 | 0.001 | 75.9575 | 2.9027 | 73.0548 | -1223500 | 4915.14 | 0.0056163 | 0.0032185 | 0.0032185 | -8.03e-05% | 0.0041233 | 28.11%
1 | 2 | 5 | 8 | 111309 | 42064.4 | 69244.4 |  | 0.5199 | 36000.0251 | 16 | 0.0009 | 75.9555 | 2.9026 | 73.0529 | -1254130 | 4915.29 | 0.0056159 | 0.0031641 | 0.0031641 | -6.881e-05% | 0.0040907 | 29.28%
1 | 2 | 6 | 8 | 111309 | 42140.5 | 69168.2 |  | 0.52047 | 35999.9731 | 16 | 0.0009 | 75.9397 | 2.9008 | 73.0389 | -1255660 | 4918.88 | 0.005613 | 0.00316 | 0.00316 | 1.595e-05% | 0.0040887 | 29.39%
1 | 2 | 7 | 8 | 111325 | 43820.1 | 67504.9 |  | 0.53329 | 36000.0256 | 16 | 0.001 | 76.1871 | 2.8906 | 73.2965 | -1271410 | 4935.49 | 0.0056412 | 0.0031661 | 0.0031661 | -0.0001501% | 0.0041404 | 30.77%
1 | 2 | 8 | 8 | 111327 | 46015 | 65312.4 |  | 0.5512 | 35999.9989 | 16 | 0.001 | 76.7965 | 2.8888 | 73.9077 | -1333110 | 4938.38 | 0.0057576 | 0.0031352 | 0.0031352 | 5.386e-05% | 0.0042191 | 34.57%
1 | 2 | 9 | 8 | 111327 | 45961.7 | 65365.8 |  | 0.55075 | 36000.0183 | 17 | 0.001 | 77.1682 | 2.8876 | 74.2806 | -1348240 | 4940.81 | 0.0058295 | 0.0031697 | 0.0031697 | 9.058e-05% | 0.0042678 | 34.64%
1 | 2 | 10 | 8 | 111327 | 44659.3 | 66668.1 |  | 0.53999 | 35999.974 | 16 | 0.0009 | 77.2816 | 2.8909 | 74.3907 | -1357270 | 4934.87 | 0.0058518 | 0.0031779 | 0.0031779 | 0.000114% | 0.0042505 | 33.75%
1 | 2 | 11 | 8 | 111327 | 44015.5 | 67312 |  | 0.53482 | 36000.0058 | 17 | 0.0011 | 77.4097 | 2.8916 | 74.5181 | -1286210 | 4933.51 | 0.005877 | 0.0033221 | 0.0033221 | 5.785e-05% | 0.0043322 | 30.41%
1 | 2 | 12 | 8 | 111327 | 43976.3 | 67351.2 |  | 0.53451 | 36000.0246 | 18 | 0.0011 | 77.4665 | 2.9044 | 74.5621 | -1287960 | 4910.47 | 0.0059077 | 0.0033379 | 0.0033379 | 0.0001581% | 0.0043531 | 30.41%
1 | 2 | 13 | 8 | 111327 | 43539.9 | 67787.5 |  | 0.53107 | 35999.9754 | 18 | 0.0011 | 77.4965 | 2.9067 | 74.5898 | -1280260 | 4906.48 | 0.0059137 | 0.0033573 | 0.0033573 | 0.0001421% | 0.0043571 | 29.78%
1 | 2 | 14 | 8 | 111327 | 44450.9 | 66876.6 |  | 0.53831 | 36000.0082 | 18 | 0.0012 | 77.4793 | 2.9171 | 74.5622 | -1267490 | 4888.77 | 0.00593 | 0.0033838 | 0.0033838 | -0.000101% | 0.0044005 | 30.04%
1 | 2 | 15 | 8 | 111327 | 44907 | 66420.5 |  | 0.542 | 36000.0438 | 17 | 0.0012 | 77.3955 | 2.9158 | 74.4797 | -1271790 | 4890.78 | 0.0059134 | 0.0033588 | 0.0033587 | -0.0001163% | 0.0043892 | 30.68%
1 | 2 | 16 | 8 | 111327 | 45217.6 | 66109.9 |  | 0.54455 | 36000.0138 | 19 | 0.0014 | 77.3456 | 2.9129 | 74.4327 | -1215700 | 4895.85 | 0.0059035 | 0.0034512 | 0.0034512 | 2.476e-05% | 0.0044472 | 28.86%
1 | 2 | 17 | 8 | 111327 | 45192.4 | 66135 |  | 0.54434 | 35999.992 | 19 | 0.0013 | 77.3259 | 2.9158 | 74.4101 | -1242700 | 4890.13 | 0.0058997 | 0.0033959 | 0.0033959 | 3.041e-05% | 0.0044123 | 29.93%
1 | 2 | 18 | 8 | 111327 | 45165.4 | 66162 |  | 0.54412 | 36000.0013 | 20 | 0.0014 | 77.326 | 2.9159 | 74.4101 | -1212100 | 4890.55 | 0.0058997 | 0.0034513 | 0.0034513 | -4.004e-05% | 0.0044446 | 28.78%
1 | 2 | 19 | 8 | 111327 | 45097.7 | 66229.8 |  | 0.54356 | 36000.0025 | 21 | 0.0014 | 77.3422 | 2.9274 | 74.4148 | -1217120 | 4870.75 | 0.0059227 | 0.0034643 | 0.0034643 | -6.991e-05% | 0.0044602 | 28.75%
1 | 2 | 20 | 8 | 111327 | 45517.9 | 65809.5 |  | 0.54703 | 35999.9682 | 21 | 0.0015 | 77.3155 | 2.9296 | 74.3859 | -1214950 | 4867.01 | 0.0059174 | 0.0035009 | 0.0035009 | -7.522e-05% | 0.0044889 | 28.22%
1 | 2 | 21 | 8 | 111327 | 45424 | 65903.5 |  | 0.54625 | 36000.0505 | 22 | 0.0017 | 77.2924 | 2.9289 | 74.3635 | -1148900 | 4867.91 | 0.0059128 | 0.0036115 | 0.0036115 | -0.0001194% | 0.0045505 | 26%
1 | 2 | 22 | 8 | 111327 | 45205.5 | 66122 |  | 0.54445 | 35999.9907 | 23 | 0.0019 | 77.3238 | 2.9405 | 74.3833 | -1086610 | 4847.72 | 0.005939 | 0.00374 | 0.00374 | 0.0001686% | 0.0046329 | 23.88%
1 | 2 | 23 | 8 | 111327 | 45159.1 | 66168.3 |  | 0.54407 | 35999.9885 | 23 | 0.0022 | 77.3388 | 2.9429 | 74.3959 | -993952 | 4842.66 | 0.0059419 | 0.0039061 | 0.0039061 | -3.867e-05% | 0.0047319 | 21.14%
1 | 2 | 24 | 8 | 111327 | 46561.8 | 64765.7 |  | 0.55585 | 36000.0143 | 27 | 0.0027 | 77.2815 | 2.9429 | 74.3386 | -855756 | 4841.12 | 0.0059305 | 0.0041348 | 0.0041348 | -0.0001098% | 0.0048859 | 18.16%
1 | 3 | 1 | 2 | 111234 | 42290.3 | 68943.8 |  | 0.52216 | 36000.0393 | 27 | 0.0027 | 76.6353 | 2.9604 | 73.6749 | -766897 | 4814.57 | 0.0058234 | 0.0041925 | 0.0041925 | 8.899e-05% | 0.0048126 | 14.79%
1 | 3 | 2 | 2 | 111309 | 43062.5 | 68246.4 |  | 0.5275 | 36000.0442 | 30 | 0.0027 | 75.9178 | 2.9616 | 72.9562 | -733409 | 4808.9 | 0.0056846 | 0.0041102 | 0.0041102 | 0.0001141% | 0.0047193 | 14.82%
1 | 3 | 3 | 2 | 111309 | 43588 | 67720.9 |  | 0.53159 | 36000.0241 | 31 | 0.0027 | 75.7353 | 2.9634 | 72.7719 | -728498 | 4806.6 | 0.0056502 | 0.0040819 | 0.0040819 | 1.836e-05% | 0.004696 | 15.05%
1 | 3 | 4 | 2 | 111309 | 44087.4 | 67221.4 |  | 0.53554 | 35999.9502 | 32 | 0.0029 | 75.6016 | 2.9739 | 72.6277 | -669629 | 4789.89 | 0.0056441 | 0.0041745 | 0.0041745 | 7.74e-05% | 0.0047566 | 13.94%
1 | 3 | 5 | 2 | 111309 | 44596.1 | 66712.7 |  | 0.53963 | 35999.9742 | 33 | 0.0033 | 75.4538 | 2.9747 | 72.4791 | -546374 | 4787.8 | 0.0056161 | 0.0043663 | 0.0043663 | -2.169e-06% | 0.004867 | 11.47%
1 | 3 | 6 | 2 | 114217 | 44482.8 | 69734 |  | 0.51625 | 36000.038 | 33 | 0.0033 | 75.3765 | 2.8996 | 72.4769 | -527312 | 4785.19 | 0.0056015 | 0.0044133 | 0.0044134 | 8.848e-06% | 0.0048761 | 10.48%
1 | 3 | 7 | 2 | 116268 | 48429.3 | 67838.2 |  | 0.53067 | 35999.9689 | 33 | 0.0035 | 75.5436 | 2.8512 | 72.6924 | -502725 | 4780.14 | 0.0056331 | 0.0045011 | 0.0045011 | -1.576e-05% | 0.0049726 | 10.48%
1 | 3 | 8 | 2 | 116442 | 52552.7 | 63889.3 |  | 0.56347 | 36000.0233 | 33 | 0.0038 | 76.2785 | 2.8552 | 73.4233 | -484084 | 4765.52 | 0.0057933 | 0.0046701 | 0.0046701 | 1.964e-05% | 0.005177 | 10.85%
1 | 3 | 9 | 2 | 116277 | 53124.3 | 63152.8 |  | 0.57005 | 36000.001 | 33 | 0.0038 | 76.6262 | 2.8575 | 73.7687 | -511328 | 4766.88 | 0.0058613 | 0.0046862 | 0.0046862 | 5.724e-05% | 0.0052231 | 11.46%
1 | 3 | 10 | 2 | 116243 | 53788.4 | 62454.5 |  | 0.57642 | 35999.9604 | 34 | 0.0041 | 76.5705 | 2.8587 | 73.7118 | -408836 | 4766.18 | 0.0058504 | 0.0048414 | 0.0048414 | -4.728e-05% | 0.0053083 | 9.643%
1 | 3 | 11 | 2 | 116140 | 54451.6 | 61688.8 |  | 0.58357 | 35999.9798 | 35 | 0.0038 | 76.5188 | 2.862 | 73.6568 | -509050 | 4763.61 | 0.0058403 | 0.0046496 | 0.0046496 | -5.784e-05% | 0.0052078 | 12.01%
1 | 3 | 12 | 2 | 116883 | 58584.8 | 58298.4 |  | 0.61751 | 36000.0199 | 38 | 0.004 | 76.3003 | 2.8543 | 73.446 | -467438 | 4747.69 | 0.0058173 | 0.0046951 | 0.0046951 | 2.715e-05% | 0.0052576 | 11.98%
1 | 3 | 13 | 2 | 116275 | 57254.9 | 59019.8 |  | 0.60996 | 36000.0123 | 38 | 0.0038 | 76.2005 | 2.8703 | 73.3302 | -515363 | 4745.55 | 0.0057977 | 0.0045792 | 0.0045792 | 5.288e-05% | 0.0051792 | 13.1%
1 | 3 | 14 | 2 | 116270 | 56461 | 59808.9 |  | 0.60192 | 36000.0535 | 37 | 0.003 | 76.2834 | 2.8711 | 73.4123 | -795058 | 4745.5 | 0.005814 | 0.0041202 | 0.0041202 | 6.67e-05% | 0.0049427 | 19.96%
1 | 3 | 15 | 2 | 115622 | 54325.5 | 61296.1 |  | 0.58731 | 35999.9964 | 36 | 0.0033 | 76.4187 | 2.8867 | 73.532 | -673330 | 4750.19 | 0.0058405 | 0.0043485 | 0.0043485 | 4.502e-05% | 0.0050495 | 16.12%
1 | 3 | 16 | 2 | 116284 | 55894.9 | 60388.7 |  | 0.59614 | 35999.9988 | 36 | 0.0029 | 76.4122 | 2.8608 | 73.5514 | -814363 | 4763.98 | 0.0058194 | 0.004079 | 0.004079 | 6.864e-05% | 0.0049156 | 20.51%
1 | 3 | 17 | 2 | 116394 | 56315 | 60079.2 |  | 0.59921 | 35999.9974 | 36 | 0.0029 | 76.338 | 2.857 | 73.481 | -818873 | 4768.08 | 0.0058049 | 0.0040643 | 0.0040643 | -4.93e-06% | 0.0049065 | 20.72%
1 | 3 | 18 | 2 | 116279 | 55413.3 | 60865.8 |  | 0.59147 | 35999.9904 | 35 | 0.0029 | 76.3645 | 2.8592 | 73.5053 | -818693 | 4769.29 | 0.0058101 | 0.0040889 | 0.0040889 | -5.616e-05% | 0.0049091 | 20.06%
1 | 3 | 19 | 2 | 116035 | 54205.3 | 61829.7 |  | 0.58225 | 36000.0337 | 34 | 0.0032 | 76.4548 | 2.8643 | 73.5905 | -710500 | 4770.58 | 0.0058277 | 0.0042978 | 0.0042978 | -0.0001% | 0.0050125 | 16.63%
1 | 3 | 20 | 2 | 115743 | 52867.3 | 62875.8 |  | 0.57256 | 36000.0423 | 33 | 0.0029 | 76.5485 | 2.8613 | 73.6872 | -793050 | 4785.76 | 0.0058263 | 0.0041508 | 0.0041508 | 1.69e-05% | 0.0049161 | 18.44%
1 | 3 | 21 | 2 | 111309 | 50941.2 | 60367.3 |  | 0.59635 | 35999.979 | 33 | 0.0025 | 76.6845 | 2.975 | 73.7095 | -929025 | 4787.53 | 0.0058528 | 0.0038534 | 0.0038533 | -0.0001317% | 0.0047684 | 23.75%
1 | 3 | 22 | 2 | 111309 | 49735.3 | 61574 |  | 0.58466 | 36000.0396 | 31 | 0.0019 | 76.7682 | 2.9723 | 73.7959 | -1130970 | 4794.42 | 0.0058691 | 0.0035485 | 0.0035485 | -0.0001189% | 0.0045854 | 29.22%
1 | 3 | 23 | 2 | 111320 | 44940.1 | 66379.7 |  | 0.54233 | 35999.9682 | 25 | 0.0017 | 77.0646 | 2.9602 | 74.1043 | -1126720 | 4816.21 | 0.0059072 | 0.0036255 | 0.0036255 | 0.0002157% | 0.0045466 | 25.41%
1 | 3 | 24 | 2 | 111327 | 45433.4 | 65894.1 |  | 0.54633 | 36000.0554 | 21 | 0.0013 | 77.246 | 2.9463 | 74.2997 | -1266780 | 4838.03 | 0.0059235 | 0.0033975 | 0.0033975 | -0.0001221% | 0.0044284 | 30.34%
1 | 4 | 1 | 3 | 111172 | 42186.2 | 68986 |  | 0.52185 | 35999.9992 | 18 | 0.0011 | 76.5777 | 2.9331 | 73.6446 | -1231460 | 4868.54 | 0.0057733 | 0.0033345 | 0.0033346 | 6.593e-05% | 0.00426 | 27.75%
1 | 4 | 2 | 3 | 111232 | 41643.6 | 69588.1 |  | 0.51733 | 36000.0118 | 16 | 0.001 | 75.9896 | 2.9279 | 73.0617 | -1219410 | 4875.12 | 0.00566 | 0.0032492 | 0.0032492 | 8.904e-05% | 0.0041518 | 27.78%
1 | 4 | 3 | 3 | 111263 | 41989.9 | 69273.1 |  | 0.51968 | 36000.0524 | 15 | 0.0009 | 75.9917 | 2.9125 | 73.0792 | -1256380 | 4900.35 | 0.0056414 | 0.0031774 | 0.0031774 | -1.784e-05% | 0.0041073 | 29.27%
1 | 4 | 4 | 3 | 111284 | 42077.8 | 69206 |  | 0.52019 | 35999.9923 | 15 | 0.0009 | 75.9447 | 2.9096 | 73.0351 | -1256580 | 4905.02 | 0.0056327 | 0.0031708 | 0.0031708 | 4.174e-05% | 0.0041017 | 29.36%
1 | 4 | 5 | 3 | 111296 | 42125.6 | 69170.2 |  | 0.52046 | 35999.9764 | 15 | 0.0009 | 75.9222 | 2.8993 | 73.0229 | -1255360 | 4921.85 | 0.0056097 | 0.0031585 | 0.0031585 | 0.0002366% | 0.0040863 | 29.37%
1 | 4 | 6 | 3 | 114062 | 42055.2 | 72006.6 |  | 0.49995 | 35999.9877 | 14 | 0.0008 | 75.8913 | 2.8288 | 73.0625 | -1254440 | 4922.43 | 0.005604 | 0.0032022 | 0.0032022 | -0.0001255% | 0.0040878 | 27.65%
1 | 4 | 7 | 3 | 115560 | 44661.7 | 70898.6 |  | 0.50777 | 35999.9694 | 14 | 0.0009 | 76.0164 | 2.7942 | 73.2222 | -1273230 | 4918.24 | 0.0056273 | 0.003227 | 0.0032269 | -6.731e-05% | 0.0041546 | 28.75%
1 | 4 | 8 | 3 | 115597 | 47212 | 68384.8 |  | 0.52643 | 36000.0154 | 14 | 0.0009 | 76.6213 | 2.7923 | 73.829 | -1349980 | 4919.85 | 0.0057432 | 0.0031936 | 0.0031936 | -0.0001413% | 0.0042349 | 32.61%
1 | 4 | 9 | 3 | 114891 | 45677.2 | 69213.7 |  | 0.52013 | 35999.9834 | 15 | 0.001 | 76.9963 | 2.808 | 74.1883 | -1317880 | 4922.67 | 0.005815 | 0.0033106 | 0.0033106 | 0.0002439% | 0.0043063 | 30.08%
1 | 4 | 10 | 3 | 115147 | 43879.7 | 71266.8 |  | 0.50514 | 35999.9964 | 16 | 0.001 | 77.1022 | 2.7968 | 74.3054 | -1272210 | 4930.37 | 0.0058165 | 0.0033835 | 0.0033835 | -3.332e-05% | 0.0043107 | 27.4%
1 | 4 | 11 | 3 | 115497 | 42774.3 | 72722.8 |  | 0.49503 | 35999.9677 | 17 | 0.0012 | 77.2161 | 2.8024 | 74.4137 | -1197960 | 4904.95 | 0.0058584 | 0.0035523 | 0.0035523 | 5.769e-05% | 0.0044064 | 24.04%
1 | 4 | 12 | 3 | 115745 | 42266.5 | 73478.9 |  | 0.48994 | 35999.9584 | 19 | 0.0011 | 77.257 | 2.8005 | 74.4565 | -1229200 | 4896.29 | 0.0058664 | 0.0035312 | 0.0035312 | 0.0001232% | 0.0043839 | 24.15%
1 | 4 | 13 | 3 | 115871 | 41367.2 | 74503.3 |  | 0.4832 | 35999.9946 | 20 | 0.0011 | 77.3001 | 2.8018 | 74.4983 | -1201470 | 4888.81 | 0.0058749 | 0.0035677 | 0.0035677 | -3.767e-05% | 0.0043914 | 23.09%
1 | 4 | 14 | 3 | 115760 | 41583.6 | 74176.8 |  | 0.48533 | 36000.0038 | 21 | 0.0011 | 77.3288 | 2.8075 | 74.5213 | -1218250 | 4883.25 | 0.0058806 | 0.0035604 | 0.0035604 | 8.527e-06% | 0.0043939 | 23.41%
1 | 4 | 15 | 3 | 115010 | 42763.6 | 72246.1 |  | 0.4983 | 36000.0149 | 22 | 0.0014 | 77.3082 | 2.8272 | 74.481 | -1142150 | 4880.96 | 0.0058765 | 0.0036459 | 0.0036459 | -0.0001779% | 0.0044753 | 22.75%
1 | 4 | 16 | 3 | 114768 | 43344.4 | 71423.9 |  | 0.50403 | 36000.0026 | 22 | 0.0014 | 77.2612 | 2.8324 | 74.4288 | -1145660 | 4881.55 | 0.0058672 | 0.0036156 | 0.0036156 | -0.0001764% | 0.004466 | 23.52%
1 | 4 | 17 | 3 | 114757 | 44096.8 | 70660.4 |  | 0.50948 | 35999.9899 | 23 | 0.0016 | 77.213 | 2.8409 | 74.3721 | -1103640 | 4867.72 | 0.0058773 | 0.0036981 | 0.0036981 | 1.024e-05% | 0.0045355 | 22.64%
1 | 4 | 18 | 3 | 114776 | 44580.9 | 70195.1 |  | 0.51286 | 35999.9782 | 22 | 0.0015 | 77.1511 | 2.841 | 74.3101 | -1148440 | 4865.96 | 0.0058651 | 0.0036264 | 0.0036264 | -6.452e-05% | 0.0044959 | 23.98%
1 | 4 | 19 | 3 | 114697 | 44632.6 | 70063.9 |  | 0.51382 | 36000.0229 | 23 | 0.0017 | 77.1257 | 2.8405 | 74.2852 | -1090300 | 4870.79 | 0.0058601 | 0.0037225 | 0.0037225 | -0.0001185% | 0.0045543 | 22.34%
1 | 4 | 20 | 3 | 114665 | 44341.3 | 70323.8 |  | 0.51192 | 36000.019 | 25 | 0.0019 | 77.1462 | 2.8521 | 74.2941 | -1023820 | 4851.53 | 0.0058838 | 0.0038444 | 0.0038444 | -9.288e-05% | 0.004633 | 20.51%
1 | 4 | 21 | 3 | 111309 | 43796.1 | 67512.4 |  | 0.53324 | 35999.9746 | 24 | 0.0018 | 77.2751 | 2.942 | 74.3331 | -1064890 | 4843.91 | 0.0059094 | 0.0037181 | 0.0037181 | 2.368e-06% | 0.0045803 | 23.19%
1 | 4 | 22 | 3 | 111319 | 44705.3 | 66614 |  | 0.54043 | 36000.0042 | 23 | 0.0018 | 77.3183 | 2.9369 | 74.3814 | -1105300 | 4852.96 | 0.0059179 | 0.0036925 | 0.0036925 | 0.0001094% | 0.0045862 | 24.2%
1 | 4 | 23 | 3 | 111320 | 44837.9 | 66482 |  | 0.5415 | 36000.003 | 22 | 0.0018 | 77.2883 | 2.9339 | 74.3544 | -1107020 | 4858.11 | 0.005912 | 0.0036853 | 0.0036853 | -7.014e-05% | 0.0045822 | 24.34%
1 | 4 | 24 | 3 | 111327 | 46316.6 | 65010.8 |  | 0.55375 | 35999.9905 | 27 | 0.0023 | 77.2193 | 2.9316 | 74.2877 | -971451 | 4861.79 | 0.0058983 | 0.0039057 | 0.0039057 | -4.975e-05% | 0.0047347 | 21.22%
1 | 5 | 1 | 4 | 111315 | 43678.8 | 67636.6 |  | 0.53226 | 35999.9862 | 30 | 0.0026 | 76.3787 | 2.9387 | 73.44 | -792266 | 4848.6 | 0.0057349 | 0.0040663 | 0.0040663 | 0.0001314% | 0.0047211 | 16.1%
1 | 5 | 2 | 4 | 111309 | 44287.2 | 67021.9 |  | 0.53714 | 36000.0093 | 33 | 0.0027 | 75.4881 | 2.9446 | 72.5435 | -716496 | 4837.77 | 0.0055661 | 0.0040266 | 0.0040266 | -0.0001084% | 0.0046391 | 15.21%
1 | 5 | 3 | 4 | 111309 | 44312.4 | 66996.5 |  | 0.53734 | 35999.9663 | 33 | 0.0028 | 75.3825 | 2.946 | 72.4365 | -680375 | 4835.73 | 0.0055463 | 0.0040706 | 0.0040706 | 0.0001421% | 0.0046581 | 14.43%
1 | 5 | 4 | 4 | 111146 | 40604.5 | 70541 |  | 0.51034 | 35999.9645 | 26 | 0.002 | 75.8524 | 2.9499 | 72.9025 | -898635 | 4836.08 | 0.0056343 | 0.0037795 | 0.0037795 | 8.522e-05% | 0.0044571 | 17.93%
1 | 5 | 5 | 4 | 111260 | 41714.3 | 69545.5 |  | 0.51765 | 36000.0194 | 27 | 0.0023 | 76.2006 | 2.9404 | 73.2602 | -847433 | 4849.27 | 0.0057006 | 0.0039403 | 0.0039403 | -8.949e-07% | 0.0046003 | 16.75%
1 | 5 | 6 | 4 | 114065 | 41496.4 | 72568.8 |  | 0.49608 | 36000.0029 | 27 | 0.0022 | 76.0656 | 2.8603 | 73.2053 | -844280 | 4861.07 | 0.0056556 | 0.0039413 | 0.0039413 | -6.452e-05% | 0.004565 | 15.82%
1 | 5 | 7 | 4 | 115178 | 44345.7 | 70832.1 |  | 0.50824 | 35999.9898 | 28 | 0.0026 | 76.1503 | 2.8354 | 73.3149 | -763887 | 4856.4 | 0.0056719 | 0.0041106 | 0.0041106 | -0.0001074% | 0.0047117 | 14.62%
1 | 5 | 8 | 4 | 115127 | 47028.3 | 68098.4 |  | 0.52865 | 36000.0149 | 28 | 0.0023 | 76.6755 | 2.8367 | 73.8388 | -911945 | 4854.83 | 0.0057728 | 0.0039369 | 0.0039369 | -0.0001347% | 0.0046869 | 19.05%
1 | 5 | 9 | 4 | 114935 | 48855.4 | 66079.1 |  | 0.5448 | 35999.9598 | 30 | 0.0027 | 76.9181 | 2.8404 | 74.0777 | -827829 | 4858.11 | 0.0058194 | 0.00412 | 0.00412 | 3.438e-05% | 0.0048424 | 17.53%
1 | 5 | 10 | 4 | 114695 | 48748.9 | 65946.5 |  | 0.5459 | 35999.9965 | 31 | 0.0028 | 76.8702 | 2.8482 | 74.022 | -783737 | 4853.29 | 0.0058102 | 0.0041669 | 0.0041669 | -1.616e-06% | 0.0048654 | 16.76%
1 | 5 | 11 | 4 | 114653 | 47564.3 | 67088.4 |  | 0.5366 | 35999.9709 | 30 | 0.0028 | 76.9254 | 2.8507 | 74.0747 | -772800 | 4850.39 | 0.0058208 | 0.0041998 | 0.0041998 | 6.867e-05% | 0.0048723 | 16.01%
1 | 5 | 12 | 4 | 114680 | 47659 | 67020.5 |  | 0.53715 | 35999.9946 | 30 | 0.0027 | 76.9618 | 2.8498 | 74.112 | -815440 | 4850.5 | 0.0058278 | 0.0041477 | 0.0041477 | -0.0001298% | 0.0048459 | 16.83%
1 | 5 | 13 | 4 | 114570 | 44397.8 | 70171.8 |  | 0.51303 | 36000.028 | 27 | 0.0022 | 77.0814 | 2.8527 | 74.2288 | -922411 | 4850.82 | 0.0058513 | 0.0039781 | 0.0039781 | -0.0001313% | 0.004704 | 18.25%
1 | 5 | 14 | 4 | 114695 | 43720.1 | 70974.8 |  | 0.50722 | 36000.051 | 26 | 0.0021 | 77.211 | 2.8486 | 74.3624 | -960219 | 4853.96 | 0.0058769 | 0.0039612 | 0.0039612 | 0.0001069% | 0.0046914 | 18.44%
1 | 5 | 15 | 4 | 114648 | 43494.9 | 71152.7 |  | 0.50595 | 35999.9932 | 24 | 0.0019 | 77.2279 | 2.8495 | 74.3784 | -1005970 | 4854.56 | 0.0058803 | 0.0038664 | 0.0038664 | 0.0001674% | 0.0046304 | 19.76%
1 | 5 | 16 | 4 | 114620 | 43873.8 | 70746.6 |  | 0.50886 | 35999.9734 | 24 | 0.0019 | 77.2063 | 2.8471 | 74.3592 | -1007500 | 4860.54 | 0.005876 | 0.0038528 | 0.0038528 | 0.0001474% | 0.0046272 | 20.1%
1 | 5 | 17 | 4 | 114677 | 44373.1 | 70303.5 |  | 0.51207 | 36000.032 | 23 | 0.0018 | 77.1663 | 2.8451 | 74.3212 | -1045760 | 4861.68 | 0.0058681 | 0.003785 | 0.003785 | -1.516e-05% | 0.004591 | 21.3%
1 | 5 | 18 | 4 | 114697 | 44847.3 | 69849.9 |  | 0.51539 | 36000.0098 | 23 | 0.0019 | 77.1201 | 2.8423 | 74.2778 | -1032700 | 4866.29 | 0.0058589 | 0.0038185 | 0.0038185 | -5.357e-05% | 0.0046163 | 20.89%
1 | 5 | 19 | 4 | 114686 | 44925.6 | 69759.9 |  | 0.51606 | 36000.015 | 23 | 0.0016 | 77.097 | 2.8418 | 74.2552 | -1122150 | 4867.36 | 0.0058544 | 0.0036589 | 0.0036589 | -8.649e-05% | 0.0045189 | 23.51%
1 | 5 | 20 | 4 | 114671 | 44887.3 | 69783.4 |  | 0.51588 | 36000 | 22 | 0.0016 | 77.0959 | 2.842 | 74.2539 | -1116130 | 4868.96 | 0.0058542 | 0.0036595 | 0.0036595 | -0.0001249% | 0.0045186 | 23.48%
1 | 5 | 21 | 4 | 111309 | 44321 | 66987.5 |  | 0.53741 | 35999.9533 | 22 | 0.0015 | 77.2141 | 2.9359 | 74.2782 | -1161800 | 4855.7 | 0.0058972 | 0.0035341 | 0.0035341 | 1.94e-05% | 0.0044751 | 26.63%
1 | 5 | 22 | 4 | 111318 | 45108.4 | 66209.4 |  | 0.54373 | 35999.9709 | 22 | 0.0016 | 77.254 | 2.9324 | 74.3216 | -1171820 | 4862.17 | 0.0059052 | 0.0035643 | 0.0035643 | -3.412e-05% | 0.0045129 | 26.61%
1 | 5 | 23 | 4 | 111318 | 45179.4 | 66139.1 |  | 0.54431 | 35999.9751 | 21 | 0.0016 | 77.232 | 2.9313 | 74.3007 | -1172120 | 4863.65 | 0.0059008 | 0.0035598 | 0.0035598 | 0.0001251% | 0.0045099 | 26.69%
1 | 5 | 24 | 4 | 111327 | 45347.5 | 65979.9 |  | 0.54562 | 36000.019 | 20 | 0.0015 | 77.2175 | 2.929 | 74.2885 | -1204280 | 4867.11 | 0.0058979 | 0.0034983 | 0.0034983 | 4.514e-05% | 0.0044758 | 27.94%
1 | 6 | 1 | 5 | 111110 | 41866.5 | 69244 |  | 0.5199 | 36000.0248 | 19 | 0.0016 | 76.623 | 2.9424 | 73.6806 | -1084780 | 4855.04 | 0.0058015 | 0.0036171 | 0.0036171 | -0.000101% | 0.0044402 | 22.75%
1 | 6 | 2 | 5 | 111148 | 41208.3 | 69939.6 |  | 0.51473 | 36000.0103 | 18 | 0.0015 | 76.0823 | 2.9422 | 73.1401 | -1072440 | 4852.71 | 0.0056969 | 0.0035366 | 0.0035366 | -0.0001384% | 0.0043375 | 22.65%
1 | 6 | 3 | 5 | 111161 | 41497.7 | 69663.1 |  | 0.51677 | 36000.0092 | 17 | 0.0014 | 76.1133 | 2.939 | 73.1743 | -1108930 | 4858.09 | 0.0057028 | 0.0034793 | 0.0034793 | 9.476e-05% | 0.0043094 | 23.86%
1 | 6 | 4 | 5 | 111176 | 41616.4 | 69559.7 |  | 0.51754 | 35999.9967 | 16 | 0.0014 | 76.0742 | 2.9464 | 73.1278 | -1110940 | 4845.77 | 0.0057145 | 0.0034816 | 0.0034816 | 0.00011% | 0.0043174 | 24.01%
1 | 6 | 5 | 5 | 111196 | 41696.8 | 69499.3 |  | 0.51799 | 36000.0119 | 16 | 0.0015 | 76.0497 | 2.9439 | 73.1058 | -1082510 | 4849 | 0.0057098 | 0.0035291 | 0.0035291 | 6.256e-05% | 0.0043468 | 23.17%
1 | 6 | 6 | 5 | 113936 | 41559.3 | 72376.7 |  | 0.4974 | 35999.9534 | 16 | 0.0015 | 76.0287 | 2.8825 | 73.1462 | -1057580 | 4832.76 | 0.005725 | 0.0036235 | 0.0036235 | 0.0002132% | 0.0043901 | 21.16%
1 | 6 | 7 | 5 | 115388 | 43910.6 | 71477.6 |  | 0.50365 | 35999.9792 | 16 | 0.0015 | 76.1541 | 2.8501 | 73.304 | -1095400 | 4825.26 | 0.0057494 | 0.0036092 | 0.0036092 | -6.697e-05% | 0.0044236 | 22.57%
1 | 6 | 8 | 5 | 115363 | 46242.9 | 69120.3 |  | 0.52083 | 35999.995 | 17 | 0.0015 | 76.7368 | 2.8501 | 73.8867 | -1160940 | 4826.49 | 0.005863 | 0.0035906 | 0.0035906 | 0.0001443% | 0.0045015 | 25.37%
1 | 6 | 9 | 5 | 114815 | 44821.7 | 69993.6 |  | 0.51433 | 36000.0183 | 18 | 0.0015 | 77.1064 | 2.8643 | 74.2421 | -1162080 | 4825.58 | 0.0059356 | 0.0036542 | 0.0036542 | -6.789e-07% | 0.0045448 | 24.37%
1 | 6 | 10 | 5 | 114925 | 43240.8 | 71684.4 |  | 0.5022 | 36000.049 | 19 | 0.0017 | 77.2286 | 2.8756 | 74.353 | -1073600 | 4801.57 | 0.0059803 | 0.0038307 | 0.0038307 | -8.633e-06% | 0.0046395 | 21.11%
1 | 6 | 11 | 5 | 115156 | 42350.1 | 72805.9 |  | 0.49447 | 36000.0421 | 20 | 0.0016 | 77.316 | 2.8743 | 74.4417 | -1089770 | 4792.49 | 0.005998 | 0.0038233 | 0.0038233 | -4.419e-05% | 0.0046231 | 20.92%
1 | 6 | 12 | 5 | 114863 | 42945.7 | 71917.1 |  | 0.50058 | 35999.9742 | 20 | 0.0017 | 77.3383 | 2.8949 | 74.4434 | -1085020 | 4770.63 | 0.0060229 | 0.003859 | 0.003859 | 0.0001297% | 0.004668 | 20.97%
1 | 6 | 13 | 5 | 114691 | 43544.4 | 71146.2 |  | 0.506 | 35999.9772 | 21 | 0.0018 | 77.2932 | 2.8984 | 74.3948 | -1053070 | 4771.78 | 0.0060138 | 0.0038816 | 0.0038816 | -7.213e-05% | 0.0046911 | 20.86%
1 | 6 | 14 | 5 | 114716 | 43984.9 | 70731.2 |  | 0.50897 | 35999.9881 | 23 | 0.0023 | 77.2557 | 2.908 | 74.3477 | -926695 | 4754.65 | 0.0060268 | 0.00413 | 0.00413 | 0.0001049% | 0.0048573 | 17.61%
1 | 6 | 15 | 5 | 114666 | 43872.3 | 70793.3 |  | 0.50852 | 35999.9505 | 23 | 0.0023 | 77.2412 | 2.912 | 74.3292 | -913254 | 4748.09 | 0.0060238 | 0.0041302 | 0.0041302 | 0.0001316% | 0.0048547 | 17.54%
1 | 6 | 16 | 5 | 114661 | 43925.8 | 70735.4 |  | 0.50894 | 36000.0037 | 24 | 0.0025 | 77.2419 | 2.9122 | 74.3297 | -853635 | 4748 | 0.006024 | 0.0042305 | 0.0042305 | -2.449e-05% | 0.0049176 | 16.24%
1 | 6 | 17 | 5 | 114670 | 44063.8 | 70606 |  | 0.50987 | 36000.0224 | 24 | 0.0025 | 77.2324 | 2.9135 | 74.3189 | -857639 | 4744.57 | 0.0060221 | 0.0042263 | 0.0042263 | -0.0001154% | 0.0049163 | 16.33%
1 | 6 | 18 | 5 | 114729 | 44468.9 | 70259.8 |  | 0.51238 | 35999.9974 | 23 | 0.0024 | 77.2047 | 2.9119 | 74.2928 | -899043 | 4744.89 | 0.0060164 | 0.0041634 | 0.0041634 | 9.624e-05% | 0.0048817 | 17.25%
1 | 6 | 19 | 5 | 114684 | 44462.4 | 70222 |  | 0.51266 | 36000.0105 | 23 | 0.0024 | 77.1873 | 2.9108 | 74.2765 | -899104 | 4749.04 | 0.0060129 | 0.0041607 | 0.0041607 | 1.04e-05% | 0.0048788 | 17.26%
1 | 6 | 20 | 5 | 114632 | 44334.3 | 70298.1 |  | 0.51211 | 36000.0085 | 25 | 0.0026 | 77.1926 | 2.912 | 74.2806 | -835928 | 4749.3 | 0.006014 | 0.0042657 | 0.0042657 | 8.275e-05% | 0.0049418 | 15.85%
1 | 6 | 21 | 5 | 111234 | 43695.3 | 67538.4 |  | 0.53303 | 36000.0609 | 25 | 0.0025 | 77.3217 | 3.0045 | 74.3172 | -874656 | 4742.72 | 0.0060402 | 0.0041532 | 0.0041531 | -0.000121% | 0.0048944 | 17.85%
1 | 6 | 22 | 5 | 111312 | 45219.4 | 66092.4 |  | 0.54469 | 36000.0015 | 26 | 0.0026 | 77.3425 | 2.9994 | 74.3431 | -884841 | 4748.39 | 0.0060444 | 0.0041683 | 0.0041683 | -4.025e-05% | 0.0049304 | 18.28%
1 | 6 | 23 | 5 | 111310 | 45949.8 | 65360.6 |  | 0.55079 | 36000.0302 | 27 | 0.0026 | 77.2628 | 2.9994 | 74.2634 | -889846 | 4748.42 | 0.0060282 | 0.00414 | 0.00414 | 4.276e-05% | 0.0049195 | 18.83%
1 | 6 | 24 | 5 | 111327 | 45960.6 | 65366.9 |  | 0.55074 | 36000.0358 | 27 | 0.0025 | 77.2319 | 2.9995 | 74.2324 | -916886 | 4747.75 | 0.006022 | 0.0040823 | 0.0040823 | 6.843e-05% | 0.0048831 | 19.62%
1 | 7 | 1 | 6 | 111133 | 42008.9 | 69124.4 |  | 0.5208 | 36000.0566 | 27 | 0.0025 | 76.6402 | 3.0047 | 73.6355 | -831977 | 4748.35 | 0.0059041 | 0.0041313 | 0.0041313 | 2.178e-05% | 0.0048014 | 16.22%
1 | 7 | 2 | 6 | 111165 | 41205.8 | 69959.3 |  | 0.51458 | 36000.0064 | 27 | 0.0024 | 76.1172 | 2.9962 | 73.121 | -818200 | 4759.94 | 0.0057814 | 0.0040414 | 0.0040414 | -7.089e-05% | 0.0046864 | 15.96%
1 | 7 | 3 | 6 | 111078 | 40931.5 | 70146.6 |  | 0.51321 | 36000.0067 | 26 | 0.0022 | 76.2401 | 2.9975 | 73.2426 | -879160 | 4762.45 | 0.0058055 | 0.0039551 | 0.0039551 | 6.592e-05% | 0.004637 | 17.24%
1 | 7 | 4 | 6 | 111014 | 40587 | 70426.8 |  | 0.51117 | 35999.9969 | 24 | 0.0019 | 76.3158 | 2.9982 | 73.3176 | -964199 | 4764.81 | 0.0058204 | 0.0038164 | 0.0038164 | 9.169e-05% | 0.0045491 | 19.2%
1 | 7 | 5 | 6 | 111040 | 40945.1 | 70094.9 |  | 0.51359 | 35999.9696 | 20 | 0.0014 | 76.3084 | 2.9947 | 73.3137 | -1111380 | 4770.49 | 0.0058189 | 0.0035494 | 0.0035494 | 0.0001812% | 0.0043863 | 23.58%
1 | 7 | 6 | 6 | 111115 | 41348.2 | 69767 |  | 0.516 | 36000.0511 | 17 | 0.0011 | 76.203 | 2.9752 | 73.2278 | -1199670 | 4800.79 | 0.0057785 | 0.0033644 | 0.0033644 | -5.77e-06% | 0.0042627 | 26.7%
1 | 7 | 7 | 6 | 111311 | 43221.4 | 68090 |  | 0.52871 | 36000.0001 | 15 | 0.001 | 76.373 | 2.9637 | 73.4093 | -1275670 | 4812.62 | 0.0058118 | 0.0032677 | 0.0032677 | 1.04e-06% | 0.0042555 | 30.23%
1 | 7 | 8 | 6 | 111327 | 45594.3 | 65733.1 |  | 0.54767 | 35999.9811 | 14 | 0.0009 | 76.9089 | 2.9578 | 73.9511 | -1368290 | 4822.41 | 0.0059165 | 0.0031691 | 0.0031691 | -0.0001087% | 0.0042943 | 35.5%
1 | 7 | 9 | 6 | 111327 | 44900.8 | 66426.6 |  | 0.54195 | 35999.9623 | 13 | 0.001 | 77.2966 | 2.9541 | 74.3426 | -1342500 | 4829.33 | 0.005994 | 0.0032875 | 0.0032875 | 0.0001529% | 0.0043791 | 33.2%
1 | 7 | 10 | 6 | 111327 | 44539.2 | 66788.3 |  | 0.53902 | 36000.0291 | 12 | 0.001 | 77.3847 | 2.9448 | 74.4399 | -1338780 | 4843.43 | 0.0059914 | 0.0033009 | 0.003301 | 1.655e-05% | 0.0043773 | 32.61%
1 | 7 | 11 | 6 | 111327 | 44490.2 | 66837.2 |  | 0.53862 | 35999.9863 | 11 | 0.001 | 77.4161 | 2.9438 | 74.4723 | -1334890 | 4845.03 | 0.0059977 | 0.0033058 | 0.0033058 | -3.537e-05% | 0.0043816 | 32.54%
1 | 7 | 12 | 6 | 111327 | 44602.4 | 66725 |  | 0.53953 | 36000.0058 | 10 | 0.0008 | 77.4157 | 2.9421 | 74.4736 | -1397330 | 4847.73 | 0.0059976 | 0.0031934 | 0.0031934 | -4.77e-05% | 0.0043169 | 35.18%
1 | 7 | 13 | 6 | 111327 | 44427.5 | 66900 |  | 0.53812 | 36000.0273 | 10 | 0.0009 | 77.4237 | 2.9401 | 74.4836 | -1365890 | 4852.05 | 0.0059992 | 0.0032552 | 0.0032553 | 6.97e-05% | 0.0043503 | 33.64%
1 | 7 | 14 | 6 | 111327 | 44491.8 | 66835.6 |  | 0.53863 | 35999.9934 | 11 | 0.0009 | 77.4422 | 2.9503 | 74.4919 | -1368950 | 4834.77 | 0.0060234 | 0.0032637 | 0.0032637 | -3.106e-05% | 0.0043666 | 33.79%
1 | 7 | 15 | 6 | 111327 | 43218.6 | 68108.8 |  | 0.52857 | 35999.996 | 12 | 0.0007 | 77.5106 | 2.9423 | 74.5683 | -1403590 | 4847.73 | 0.0060167 | 0.0032065 | 0.0032065 | -3.104e-05% | 0.0042974 | 34.02%
1 | 7 | 16 | 6 | 111327 | 43652 | 67675.5 |  | 0.53195 | 35999.9822 | 11 | 0.0009 | 77.564 | 2.9465 | 74.6174 | -1355160 | 4841.3 | 0.0060274 | 0.0032999 | 0.0032999 | 6.334e-06% | 0.0043693 | 32.41%
1 | 7 | 17 | 6 | 111327 | 45304.6 | 66022.8 |  | 0.54527 | 35999.9881 | 10 | 0.0007 | 77.4269 | 2.9442 | 74.4827 | -1441810 | 4844.34 | 0.0059999 | 0.00311 | 0.00311 | -0.0001405% | 0.004286 | 37.81%
1 | 7 | 18 | 6 | 111327 | 45696.7 | 65630.7 |  | 0.54852 | 35999.9485 | 9 | 0.0008 | 77.2979 | 2.9389 | 74.359 | -1415770 | 4854.69 | 0.005974 | 0.0031359 | 0.0031359 | 6.371e-05% | 0.0043009 | 37.15%
1 | 7 | 19 | 6 | 111327 | 45917.5 | 65409.9 |  | 0.55037 | 35999.9737 | 9 | 0.0008 | 77.257 | 2.9357 | 74.3213 | -1425290 | 4859.77 | 0.0059658 | 0.0031227 | 0.0031227 | 9.047e-05% | 0.0042953 | 37.55%
1 | 7 | 20 | 6 | 111327 | 46507.2 | 64820.2 |  | 0.55538 | 36000.0371 | 10 | 0.0008 | 77.1995 | 2.9351 | 74.2644 | -1462370 | 4860.92 | 0.0059543 | 0.0030917 | 0.0030917 | 5.235e-05% | 0.0042875 | 38.68%
1 | 7 | 21 | 6 | 111327 | 46523.7 | 64803.7 |  | 0.55552 | 36000.0106 | 10 | 0.0009 | 77.154 | 2.9357 | 74.2183 | -1426530 | 4860.26 | 0.0059451 | 0.0031424 | 0.0031424 | -2.54e-05% | 0.0043137 | 37.27%
1 | 7 | 22 | 6 | 111327 | 46680.6 | 64646.8 |  | 0.55687 | 35999.9928 | 9 | 0.0008 | 77.1361 | 2.9354 | 74.2007 | -1460180 | 4860.19 | 0.0059416 | 0.0030784 | 0.0030784 | 0.0001549% | 0.0042789 | 39%
1 | 7 | 23 | 6 | 111327 | 46851.4 | 64476.1 |  | 0.55835 | 36000.037 | 8 | 0.0007 | 77.1092 | 2.9332 | 74.176 | -1495220 | 4864.48 | 0.0059361 | 0.0030126 | 0.0030126 | -0.0001016% | 0.0042429 | 40.84%
1 | 7 | 24 | 6 | 111327 | 47029.6 | 64297.9 |  | 0.55989 | 36000.0084 | 7 | 0.0007 | 77.0831 | 2.9308 | 74.1523 | -1499240 | 4868.97 | 0.0059309 | 0.0030022 | 0.0030022 | -2.407e-05% | 0.0042394 | 41.21%
1 | 8 | 1 | 7 | 111278 | 43107.1 | 68171.2 |  | 0.52808 | 35999.9836 | 7 | 0.0007 | 76.4045 | 2.9297 | 73.4748 | -1375230 | 4873.09 | 0.0057982 | 0.0031059 | 0.0031059 | 7.558e-05% | 0.0041489 | 33.58%
1 | 8 | 2 | 7 | 111295 | 42270.6 | 69024.3 |  | 0.52156 | 36000.0378 | 7 | 0.0008 | 75.8302 | 2.934 | 72.8962 | -1293810 | 4864.38 | 0.0056873 | 0.0031383 | 0.0031383 | -2.035e-05% | 0.0041064 | 30.85%
1 | 8 | 3 | 7 | 111295 | 42524.6 | 68770.5 |  | 0.52348 | 36000.0501 | 6 | 0.0008 | 75.8867 | 2.9333 | 72.9534 | -1301980 | 4865.21 | 0.005698 | 0.003134 | 0.003134 | 1.696e-05% | 0.0041137 | 31.26%
1 | 8 | 4 | 7 | 111309 | 42617.4 | 68691.4 |  | 0.52408 | 35999.995 | 6 | 0.0008 | 75.8456 | 2.9309 | 72.9147 | -1302370 | 4868.62 | 0.0056902 | 0.0031273 | 0.0031273 | -3.736e-05% | 0.0041086 | 31.38%
1 | 8 | 5 | 7 | 111309 | 42676.1 | 68632.8 |  | 0.52453 | 36000.0312 | 5 | 0.0008 | 75.828 | 2.9306 | 72.8974 | -1302680 | 4869.23 | 0.0056869 | 0.0031236 | 0.0031236 | -0.0001696% | 0.0041064 | 31.46%
1 | 8 | 6 | 7 | 111309 | 42794.8 | 68514 |  | 0.52544 | 35999.9962 | 5 | 0.0008 | 75.8044 | 2.9286 | 72.8758 | -1304600 | 4872.56 | 0.0056824 | 0.003117 | 0.003117 | 3.963e-05% | 0.0041033 | 31.64%
1 | 8 | 7 | 7 | 111327 | 44523.9 | 66803.5 |  | 0.53889 | 36000.0053 | 6 | 0.0008 | 76.0737 | 2.9278 | 73.1459 | -1355780 | 4873.18 | 0.0057338 | 0.003075 | 0.003075 | -0.0001444% | 0.0041383 | 34.58%
1 | 8 | 8 | 7 | 111327 | 46937.3 | 64390.1 |  | 0.55909 | 35999.9898 | 6 | 0.0008 | 76.7213 | 2.9275 | 73.7938 | -1426930 | 4873.99 | 0.0058599 | 0.003031 | 0.003031 | 0.0001193% | 0.0042237 | 39.35%
1 | 8 | 9 | 7 | 111327 | 46577.6 | 64749.9 |  | 0.55599 | 36000.0379 | 6 | 0.0008 | 77.1231 | 2.9252 | 74.1979 | -1437530 | 4878.14 | 0.0059389 | 0.0030818 | 0.0030818 | -0.0001017% | 0.0042771 | 38.79%
1 | 8 | 10 | 7 | 111327 | 45934.7 | 65392.7 |  | 0.55052 | 35999.9892 | 6 | 0.0008 | 77.2114 | 2.9274 | 74.284 | -1427500 | 4874.06 | 0.0059566 | 0.0031178 | 0.0031178 | -0.0001107% | 0.0042891 | 37.57%
1 | 8 | 11 | 7 | 111327 | 44950.4 | 66377 |  | 0.54236 | 36000.0306 | 6 | 0.0007 | 77.3275 | 2.9291 | 74.3984 | -1436830 | 4870.99 | 0.0059799 | 0.0031163 | 0.0031163 | -7.761e-05% | 0.0042726 | 37.1%
1 | 8 | 12 | 7 | 111327 | 44184.5 | 67143 |  | 0.53617 | 35999.9952 | 7 | 0.0007 | 77.4447 | 2.9315 | 74.5132 | -1426120 | 4866.99 | 0.0060034 | 0.0031599 | 0.0031599 | 0.0001429% | 0.0042885 | 35.72%
1 | 8 | 13 | 7 | 111327 | 44198 | 67129.5 |  | 0.53628 | 36000.0069 | 6 | 0.0006 | 77.4907 | 2.9353 | 74.5554 | -1456590 | 4860.33 | 0.0060127 | 0.00311 | 0.00311 | 0.0001353% | 0.0042624 | 37.05%
1 | 8 | 14 | 7 | 111327 | 44488.5 | 66838.9 |  | 0.53861 | 35999.9663 | 7 | 0.0007 | 77.4722 | 2.9337 | 74.5385 | -1433090 | 4863.42 | 0.006009 | 0.0031495 | 0.0031495 | -0.0001179% | 0.0042922 | 36.28%
1 | 8 | 15 | 7 | 111327 | 44410.4 | 66917 |  | 0.53798 | 36000.0077 | 7 | 0.0006 | 77.4606 | 2.9348 | 74.5258 | -1459680 | 4861.12 | 0.0060066 | 0.003098 | 0.003098 | -0.0001352% | 0.0042583 | 37.45%
1 | 8 | 16 | 7 | 111327 | 44641.6 | 66685.8 |  | 0.53985 | 35999.9957 | 7 | 0.0007 | 77.4467 | 2.935 | 74.5117 | -1434170 | 4861.32 | 0.0060039 | 0.0031406 | 0.0031406 | -7.329e-05% | 0.0042887 | 36.56%
1 | 8 | 17 | 7 | 111327 | 46076.9 | 65250.5 |  | 0.55172 | 36000.0059 | 6 | 0.0007 | 77.3284 | 2.9247 | 74.4037 | -1457870 | 4878.11 | 0.0059599 | 0.0030579 | 0.0030579 | -0.0001001% | 0.004259 | 39.28%
1 | 8 | 18 | 7 | 111327 | 46468.3 | 64859.1 |  | 0.55505 | 35999.9786 | 5 | 0.0007 | 77.2073 | 2.9194 | 74.2879 | -1462370 | 4887.62 | 0.0059357 | 0.0030296 | 0.0030296 | -3.797e-05% | 0.0042426 | 40.04%
1 | 8 | 19 | 7 | 111327 | 46832.1 | 64495.3 |  | 0.55818 | 35999.9866 | 4 | 0.0005 | 77.1531 | 2.9162 | 74.2369 | -1537170 | 4893.3 | 0.0059249 | 0.0028968 | 0.0028968 | 0.0001691% | 0.0041706 | 43.97%
1 | 8 | 20 | 7 | 111327 | 47682.3 | 63645.1 |  | 0.56564 | 36000.0234 | 2 | 0.0005 | 77.0611 | 2.9133 | 74.1478 | -1583350 | 4899.27 | 0.0059065 | 0.0028484 | 0.0028484 | -0.00018% | 0.0041582 | 45.98%
1 | 8 | 21 | 7 | 111327 | 47911.5 | 63415.9 |  | 0.56768 | 36000.0015 | 1 | 0.0005 | 76.9789 | 2.9072 | 74.0716 | -1585580 | 4909.95 | 0.0058902 | 0.0028303 | 0.0028303 | 0.0001026% | 0.0041471 | 46.53%
1 | 8 | 22 | 7 | 111327 | 48008 | 63319.4 |  | 0.56855 | 35999.9916 | 1 | 0.0005 | 76.9523 | 2.9044 | 74.0479 | -1588110 | 4914.98 | 0.005885 | 0.0028234 | 0.0028234 | 0.0001454% | 0.0041437 | 46.76%
1 | 8 | 23 | 7 | 111327 | 48094.6 | 63232.8 |  | 0.56932 | 36000.0139 | 0 | 0.0005 | 76.9261 | 2.8943 | 74.0318 | -1588280 | 4932.11 | 0.0058601 | 0.0028085 | 0.0028085 | -6.073e-05% | 0.0041268 | 46.94%
1 | 8 | 24 | 7 | 111327 | 48325.2 | 63002.2 |  | 0.57141 | 35999.9611 | -1 | 0.0005 | 76.8987 | 2.8909 | 74.0078 | -1594470 | 4938.06 | 0.0058548 | 0.002795 | 0.002795 | 5.672e-05% | 0.0041232 | 47.52%
1 | 9 | 1 | 1 | 111315 | 44053.9 | 67261.5 |  | 0.53522 | 36000.0363 | -1 | 0.0005 | 76.1711 | 2.8895 | 73.2816 | -1451240 | 4941.08 | 0.005714 | 0.0029233 | 0.0029234 | 0.0001861% | 0.0040278 | 37.78%
1 | 9 | 2 | 1 | 111309 | 43292.8 | 68016 |  | 0.52929 | 35999.9846 | -2 | 0.0004 | 75.5355 | 2.8866 | 72.6489 | -1424530 | 4945.23 | 0.0055749 | 0.0028359 | 0.0028359 | -0.000112% | 0.0039012 | 37.57%
1 | 9 | 3 | 1 | 111309 | 43628.3 | 67680.7 |  | 0.53191 | 36000.0411 | -3 | 0.0004 | 75.5698 | 2.8839 | 72.6859 | -1435280 | 4950.69 | 0.0055813 | 0.0028253 | 0.0028253 | -0.0002322% | 0.0039056 | 38.23%
1 | 9 | 4 | 1 | 111309 | 43746.1 | 67562.7 |  | 0.53284 | 36000.0415 | -3 | 0.0004 | 75.512 | 2.8805 | 72.6315 | -1436360 | 4956.56 | 0.0055705 | 0.0028155 | 0.0028155 | -0.0001905% | 0.0038983 | 38.46%
1 | 9 | 5 | 1 | 111309 | 43820.1 | 67488.7 |  | 0.53342 | 36000.0248 | -3 | 0.0004 | 75.4845 | 2.8801 | 72.6044 | -1436630 | 4957.41 | 0.0055654 | 0.0028101 | 0.00281 | -8.881e-05% | 0.0038948 | 38.6%
1 | 9 | 6 | 1 | 114264 | 43816.8 | 70446.9 |  | 0.51102 | 35999.9862 | -4 | 0.0004 | 75.4524 | 2.7963 | 72.6561 | -1400490 | 4973.88 | 0.0055408 | 0.0029137 | 0.0029137 | 0.0001016% | 0.0039211 | 34.57%
1 | 9 | 7 | 1 | 116903 | 47811.8 | 69090.7 |  | 0.52106 | 36000.0547 | -4 | 0.0004 | 75.614 | 2.7373 | 72.8767 | -1475140 | 4965.5 | 0.0055709 | 0.0028766 | 0.0028766 | 2.252e-05% | 0.0039786 | 38.31%
1 | 9 | 8 | 1 | 117215 | 54580.2 | 62635.2 |  | 0.57476 | 36000.0196 | -4 | 0.0003 | 76.2193 | 2.7282 | 73.4911 | -1698640 | 4969.18 | 0.0056851 | 0.00259 | 0.00259 | 1.281e-05% | 0.0040312 | 55.65%
1 | 9 | 9 | 1 | 116033 | 48539.2 | 67493.4 |  | 0.53338 | 35999.9672 | -3 | 0.0004 | 76.6546 | 2.7355 | 73.9191 | -1562690 | 5008.94 | 0.0057496 | 0.0028962 | 0.0028962 | 0.0001705% | 0.0040898 | 41.21%
1 | 9 | 10 | 1 | 115525 | 46892.7 | 68632.3 |  | 0.52453 | 35999.9748 | -2 | 0.0004 | 76.9031 | 2.7609 | 74.1422 | -1520250 | 4981.91 | 0.0057972 | 0.0029662 | 0.0029662 | 0.0001883% | 0.0041153 | 38.74%
1 | 9 | 11 | 1 | 115767 | 45660.9 | 70105.7 |  | 0.51351 | 35999.978 | 0 | 0.0003 | 77.0018 | 2.7603 | 74.2416 | -1524160 | 4972.06 | 0.0058161 | 0.0029835 | 0.0029835 | -8.416e-05% | 0.0041008 | 37.45%
1 | 9 | 12 | 1 | 116082 | 45437.6 | 70644.9 |  | 0.50959 | 36000.0052 | 1 | 0.0004 | 77.0412 | 2.7593 | 74.2819 | -1500130 | 4960.04 | 0.0058239 | 0.0030599 | 0.0030599 | -7.885e-06% | 0.0041418 | 35.36%
1 | 9 | 13 | 1 | 116168 | 44348.3 | 71819.3 |  | 0.50126 | 35999.9987 | 3 | 0.0005 | 77.0822 | 2.7601 | 74.3221 | -1432700 | 4954.24 | 0.0058319 | 0.0031593 | 0.0031593 | 7.658e-05% | 0.0041796 | 32.3%
1 | 9 | 14 | 1 | 116119 | 44059.1 | 72059.7 |  | 0.49959 | 36000.0173 | 6 | 0.0006 | 77.1257 | 2.7667 | 74.359 | -1411530 | 4943.62 | 0.0058405 | 0.0032224 | 0.0032224 | -0.0001682% | 0.0042158 | 30.83%
1 | 9 | 15 | 1 | 115770 | 43809.3 | 71960.5 |  | 0.50028 | 36000.0391 | 7 | 0.0006 | 77.1544 | 2.7806 | 74.3738 | -1393270 | 4933.23 | 0.0058462 | 0.0032216 | 0.0032217 | 7.132e-05% | 0.0042148 | 30.83%
1 | 9 | 16 | 1 | 115375 | 44471.4 | 70904 |  | 0.50773 | 36000.017 | 7 | 0.0007 | 77.1521 | 2.7918 | 74.3603 | -1373050 | 4930.26 | 0.0058457 | 0.0032331 | 0.0032331 | -4.406e-05% | 0.0042401 | 31.15%
1 | 9 | 17 | 1 | 115382 | 46494.9 | 68887.3 |  | 0.52259 | 36000.0208 | 7 | 0.0005 | 77.0541 | 2.7992 | 74.2549 | -1475500 | 4916.79 | 0.0058459 | 0.0030522 | 0.0030522 | -0.0001389% | 0.0041779 | 36.88%
1 | 9 | 18 | 1 | 115517 | 47444.2 | 68072.6 |  | 0.52885 | 35999.9903 | 7 | 0.0005 | 76.934 | 2.7925 | 74.1415 | -1505640 | 4924.48 | 0.0058225 | 0.0030077 | 0.0030077 | 8.044e-05% | 0.0041638 | 38.44%
1 | 9 | 19 | 1 | 115597 | 47763.1 | 67833.5 |  | 0.53071 | 35999.9846 | 6 | 0.0005 | 76.8958 | 2.7887 | 74.1071 | -1510980 | 4928.18 | 0.0058151 | 0.0029943 | 0.0029943 | 4.77e-05% | 0.0041599 | 38.92%
1 | 9 | 20 | 1 | 115503 | 47718.4 | 67784.7 |  | 0.53109 | 35999.9797 | 7 | 0.0006 | 76.8881 | 2.7886 | 74.0995 | -1473010 | 4932.41 | 0.0058137 | 0.0030447 | 0.0030447 | 5.484e-05% | 0.0041887 | 37.57%
1 | 9 | 21 | 1 | 111327 | 46112 | 65215.4 |  | 0.55202 | 36000.0095 | 8 | 0.0007 | 77.0045 | 2.9045 | 74.1 | -1443800 | 4912.87 | 0.0058556 | 0.0030096 | 0.0030096 | -3.076e-05% | 0.0041885 | 39.17%
1 | 9 | 22 | 1 | 111327 | 46833 | 64494.5 |  | 0.55819 | 36000.056 | 10 | 0.0008 | 77.0261 | 2.9022 | 74.1239 | -1458520 | 4917.08 | 0.0058599 | 0.0030355 | 0.0030355 | -3.436e-05% | 0.0042237 | 39.14%
1 | 9 | 23 | 1 | 111327 | 46643.1 | 64684.4 |  | 0.55655 | 36000.0381 | 11 | 0.001 | 77.0272 | 2.9046 | 74.1226 | -1389490 | 4912.73 | 0.0058601 | 0.0031552 | 0.0031552 | -5.142e-05% | 0.0042885 | 35.92%
1 | 9 | 24 | 1 | 111327 | 46571.1 | 64756.4 |  | 0.55593 | 36000.0255 | 12 | 0.001 | 77.0422 | 2.9068 | 74.1353 | -1385530 | 4907.88 | 0.0058631 | 0.0031596 | 0.0031596 | 3.981e-05% | 0.0042905 | 35.79%
1 | 10 | 1 | 2 | 111240 | 42581.3 | 68658.6 |  | 0.52433 | 36000.0384 | 13 | 0.001 | 76.447 | 2.921 | 73.526 | -1271510 | 4887.95 | 0.0057674 | 0.0032677 | 0.0032677 | -0.0001726% | 0.0042246 | 29.28%
1 | 10 | 2 | 2 | 111239 | 41694.6 | 69544 |  | 0.51766 | 36000.008 | 13 | 0.001 | 75.9244 | 2.9274 | 72.997 | -1222560 | 4876.26 | 0.0056667 | 0.003251 | 0.003251 | -0.0001629% | 0.0041565 | 27.85%
1 | 10 | 3 | 2 | 111229 | 41792.7 | 69436.2 |  | 0.51846 | 35999.9617 | 15 | 0.0011 | 76.021 | 2.9369 | 73.0841 | -1201850 | 4861.02 | 0.0057042 | 0.0033171 | 0.0033171 | -8.898e-05% | 0.004214 | 27.04%
1 | 10 | 4 | 2 | 111207 | 41682.3 | 69524.9 |  | 0.5178 | 36000.0627 | 15 | 0.0011 | 76.0339 | 2.9414 | 73.0925 | -1198890 | 4854.04 | 0.0057067 | 0.0033213 | 0.0033214 | 2.876e-05% | 0.0042154 | 26.92%
1 | 10 | 5 | 2 | 111217 | 41927.9 | 69288.9 |  | 0.51956 | 36000.018 | 12 | 0.001 | 76.0115 | 2.9414 | 73.0701 | -1230850 | 4853.61 | 0.0057024 | 0.0032592 | 0.0032592 | -5.447e-05% | 0.0041802 | 28.26%
1 | 10 | 6 | 2 | 114065 | 42001.2 | 72064.1 |  | 0.49956 | 35999.9815 | 12 | 0.001 | 75.9301 | 2.8623 | 73.0678 | -1203350 | 4863.67 | 0.0056869 | 0.0033456 | 0.0033456 | 2.044e-05% | 0.0042077 | 25.77%
1 | 10 | 7 | 2 | 115853 | 44873.8 | 70978.8 |  | 0.50719 | 36000.0215 | 10 | 0.001 | 76.0329 | 2.8218 | 73.2111 | -1251080 | 4856.66 | 0.0057065 | 0.0033194 | 0.0033194 | -0.0001094% | 0.004244 | 27.85%
1 | 10 | 8 | 2 | 115841 | 47566.4 | 68274.9 |  | 0.52728 | 35999.9893 | 10 | 0.001 | 76.6305 | 2.8176 | 73.8129 | -1331770 | 4864.55 | 0.0058225 | 0.0032797 | 0.0032797 | 5.044e-05% | 0.0043238 | 31.84%
1 | 10 | 9 | 2 | 115609 | 47580.9 | 68028.5 |  | 0.52919 | 36000.0019 | 11 | 0.001 | 76.9417 | 2.8307 | 74.111 | -1354710 | 4852.15 | 0.0059029 | 0.0033083 | 0.0033083 | -0.0001532% | 0.0043762 | 32.28%
1 | 10 | 10 | 2 | 115218 | 46426 | 68792.4 |  | 0.52331 | 36000.026 | 11 | 0.0011 | 76.9824 | 2.8429 | 74.1395 | -1292430 | 4847.43 | 0.0059108 | 0.0033932 | 0.0033932 | -0.0001245% | 0.0044077 | 29.9%
1 | 10 | 11 | 2 | 115007 | 45832.2 | 69174.6 |  | 0.52042 | 35999.9837 | 12 | 0.0011 | 77.0362 | 2.8495 | 74.1867 | -1285180 | 4844.32 | 0.0059215 | 0.0034123 | 0.0034123 | 0.0001561% | 0.0044123 | 29.31%
1 | 10 | 12 | 2 | 114991 | 45777.2 | 69214 |  | 0.52013 | 36000.001 | 13 | 0.0011 | 77.053 | 2.8525 | 74.2005 | -1297280 | 4839.8 | 0.0059249 | 0.0034153 | 0.0034153 | -9.768e-06% | 0.0044144 | 29.25%
1 | 10 | 13 | 2 | 114848 | 45154.8 | 69693.2 |  | 0.51655 | 36000.0225 | 13 | 0.0012 | 77.0902 | 2.8676 | 74.2227 | -1246640 | 4820.33 | 0.0059525 | 0.0034976 | 0.0034976 | -0.0001108% | 0.0044628 | 27.6%
1 | 10 | 14 | 2 | 114910 | 45412.4 | 69497.8 |  | 0.518 | 35999.9994 | 15 | 0.0014 | 77.0993 | 2.867 | 74.2323 | -1204470 | 4817.93 | 0.0059543 | 0.0035952 | 0.0035952 | 8.71e-05% | 0.0045275 | 25.93%
1 | 10 | 15 | 2 | 114794 | 44969.1 | 69824.5 |  | 0.51558 | 36000.0459 | 16 | 0.0014 | 77.11 | 2.8731 | 74.2369 | -1184090 | 4811.79 | 0.0059565 | 0.0036073 | 0.0036073 | -1.546e-05% | 0.0045275 | 25.51%
1 | 10 | 16 | 2 | 114900 | 45169.2 | 69730.5 |  | 0.51627 | 36000.0442 | 17 | 0.0014 | 77.1182 | 2.8727 | 74.2455 | -1181350 | 4807.86 | 0.0059581 | 0.0036049 | 0.0036049 | -0.0001112% | 0.00453 | 25.66%
1 | 10 | 17 | 2 | 115042 | 45588.6 | 69453.2 |  | 0.51833 | 35999.955 | 17 | 0.0015 | 77.0967 | 2.8708 | 74.2259 | -1161040 | 4805.12 | 0.0059538 | 0.0036453 | 0.0036452 | -3.162e-05% | 0.0045601 | 25.1%
1 | 10 | 18 | 2 | 115133 | 45966 | 69167.3 |  | 0.52048 | 35999.9888 | 18 | 0.0016 | 77.0768 | 2.8777 | 74.1991 | -1149930 | 4789.39 | 0.0059701 | 0.0036956 | 0.0036956 | 0.0002345% | 0.0046036 | 24.57%
1 | 10 | 19 | 2 | 115152 | 46019.4 | 69132.6 |  | 0.52074 | 35999.9719 | 17 | 0.0015 | 77.0621 | 2.8786 | 74.1835 | -1178780 | 4786.71 | 0.0059671 | 0.0036409 | 0.0036409 | 0.0001554% | 0.0045706 | 25.53%
1 | 10 | 20 | 2 | 114991 | 45694.2 | 69296.9 |  | 0.5195 | 36000.0167 | 19 | 0.0017 | 77.074 | 2.8808 | 74.1932 | -1111030 | 4790.16 | 0.0059695 | 0.0037515 | 0.0037515 | 5.563e-05% | 0.0046329 | 23.49%
1 | 10 | 21 | 2 | 111311 | 44330.2 | 66981.3 |  | 0.53746 | 36000.0374 | 24 | 0.0018 | 77.2255 | 2.9798 | 74.2456 | -1084650 | 4783.13 | 0.0060001 | 0.0037427 | 0.0037427 | -0.0001081% | 0.0046417 | 24.02%
1 | 10 | 22 | 2 | 111309 | 50622.9 | 60686.1 |  | 0.59322 | 36000.0262 | 32 | 0.0023 | 77.0261 | 2.9864 | 74.0397 | -1040150 | 4772.85 | 0.0059599 | 0.0037888 | 0.0037888 | -3.087e-05% | 0.0047762 | 26.06%
1 | 10 | 23 | 2 | 111319 | 45263.5 | 66055.3 |  | 0.545 | 36000.0064 | 26 | 0.0022 | 77.008 | 2.992 | 74.016 | -982411 | 4763.05 | 0.0059562 | 0.0039091 | 0.0039091 | 7.834e-05% | 0.0047415 | 21.29%
1 | 10 | 24 | 2 | 111327 | 45546.5 | 65780.9 |  | 0.54727 | 35999.9789 | 26 | 0.0019 | 77.2389 | 2.9775 | 74.2614 | -1089350 | 4784.89 | 0.0059824 | 0.0037482 | 0.0037482 | -2.725e-05% | 0.0046623 | 24.39%
1 | 11 | 1 | 3 | 111006 | 41331 | 69674.8 |  | 0.51669 | 35999.9937 | 24 | 0.0015 | 76.7025 | 2.9865 | 73.716 | -1109520 | 4785.6 | 0.0058762 | 0.0036151 | 0.0036151 | 0.0001169% | 0.0044569 | 23.29%
1 | 11 | 2 | 3 | 111050 | 40768.8 | 70281 |  | 0.51223 | 36000.0366 | 22 | 0.0013 | 76.2175 | 2.9849 | 73.2326 | -1130660 | 4787.45 | 0.0057814 | 0.0034859 | 0.0034859 | 8.512e-05% | 0.0043286 | 24.18%
1 | 11 | 3 | 3 | 111075 | 41103.8 | 69971.4 |  | 0.5145 | 36000.0054 | 21 | 0.0013 | 76.2318 | 2.9796 | 73.2522 | -1138990 | 4795.97 | 0.0057842 | 0.0034771 | 0.0034771 | -6.854e-05% | 0.0043308 | 24.55%
1 | 11 | 4 | 3 | 111098 | 41276.1 | 69821.8 |  | 0.5156 | 35999.9804 | 19 | 0.0012 | 76.1748 | 2.9769 | 73.198 | -1168030 | 4799.55 | 0.005773 | 0.0034152 | 0.0034152 | 9.967e-07% | 0.0042912 | 25.65%
1 | 11 | 5 | 3 | 111133 | 41416.1 | 69716.9 |  | 0.51637 | 35999.9945 | 19 | 0.0013 | 76.1371 | 2.9719 | 73.1652 | -1141250 | 4806.5 | 0.0057656 | 0.0034597 | 0.0034597 | -0.0001605% | 0.0043191 | 24.84%
1 | 11 | 6 | 3 | 113967 | 41353.6 | 72613.6 |  | 0.49578 | 36000.0075 | 18 | 0.0012 | 76.0917 | 2.8977 | 73.194 | -1141100 | 4806.72 | 0.0057568 | 0.0034976 | 0.0034976 | -7.567e-05% | 0.0043174 | 23.44%
1 | 11 | 7 | 3 | 115440 | 43797.9 | 71642.3 |  | 0.5025 | 36000.0408 | 17 | 0.0012 | 76.1882 | 2.8626 | 73.3256 | -1182080 | 4803.21 | 0.0057756 | 0.0034764 | 0.0034764 | -0.0001546% | 0.0043487 | 25.09%
1 | 11 | 8 | 3 | 115503 | 46436.3 | 69067.1 |  | 0.52123 | 35999.9827 | 16 | 0.001 | 76.7326 | 2.8489 | 73.8837 | -1312310 | 4823.78 | 0.0058621 | 0.0033278 | 0.0033278 | 6.779e-05% | 0.0043467 | 30.62%
1 | 11 | 9 | 3 | 115295 | 46607.1 | 68688.3 |  | 0.52411 | 36000.0188 | 12 | 0.0008 | 77.0136 | 2.8508 | 74.1628 | -1396040 | 4830.64 | 0.005917 | 0.0032351 | 0.0032351 | -0.0001408% | 0.0043192 | 33.51%
1 | 11 | 10 | 3 | 115073 | 46313.4 | 68759.2 |  | 0.52357 | 36000.0481 | 8 | 0.0007 | 77.0014 | 2.8403 | 74.1611 | -1409750 | 4858.65 | 0.0058946 | 0.0031749 | 0.0031749 | -6.158e-06% | 0.0042695 | 34.48%
1 | 11 | 11 | 3 | 115196 | 46949 | 68247 |  | 0.5275 | 35999.9513 | 6 | 0.0007 | 76.9803 | 2.8302 | 74.1501 | -1424710 | 4871.36 | 0.0058905 | 0.0031525 | 0.0031525 | 0.0001135% | 0.0042684 | 35.4%
1 | 11 | 12 | 3 | 115276 | 47438.3 | 67837.5 |  | 0.53068 | 36000.0045 | 5 | 0.0007 | 76.9406 | 2.8237 | 74.1169 | -1449340 | 4879.42 | 0.0058827 | 0.0031324 | 0.0031324 | -3.692e-05% | 0.0042642 | 36.13%
1 | 11 | 13 | 3 | 114769 | 45974.7 | 68794.1 |  | 0.5233 | 36000.0213 | 6 | 0.0006 | 76.9852 | 2.8334 | 74.1518 | -1442580 | 4884.27 | 0.0058914 | 0.0031224 | 0.0031224 | -0.0001573% | 0.0042316 | 35.52%
1 | 11 | 14 | 3 | 115353 | 47567 | 67786 |  | 0.53108 | 35999.9922 | 6 | 0.0006 | 76.9561 | 2.8132 | 74.1429 | -1482200 | 4894.5 | 0.0058659 | 0.0030693 | 0.0030693 | -3.952e-05% | 0.0042225 | 37.57%
1 | 11 | 15 | 3 | 114714 | 45170.5 | 69544 |  | 0.51766 | 36000.008 | 6 | 0.0005 | 77.0143 | 2.827 | 74.1874 | -1456460 | 4898.35 | 0.0058773 | 0.0030937 | 0.0030937 | -7.639e-05% | 0.0041898 | 35.43%
1 | 11 | 16 | 3 | 114769 | 45271.4 | 69497.4 |  | 0.51801 | 36000.0007 | 5 | 0.0005 | 77.0907 | 2.8289 | 74.2618 | -1454920 | 4892.53 | 0.0058925 | 0.0030992 | 0.0030992 | 9.22e-05% | 0.004201 | 35.55%
1 | 11 | 17 | 3 | 115320 | 47565.4 | 67754.8 |  | 0.53133 | 35999.9546 | 5 | 0.0006 | 76.9748 | 2.8045 | 74.1703 | -1467950 | 4911.33 | 0.0058499 | 0.0030605 | 0.0030605 | 5.542e-05% | 0.004211 | 37.59%
1 | 11 | 18 | 3 | 115622 | 48678 | 66943.8 |  | 0.53776 | 35999.9657 | 3 | 0.0005 | 76.8554 | 2.7936 | 74.0619 | -1531620 | 4918.1 | 0.0058268 | 0.0029623 | 0.0029623 | 6.2e-05% | 0.0041683 | 40.71%
1 | 11 | 19 | 3 | 115699 | 49097.7 | 66600.8 |  | 0.54053 | 35999.9968 | 2 | 0.0004 | 76.8075 | 2.7862 | 74.0213 | -1573090 | 4928.62 | 0.0058176 | 0.0028892 | 0.0028892 | 0.0001039% | 0.0041319 | 43.01%
1 | 11 | 20 | 3 | 115690 | 49198.6 | 66491.2 |  | 0.54143 | 35999.998 | 0 | 0.0004 | 76.7831 | 2.7746 | 74.0085 | -1567480 | 4950.39 | 0.0057935 | 0.0028733 | 0.0028733 | 1.758e-05% | 0.0041151 | 43.22%
1 | 11 | 21 | 3 | 111327 | 47448.8 | 63878.7 |  | 0.56357 | 35999.9912 | -1 | 0.0004 | 76.8417 | 2.879 | 73.9626 | -1568230 | 4957.82 | 0.0058047 | 0.0027588 | 0.0027588 | 5.392e-05% | 0.004057 | 47.06%
1 | 11 | 22 | 3 | 111327 | 48488.2 | 62839.2 |  | 0.57289 | 35999.9493 | -2 | 0.0003 | 76.7735 | 2.8723 | 73.9012 | -1657390 | 4970.48 | 0.0057916 | 0.0026455 | 0.0026455 | 3.376e-06% | 0.0040158 | 51.8%
1 | 11 | 23 | 3 | 111327 | 48575.2 | 62752.2 |  | 0.57369 | 35999.9959 | -3 | 0.0003 | 76.7193 | 2.867 | 73.8523 | -1659980 | 4980.74 | 0.0057812 | 0.0026367 | 0.0026367 | -8.427e-05% | 0.0040087 | 52.03%
1 | 11 | 24 | 3 | 111327 | 48671.5 | 62655.9 |  | 0.57457 | 36000.0125 | -4 | 0.0003 | 76.6945 | 2.8645 | 73.83 | -1660390 | 4985.13 | 0.0057764 | 0.0026299 | 0.0026299 | 9.707e-05% | 0.0040055 | 52.31%
1 | 12 | 1 | 4 | 111315 | 44403.9 | 66911.3 |  | 0.53803 | 36000.0191 | -5 | 0.0003 | 75.9528 | 2.8625 | 73.0903 | -1511810 | 4989.27 | 0.0056342 | 0.0027643 | 0.0027642 | -7.772e-05% | 0.0039091 | 41.41%
1 | 12 | 2 | 4 | 111309 | 43770.6 | 67538.3 |  | 0.53303 | 36000.0076 | -6 | 0.0003 | 75.2817 | 2.8582 | 72.4235 | -1455570 | 4995.75 | 0.0054906 | 0.0027239 | 0.0027239 | -0.0002217% | 0.0038118 | 39.94%
1 | 12 | 3 | 4 | 111309 | 43963.6 | 67345.3 |  | 0.53456 | 36000.0362 | -6 | 0.0003 | 75.3271 | 2.8552 | 72.472 | -1464200 | 5001.5 | 0.005499 | 0.0027198 | 0.0027198 | -0.0001332% | 0.0038175 | 40.36%
1 | 12 | 4 | 4 | 111309 | 44055.4 | 67253.5 |  | 0.53529 | 35999.9915 | -7 | 0.0003 | 75.2887 | 2.8548 | 72.4339 | -1464170 | 5002.07 | 0.0054919 | 0.0027127 | 0.0027127 | 0.0002775% | 0.0038127 | 40.55%
1 | 12 | 5 | 4 | 111309 | 44102.5 | 67206.4 |  | 0.53566 | 36000.049 | -7 | 0.0003 | 75.267 | 2.8527 | 72.4143 | -1465200 | 5005.95 | 0.0054879 | 0.0027089 | 0.0027089 | -2.039e-05% | 0.00381 | 40.65%
1 | 12 | 6 | 4 | 113631 | 44073.8 | 69557.1 |  | 0.51756 | 36000.0422 | -7 | 0.0003 | 75.2526 | 2.7942 | 72.4584 | -1434210 | 5006.38 | 0.0054852 | 0.0028015 | 0.0028015 | -7.573e-05% | 0.0038424 | 37.15%
1 | 12 | 7 | 4 | 116468 | 50183.1 | 66284.6 |  | 0.54311 | 36000.028 | -7 | 0.0003 | 75.3873 | 2.7307 | 72.6566 | -1555470 | 4997.05 | 0.0055102 | 0.0026805 | 0.0026805 | 3.443e-05% | 0.0038998 | 45.49%
1 | 12 | 8 | 4 | 117359 | 59712.4 | 57646.7 |  | 0.62449 | 36000.0183 | -8 | 0.0003 | 75.8774 | 2.704 | 73.1734 | -1832470 | 5009.24 | 0.0056014 | 0.0022907 | 0.0022907 | -7.509e-08% | 0.0039752 | 73.54%
1 | 12 | 9 | 4 | 115986 | 53347.7 | 62638 |  | 0.57473 | 36000.0004 | -7 | 0.0003 | 76.2939 | 2.7053 | 73.5886 | -1709720 | 5069.65 | 0.0056616 | 0.0025801 | 0.0025801 | -0.0001348% | 0.0039975 | 54.93%
1 | 12 | 10 | 4 | 115130 | 47578.4 | 67551.4 |  | 0.53293 | 35999.9649 | -6 | 0.0003 | 76.7005 | 2.7419 | 73.9586 | -1571120 | 5036.56 | 0.0057392 | 0.0028405 | 0.0028405 | 0.0002631% | 0.0040384 | 42.17%
1 | 12 | 11 | 4 | 115183 | 46891.3 | 68291.3 |  | 0.52715 | 35999.9637 | -5 | 0.0003 | 76.9073 | 2.7547 | 74.1526 | -1557590 | 5008.4 | 0.0057787 | 0.0028906 | 0.0028906 | 0.0002185% | 0.0040664 | 40.68%
1 | 12 | 12 | 4 | 115473 | 46936.7 | 68536.8 |  | 0.52527 | 36000.0508 | -4 | 0.0003 | 76.932 | 2.7521 | 74.1799 | -1570470 | 5000.17 | 0.0057834 | 0.0029032 | 0.0029032 | 2.265e-05% | 0.0040739 | 40.33%
1 | 12 | 13 | 4 | 115493 | 45873.3 | 69620.1 |  | 0.51709 | 35999.9967 | -2 | 0.0004 | 76.976 | 2.7631 | 74.2129 | -1501650 | 4979.29 | 0.0058111 | 0.0030131 | 0.0030131 | 9.277e-05% | 0.0041244 | 36.88%
1 | 12 | 14 | 4 | 115477 | 46008.1 | 69469 |  | 0.51822 | 35999.9473 | -1 | 0.0004 | 77.0057 | 2.7693 | 74.2364 | -1518070 | 4967.78 | 0.0058169 | 0.0030097 | 0.0030098 | 0.0002152% | 0.0041282 | 37.16%
1 | 12 | 15 | 4 | 115187 | 45548.4 | 69638.1 |  | 0.51696 | 36000.0425 | 0 | 0.0004 | 77.0229 | 2.778 | 74.245 | -1495280 | 4964.87 | 0.0058202 | 0.0030182 | 0.0030182 | -0.0002326% | 0.0041262 | 36.71%
1 | 12 | 16 | 4 | 114882 | 45770.7 | 69111 |  | 0.5209 | 35999.989 | 1 | 0.0005 | 77.0357 | 2.7874 | 74.2483 | -1465920 | 4961.02 | 0.0058228 | 0.0030501 | 0.0030501 | 0.0001241% | 0.0041548 | 36.22%
1 | 12 | 17 | 4 | 115453 | 48225.3 | 67227.3 |  | 0.5355 | 36000.0175 | 0 | 0.0005 | 76.9248 | 2.7745 | 74.1503 | -1513250 | 4959.28 | 0.0058013 | 0.0029625 | 0.0029625 | -3.227e-05% | 0.0041483 | 40.03%
1 | 12 | 18 | 4 | 115654 | 49369.6 | 66284.1 |  | 0.54312 | 35999.9553 | 0 | 0.0005 | 76.7828 | 2.7549 | 74.0279 | -1547700 | 4986.59 | 0.0057549 | 0.0029009 | 0.0029009 | 8.879e-05% | 0.0041192 | 42%
1 | 12 | 19 | 4 | 115714 | 49600.6 | 66113.2 |  | 0.54452 | 36000.0258 | 0 | 0.0005 | 76.7417 | 2.7509 | 73.9908 | -1551810 | 4991.89 | 0.0057471 | 0.00289 | 0.0028899 | -5.482e-05% | 0.0041147 | 42.38%
1 | 12 | 20 | 4 | 115621 | 49342.5 | 66278.9 |  | 0.54316 | 36000.0473 | 0 | 0.0005 | 76.7546 | 2.7616 | 73.993 | -1540580 | 4976.53 | 0.0057687 | 0.002907 | 0.002907 | -0.0002737% | 0.0041282 | 42.01%
1 | 12 | 21 | 4 | 111327 | 47316 | 64011.5 |  | 0.5624 | 36000.0036 | 0 | 0.0005 | 76.8358 | 2.8687 | 73.9671 | -1532650 | 4975.41 | 0.0057843 | 0.0028124 | 0.0028124 | 6.529e-05% | 0.0040755 | 44.91%
1 | 12 | 22 | 4 | 111327 | 48176.4 | 63151 |  | 0.57006 | 35999.9854 | 0 | 0.0005 | 76.7912 | 2.8642 | 73.927 | -1583050 | 4984.14 | 0.0057757 | 0.0027682 | 0.0027682 | 3.989e-05% | 0.0040697 | 47.01%
1 | 12 | 23 | 4 | 111327 | 48282.1 | 63045.4 |  | 0.57102 | 35999.9952 | -1 | 0.0005 | 76.7534 | 2.8621 | 73.8913 | -1584690 | 4988.07 | 0.0057685 | 0.0027601 | 0.0027601 | -5.957e-05% | 0.0040648 | 47.27%
1 | 12 | 24 | 4 | 111327 | 48341.3 | 62986.1 |  | 0.57155 | 35999.9574 | -1 | 0.0005 | 76.7324 | 2.8596 | 73.8728 | -1584330 | 4992.54 | 0.0057645 | 0.0027555 | 0.0027555 | 4.041e-05% | 0.0040621 | 47.42%
1 | 13 | 1 | 5 | 111315 | 44104.4 | 67210.8 |  | 0.53563 | 36000.0536 | -1 | 0.0005 | 76.0277 | 2.8597 | 73.168 | -1442950 | 4993.04 | 0.0056295 | 0.002882 | 0.002882 | -0.0001249% | 0.0039706 | 37.77%
1 | 13 | 2 | 5 | 111309 | 43270.2 | 68038.7 |  | 0.52911 | 36000.0246 | -2 | 0.0005 | 75.4184 | 2.8664 | 72.552 | -1386760 | 4980.52 | 0.005516 | 0.002862 | 0.002862 | -0.0002323% | 0.0038937 | 36.05%
1 | 13 | 3 | 5 | 111309 | 43596 | 67712.9 |  | 0.53166 | 36000.0373 | -2 | 0.0005 | 75.4683 | 2.864 | 72.6043 | -1397580 | 4984.73 | 0.0055253 | 0.0028536 | 0.0028536 | -4.341e-05% | 0.0039 | 36.67%
1 | 13 | 4 | 5 | 111309 | 43587.2 | 67721.6 |  | 0.53159 | 35999.9899 | -2 | 0.0005 | 75.4333 | 2.8635 | 72.5698 | -1395700 | 4985.68 | 0.0055188 | 0.0028509 | 0.0028509 | -0.0001352% | 0.0038956 | 36.65%
1 | 13 | 5 | 5 | 111309 | 43697.6 | 67611.2 |  | 0.53246 | 35999.9891 | -3 | 0.0005 | 75.4266 | 2.8729 | 72.5537 | -1398220 | 4969.47 | 0.005536 | 0.0028545 | 0.0028545 | -0.0001083% | 0.0039072 | 36.88%
1 | 13 | 6 | 5 | 113570 | 43617.9 | 69952.2 |  | 0.51464 | 36000.0603 | -3 | 0.0005 | 75.3924 | 2.8137 | 72.5787 | -1368130 | 4972.92 | 0.0055296 | 0.0029412 | 0.0029412 | -0.0001117% | 0.0039353 | 33.8%
1 | 13 | 7 | 5 | 116124 | 47672.7 | 68450.9 |  | 0.52592 | 36000.0396 | -3 | 0.0005 | 75.6117 | 2.7562 | 72.8555 | -1446990 | 4964.28 | 0.0055705 | 0.0029038 | 0.0029038 | -0.0001113% | 0.0039986 | 37.7%
1 | 13 | 8 | 5 | 116354 | 52425.5 | 63928.7 |  | 0.56313 | 36000.041 | 0 | 0.0006 | 76.2926 | 2.7488 | 73.5438 | -1555470 | 4968.07 | 0.0056992 | 0.0028277 | 0.0028277 | 7.324e-05% | 0.0041215 | 45.75%
1 | 13 | 9 | 5 | 115268 | 48024.3 | 67243.4 |  | 0.53537 | 35999.9646 | 1 | 0.0006 | 76.7429 | 2.7734 | 73.9695 | -1493360 | 4971.22 | 0.0057857 | 0.0030095 | 0.0030095 | 2.484e-05% | 0.0041662 | 38.44%
1 | 13 | 10 | 5 | 114757 | 46560.3 | 68197.1 |  | 0.52788 | 36000.0215 | 3 | 0.0007 | 76.922 | 2.7958 | 74.1262 | -1424570 | 4951.57 | 0.0058202 | 0.0031173 | 0.0031173 | -0.000179% | 0.0042139 | 35.18%
1 | 13 | 11 | 5 | 114717 | 44984.4 | 69733 |  | 0.51626 | 36000.0099 | 4 | 0.0007 | 77.0399 | 2.8122 | 74.2277 | -1396650 | 4923.43 | 0.0058627 | 0.0031974 | 0.0031974 | 3.008e-05% | 0.0042425 | 32.69%
1 | 13 | 12 | 5 | 114965 | 45057.2 | 69907.8 |  | 0.51496 | 36000.0003 | 5 | 0.0007 | 77.0911 | 2.8113 | 74.2798 | -1410520 | 4913.71 | 0.0058728 | 0.003209 | 0.003209 | 0.0001129% | 0.004253 | 32.53%
1 | 13 | 13 | 5 | 115027 | 44357.8 | 70669.2 |  | 0.50942 | 36000.0212 | 5 | 0.0007 | 77.1225 | 2.8215 | 74.301 | -1383160 | 4893.3 | 0.0058988 | 0.0032505 | 0.0032505 | -7.006e-05% | 0.0042718 | 31.42%
1 | 13 | 14 | 5 | 114714 | 45442.3 | 69272.2 |  | 0.51969 | 36000.0003 | 7 | 0.0007 | 77.1099 | 2.8307 | 74.2792 | -1420010 | 4890.2 | 0.0058963 | 0.0031959 | 0.0031959 | -2.31e-05% | 0.0042656 | 33.47%
1 | 13 | 15 | 5 | 114744 | 45994.9 | 68749.2 |  | 0.52364 | 35999.9686 | 6 | 0.0007 | 77.0476 | 2.8405 | 74.2071 | -1413120 | 4872.52 | 0.0059038 | 0.0031789 | 0.0031789 | 0.0002201% | 0.0042711 | 34.36%
1 | 13 | 16 | 5 | 114905 | 46688.8 | 68216.5 |  | 0.52773 | 35999.9618 | 6 | 0.0007 | 76.9896 | 2.8339 | 74.1557 | -1418500 | 4877.28 | 0.0058923 | 0.0031521 | 0.0031521 | 0.0001091% | 0.0042655 | 35.32%
1 | 13 | 17 | 5 | 115290 | 47701.2 | 67588.4 |  | 0.53264 | 36000.015 | 5 | 0.0006 | 76.9319 | 2.8233 | 74.1086 | -1470250 | 4879.55 | 0.005881 | 0.0030682 | 0.0030682 | -0.0002395% | 0.004232 | 37.93%
1 | 13 | 18 | 5 | 115526 | 48436.8 | 67089.7 |  | 0.5366 | 35999.9976 | 5 | 0.0006 | 76.8859 | 2.8239 | 74.062 | -1499500 | 4869.27 | 0.005892 | 0.0030523 | 0.0030523 | -2.424e-05% | 0.0042429 | 39.01%
1 | 13 | 19 | 5 | 115508 | 48450.9 | 67056.9 |  | 0.53686 | 36000.0332 | 6 | 0.0007 | 76.866 | 2.8233 | 74.0427 | -1468210 | 4871.07 | 0.0058881 | 0.0031028 | 0.0031028 | 2.915e-05% | 0.0042712 | 37.65%
1 | 13 | 20 | 5 | 115383 | 48072 | 67311.1 |  | 0.53483 | 35999.9956 | 6 | 0.0007 | 76.8813 | 2.828 | 74.0533 | -1453510 | 4867.87 | 0.0058911 | 0.0031147 | 0.0031147 | -4.37e-05% | 0.0042715 | 37.14%
1 | 13 | 21 | 5 | 111327 | 46447.9 | 64879.5 |  | 0.55488 | 36000.0126 | 6 | 0.0007 | 76.9738 | 2.9316 | 74.0422 | -1452730 | 4866.83 | 0.0059091 | 0.0030187 | 0.0030187 | 0.0001322% | 0.0042246 | 39.95%
1 | 13 | 22 | 5 | 111327 | 47392.7 | 63934.8 |  | 0.56307 | 36000.0236 | 5 | 0.0008 | 76.9403 | 2.9273 | 74.013 | -1470920 | 4874.86 | 0.0059026 | 0.0030295 | 0.0030295 | -4.596e-05% | 0.0042526 | 40.37%
1 | 13 | 23 | 5 | 111327 | 47420.8 | 63906.6 |  | 0.56332 | 35999.9937 | 6 | 0.0008 | 76.9053 | 2.9232 | 73.9821 | -1471640 | 4881.59 | 0.0058958 | 0.0030252 | 0.0030252 | 0.0001659% | 0.0042479 | 40.42%
1 | 13 | 24 | 5 | 111327 | 47318.8 | 64008.6 |  | 0.56242 | 35999.9728 | 6 | 0.0008 | 76.9186 | 2.9347 | 73.9839 | -1468180 | 4862.46 | 0.0059184 | 0.0030397 | 0.0030397 | -7.402e-05% | 0.0042633 | 40.25%
1 | 14 | 1 | 6 | 111308 | 43297.3 | 68010.3 |  | 0.52933 | 35999.9601 | 5 | 0.0008 | 76.2566 | 2.9357 | 73.3209 | -1342710 | 4861.55 | 0.005789 | 0.0031482 | 0.0031482 | 7.457e-05% | 0.0041754 | 32.63%
1 | 14 | 2 | 6 | 111309 | 42455.3 | 68853.5 |  | 0.52285 | 35999.9836 | 6 | 0.0008 | 75.6798 | 2.939 | 72.7408 | -1291700 | 4855 | 0.0056781 | 0.0031276 | 0.0031276 | 2.398e-05% | 0.0041004 | 31.1%
1 | 14 | 3 | 6 | 111309 | 42603 | 68705.9 |  | 0.52397 | 35999.9678 | 6 | 0.0008 | 75.7599 | 2.9402 | 72.8197 | -1298430 | 4853.26 | 0.0056933 | 0.0031293 | 0.0031293 | -5.459e-05% | 0.0041107 | 31.36%
1 | 14 | 4 | 6 | 111309 | 42560.4 | 68748.4 |  | 0.52365 | 35999.9622 | 7 | 0.0009 | 75.7569 | 2.9403 | 72.8166 | -1268000 | 4853.13 | 0.0056927 | 0.003183 | 0.003183 | 7.007e-05% | 0.0041426 | 30.15%
1 | 14 | 5 | 6 | 111309 | 42621.6 | 68687.2 |  | 0.52411 | 35999.9918 | 7 | 0.0008 | 75.7517 | 2.9322 | 72.8195 | -1296410 | 4865.95 | 0.0056724 | 0.0031187 | 0.0031187 | -0.0001325% | 0.0040966 | 31.35%
1 | 14 | 6 | 6 | 111309 | 42667.7 | 68641.1 |  | 0.52447 | 35999.9918 | 8 | 0.0009 | 75.7389 | 2.932 | 72.8069 | -1267280 | 4866.88 | 0.00567 | 0.0031683 | 0.0031683 | 0.0002107% | 0.0041273 | 30.27%
1 | 14 | 7 | 6 | 111326 | 44398.7 | 66927.5 |  | 0.5379 | 35999.9676 | 8 | 0.0009 | 76.0133 | 2.9332 | 73.0801 | -1316440 | 4863.72 | 0.005722 | 0.0031283 | 0.0031283 | 0.0001576% | 0.0041627 | 33.07%
1 | 14 | 8 | 6 | 111327 | 46740.6 | 64586.8 |  | 0.55739 | 35999.9719 | 8 | 0.0009 | 76.6519 | 2.9312 | 73.7206 | -1385150 | 4867.26 | 0.0058464 | 0.0030893 | 0.0030893 | 0.0001773% | 0.0042469 | 37.47%
1 | 14 | 9 | 6 | 111327 | 46933 | 64394.5 |  | 0.55905 | 36000.0028 | 8 | 0.0009 | 77.0203 | 2.9292 | 74.0911 | -1405640 | 4870.94 | 0.0059183 | 0.0031128 | 0.0031128 | -2.211e-05% | 0.0042955 | 38%
1 | 14 | 10 | 6 | 111327 | 44997.9 | 66329.6 |  | 0.54274 | 35999.9924 | 9 | 0.0009 | 77.164 | 2.9302 | 74.2338 | -1372760 | 4869.14 | 0.0059471 | 0.0032078 | 0.0032078 | -0.0001544% | 0.004315 | 34.52%
1 | 14 | 11 | 6 | 111327 | 43515.7 | 67811.7 |  | 0.53088 | 36000.0109 | 10 | 0.0009 | 77.3923 | 2.9363 | 74.456 | -1347540 | 4858.14 | 0.0059929 | 0.0032892 | 0.0032892 | -5.262e-06% | 0.004346 | 32.13%
1 | 14 | 12 | 6 | 111327 | 42910 | 68417.4 |  | 0.52618 | 36000.0044 | 12 | 0.0011 | 77.5205 | 2.9418 | 74.5787 | -1282160 | 4848.41 | 0.0060187 | 0.0034306 | 0.0034305 | -0.0001485% | 0.0044281 | 29.08%
1 | 14 | 13 | 6 | 111327 | 42274.7 | 69052.7 |  | 0.52134 | 36000.0037 | 14 | 0.0009 | 77.6021 | 2.947 | 74.6551 | -1329520 | 4838.66 | 0.006035 | 0.0033579 | 0.0033579 | -4.989e-05% | 0.0043745 | 30.27%
1 | 14 | 14 | 6 | 111327 | 42010.2 | 69317.2 |  | 0.51935 | 35999.9571 | 16 | 0.0011 | 77.666 | 2.952 | 74.714 | -1268790 | 4830.96 | 0.0060479 | 0.0034782 | 0.0034782 | 0.0001139% | 0.0044479 | 27.88%
1 | 14 | 15 | 6 | 111327 | 42161.9 | 69165.5 |  | 0.52049 | 35999.9511 | 16 | 0.0011 | 77.6827 | 2.9563 | 74.7264 | -1270190 | 4822.98 | 0.0060512 | 0.0034742 | 0.0034741 | -2.533e-06% | 0.0044501 | 28.09%
1 | 14 | 16 | 6 | 111327 | 42712.7 | 68614.7 |  | 0.52467 | 36000.006 | 17 | 0.0012 | 77.6496 | 2.9562 | 74.6934 | -1249800 | 4823.19 | 0.0060446 | 0.0035028 | 0.0035028 | -1.287e-05% | 0.004478 | 27.84%
1 | 14 | 17 | 6 | 111327 | 44472 | 66855.4 |  | 0.53848 | 35999.9615 | 15 | 0.0011 | 77.5158 | 2.957 | 74.5588 | -1303820 | 4821.63 | 0.0060177 | 0.0033697 | 0.0033697 | 2.146e-05% | 0.0044275 | 31.39%
1 | 14 | 18 | 6 | 111327 | 45031.9 | 66295.6 |  | 0.54302 | 36000.0356 | 14 | 0.0011 | 77.3724 | 2.9501 | 74.4223 | -1310010 | 4834.04 | 0.0059889 | 0.0033341 | 0.0033341 | -0.0002059% | 0.004408 | 32.21%
1 | 14 | 19 | 6 | 111327 | 45343.2 | 65984.3 |  | 0.54558 | 36000.0443 | 13 | 0.001 | 77.3184 | 2.9466 | 74.3717 | -1350060 | 4840 | 0.0059781 | 0.0032621 | 0.0032621 | -6.573e-05% | 0.0043683 | 33.91%
1 | 14 | 20 | 6 | 111327 | 45862.1 | 65465.4 |  | 0.54991 | 36000.0126 | 15 | 0.0011 | 77.262 | 2.944 | 74.318 | -1353930 | 4844.96 | 0.0059668 | 0.0032905 | 0.0032905 | 8.749e-05% | 0.004393 | 33.51%
1 | 14 | 21 | 6 | 111327 | 45679.3 | 65648.2 |  | 0.54838 | 36000.0286 | 15 | 0.0012 | 77.2419 | 2.9466 | 74.2953 | -1315050 | 4840.46 | 0.0059628 | 0.003351 | 0.003351 | 5.112e-05% | 0.0044226 | 31.98%
1 | 14 | 22 | 6 | 111327 | 45635.2 | 65692.3 |  | 0.54801 | 36000.0373 | 16 | 0.0012 | 77.2551 | 2.9468 | 74.3083 | -1314700 | 4839.53 | 0.0059654 | 0.0033539 | 0.0033539 | 6.517e-05% | 0.0044244 | 31.92%
1 | 14 | 23 | 6 | 111327 | 45551.9 | 65775.5 |  | 0.54732 | 35999.9836 | 16 | 0.0013 | 77.2652 | 2.9489 | 74.3163 | -1282000 | 4836.2 | 0.0059675 | 0.0034129 | 0.0034129 | -1.881e-06% | 0.0044581 | 30.63%
1 | 14 | 24 | 6 | 111327 | 45525.1 | 65802.3 |  | 0.54709 | 35999.9777 | 17 | 0.0014 | 77.2729 | 2.949 | 74.3239 | -1251090 | 4835.4 | 0.005969 | 0.0034693 | 0.0034693 | 0.0002177% | 0.0044915 | 29.46%
1 | 15 | 1 | 7 | 111124 | 41900.9 | 69223.5 |  | 0.52005 | 35999.9581 | 17 | 0.0015 | 76.6817 | 2.9563 | 73.7254 | -1123130 | 4831.76 | 0.0058522 | 0.0035888 | 0.0035888 | 1.616e-05% | 0.0044423 | 23.78%
1 | 15 | 2 | 7 | 111151 | 41295.7 | 69855.2 |  | 0.51535 | 36000.017 | 14 | 0.0013 | 76.1355 | 2.9587 | 73.1768 | -1138600 | 4825.76 | 0.0057458 | 0.0034547 | 0.0034547 | -6.451e-05% | 0.0043059 | 24.64%
1 | 15 | 3 | 7 | 111196 | 41707.4 | 69489 |  | 0.51807 | 36000.0273 | 13 | 0.0012 | 76.1389 | 2.951 | 73.1879 | -1177340 | 4837.41 | 0.0057465 | 0.0033911 | 0.0033911 | -1.828e-05% | 0.0042745 | 26.05%
1 | 15 | 4 | 7 | 111216 | 41814.4 | 69401.8 |  | 0.51872 | 36000.0323 | 13 | 0.0012 | 76.0795 | 2.9482 | 73.1313 | -1176890 | 4841.88 | 0.0057349 | 0.0033826 | 0.0033826 | -0.0001177% | 0.004267 | 26.15%
1 | 15 | 5 | 7 | 111234 | 41997.2 | 69236.6 |  | 0.51996 | 35999.9856 | 11 | 0.001 | 76.0297 | 2.9374 | 73.0923 | -1234490 | 4858.86 | 0.0057059 | 0.003259 | 0.003259 | -1.661e-05% | 0.0041829 | 28.35%
1 | 15 | 6 | 7 | 111274 | 42283.9 | 68989.6 |  | 0.52182 | 36000.0151 | 9 | 0.0008 | 75.964 | 2.9323 | 73.0317 | -1296690 | 4866.75 | 0.0056933 | 0.0031399 | 0.0031399 | 7.408e-05% | 0.0041102 | 30.9%
1 | 15 | 7 | 7 | 111327 | 44186.4 | 67141.1 |  | 0.53618 | 35999.9836 | 8 | 0.0008 | 76.1715 | 2.9266 | 73.2449 | -1349360 | 4874.84 | 0.0057334 | 0.0030882 | 0.0030882 | 0.0001455% | 0.0041381 | 34%
1 | 15 | 8 | 7 | 111327 | 47123.7 | 64203.8 |  | 0.56071 | 36000.0337 | 5 | 0.0007 | 76.7364 | 2.9224 | 73.814 | -1459870 | 4882.42 | 0.0058431 | 0.0029593 | 0.0029593 | -7.104e-05% | 0.00418 | 41.25%
1 | 15 | 9 | 7 | 111327 | 45995.6 | 65331.8 |  | 0.55103 | 35999.9777 | 3 | 0.0006 | 77.1316 | 2.9034 | 74.2282 | -1486670 | 4915.4 | 0.0059007 | 0.0029798 | 0.0029798 | 4.759e-05% | 0.0041866 | 40.5%
1 | 15 | 10 | 7 | 111327 | 45159.8 | 66167.6 |  | 0.54407 | 36000.0046 | 2 | 0.0005 | 77.2789 | 2.9031 | 74.3758 | -1507450 | 4915.8 | 0.00593 | 0.0029757 | 0.0029757 | -6.152e-05% | 0.0041741 | 40.27%
1 | 15 | 11 | 7 | 111327 | 44342.5 | 66984.9 |  | 0.53743 | 35999.9627 | 2 | 0.0006 | 77.3881 | 2.9035 | 74.4846 | -1459570 | 4915.16 | 0.0059518 | 0.0030755 | 0.0030755 | 7.206e-05% | 0.0042212 | 37.25%
1 | 15 | 12 | 7 | 111327 | 43916.4 | 67411 |  | 0.53404 | 35999.9682 | 2 | 0.0005 | 77.4671 | 2.9055 | 74.5616 | -1483410 | 4910.84 | 0.0059675 | 0.0030477 | 0.0030477 | -8.655e-05% | 0.0041995 | 37.79%
1 | 15 | 13 | 7 | 111327 | 43675.9 | 67651.5 |  | 0.53214 | 36000.0016 | 2 | 0.0005 | 77.4996 | 2.9067 | 74.5929 | -1479460 | 4909.04 | 0.005974 | 0.0030611 | 0.0030611 | 5.739e-05% | 0.0042038 | 37.33%
1 | 15 | 14 | 7 | 111327 | 43487 | 67840.5 |  | 0.53066 | 36000.0362 | 2 | 0.0004 | 77.5257 | 2.9073 | 74.6184 | -1506080 | 4907.88 | 0.0059792 | 0.0030186 | 0.0030186 | 0.000125% | 0.004175 | 38.31%
1 | 15 | 15 | 7 | 111327 | 43650.1 | 67677.4 |  | 0.53194 | 35999.9778 | 3 | 0.0006 | 77.534 | 2.9078 | 74.6262 | -1450750 | 4907.4 | 0.0059808 | 0.0031186 | 0.0031186 | 9.218e-05% | 0.0042408 | 35.99%
1 | 15 | 16 | 7 | 111327 | 44349.6 | 66977.9 |  | 0.53749 | 36000.0184 | 2 | 0.0005 | 77.4858 | 2.9093 | 74.5765 | -1491840 | 4904.01 | 0.0059712 | 0.0030305 | 0.0030305 | -7.454e-05% | 0.004202 | 38.66%
1 | 15 | 17 | 7 | 111327 | 46310.7 | 65016.8 |  | 0.5537 | 35999.9972 | 0 | 0.0003 | 77.3181 | 2.906 | 74.4121 | -1590470 | 4910.4 | 0.0059378 | 0.0028161 | 0.0028161 | -8.204e-05% | 0.0041147 | 46.11%
1 | 15 | 18 | 7 | 111327 | 46966.4 | 64361 |  | 0.55934 | 36000.0035 | -1 | 0.0003 | 77.1481 | 2.8976 | 74.2505 | -1601880 | 4926.62 | 0.0059039 | 0.0027694 | 0.0027694 | -5.101e-05% | 0.0040918 | 47.75%
1 | 15 | 19 | 7 | 111327 | 47374.2 | 63953.3 |  | 0.56291 | 36000.0161 | -2 | 0.0003 | 77.0724 | 2.8934 | 74.179 | -1616300 | 4934.1 | 0.0058889 | 0.0027428 | 0.0027428 | 0.0001312% | 0.0040816 | 48.81%
1 | 15 | 20 | 7 | 111327 | 48230 | 63097.5 |  | 0.57055 | 36000.0262 | -3 | 0.0003 | 76.9751 | 2.8906 | 74.0845 | -1664650 | 4939.17 | 0.0058696 | 0.0026919 | 0.0026919 | 4.803e-05% | 0.0040686 | 51.14%
1 | 15 | 21 | 7 | 111327 | 48221.3 | 63106.1 |  | 0.57047 | 36000.0107 | -4 | 0.0003 | 76.9126 | 2.8955 | 74.0171 | -1661910 | 4931.27 | 0.0058773 | 0.0026956 | 0.0026956 | -4.364e-05% | 0.0040738 | 51.12%
1 | 15 | 22 | 7 | 111327 | 48277.5 | 63049.9 |  | 0.57098 | 35999.9797 | -4 | 0.0003 | 76.8983 | 2.8934 | 74.0049 | -1663780 | 4934.78 | 0.0058745 | 0.0026916 | 0.0026916 | -0.0001056% | 0.0040719 | 51.28%
1 | 15 | 23 | 7 | 111327 | 48389.4 | 62938.1 |  | 0.57199 | 36000.0268 | -5 | 0.0003 | 76.8793 | 2.8932 | 73.9861 | -1665690 | 4935.21 | 0.0058708 | 0.0026844 | 0.0026844 | -0.0001722% | 0.0040694 | 51.6%
1 | 15 | 24 | 7 | 111327 | 48497.8 | 62829.6 |  | 0.57298 | 35999.9785 | -6 | 0.0003 | 76.8554 | 2.8909 | 73.9645 | -1668530 | 4939.24 | 0.0058662 | 0.0026769 | 0.0026769 | 0.0002087% | 0.0040662 | 51.9%
1 | 16 | 1 | 8 | 111316 | 44206.1 | 67109.5 |  | 0.53644 | 36000.0189 | -6 | 0.0003 | 76.1188 | 2.8888 | 73.23 | -1519480 | 4943.38 | 0.0057232 | 0.002814 | 0.002814 | -0.0001567% | 0.0039693 | 41.06%
1 | 16 | 2 | 8 | 111309 | 43494.8 | 67813.9 |  | 0.53087 | 36000.026 | -5 | 0.0003 | 75.4867 | 2.9059 | 72.5808 | -1463140 | 4913.35 | 0.0056223 | 0.0027969 | 0.0027969 | 4.593e-05% | 0.003901 | 39.47%
1 | 16 | 3 | 8 | 111309 | 43653.2 | 67655.6 |  | 0.53211 | 36000.0183 | -5 | 0.0003 | 75.5446 | 2.9072 | 72.6374 | -1469220 | 4911.33 | 0.0056333 | 0.0027954 | 0.0027954 | -3.37e-05% | 0.0039084 | 39.81%
1 | 16 | 4 | 8 | 111309 | 43721.7 | 67587.1 |  | 0.53265 | 35999.9985 | -5 | 0.0004 | 75.5152 | 2.9071 | 72.6081 | -1438790 | 4911.49 | 0.0056277 | 0.0028432 | 0.0028432 | 0.0002059% | 0.003937 | 38.47%
1 | 16 | 5 | 8 | 111309 | 43736.9 | 67571.8 |  | 0.53277 | 36000.0252 | -4 | 0.0004 | 75.503 | 2.9068 | 72.5962 | -1438440 | 4911.56 | 0.0056254 | 0.0028415 | 0.0028415 | -4.706e-05% | 0.0039354 | 38.5%
1 | 16 | 6 | 8 | 111309 | 43723.6 | 67585.1 |  | 0.53266 | 36000.0145 | -3 | 0.0004 | 75.5077 | 2.9089 | 72.5988 | -1437280 | 4908.01 | 0.0056263 | 0.0028424 | 0.0028424 | 0.0001378% | 0.003936 | 38.47%
1 | 16 | 7 | 8 | 111327 | 46060.2 | 65267.3 |  | 0.55158 | 36000.0068 | -3 | 0.0004 | 75.7745 | 2.91 | 72.8645 | -1505410 | 4905.34 | 0.0056768 | 0.0027662 | 0.0027662 | 0.0001906% | 0.0039704 | 43.53%
1 | 16 | 8 | 8 | 111327 | 52477.8 | 58849.6 |  | 0.61173 | 36000.007 | -2 | 0.0004 | 76.2466 | 2.9069 | 73.3397 | -1680240 | 4911.21 | 0.0057675 | 0.002484 | 0.002484 | -3.777e-05% | 0.0040318 | 62.31%
1 | 16 | 9 | 8 | 111327 | 47639.6 | 63687.9 |  | 0.56526 | 36000.0313 | -1 | 0.0005 | 76.7077 | 2.8941 | 73.8136 | -1549900 | 4935.46 | 0.0058573 | 0.002829 | 0.002829 | 0.0001529% | 0.0041249 | 45.81%
1 | 16 | 10 | 8 | 111327 | 47586.5 | 63741 |  | 0.56479 | 36000.0244 | 1 | 0.0005 | 76.9941 | 2.9095 | 74.0846 | -1556160 | 4906.25 | 0.0059131 | 0.0028559 | 0.0028559 | 8.933e-05% | 0.0041626 | 45.76%
1 | 16 | 11 | 8 | 111327 | 46560.7 | 64766.7 |  | 0.55584 | 35999.9873 | 3 | 0.0006 | 77.087 | 2.9149 | 74.1721 | -1497200 | 4896.93 | 0.0059317 | 0.0029681 | 0.0029681 | 8.559e-05% | 0.0042076 | 41.76%
1 | 16 | 12 | 8 | 111327 | 45890.1 | 65437.3 |  | 0.55014 | 36000.0034 | 5 | 0.0007 | 77.2098 | 2.9214 | 74.2884 | -1454890 | 4885.03 | 0.0059563 | 0.0030646 | 0.0030646 | 2.711e-05% | 0.0042566 | 38.9%
1 | 16 | 13 | 8 | 111327 | 44975.6 | 66351.9 |  | 0.54256 | 36000.0196 | 6 | 0.0007 | 77.3114 | 2.9272 | 74.3842 | -1437580 | 4874.61 | 0.0059767 | 0.0031138 | 0.0031138 | 0.0002463% | 0.0042704 | 37.15%
1 | 16 | 14 | 8 | 111327 | 44993.8 | 66333.7 |  | 0.54271 | 36000.0287 | 9 | 0.0008 | 77.3721 | 2.9313 | 74.4408 | -1409240 | 4867.25 | 0.0059889 | 0.0031728 | 0.0031728 | -7.103e-05% | 0.0043109 | 35.87%
1 | 16 | 15 | 8 | 111327 | 43968.9 | 67358.6 |  | 0.53445 | 36000.0058 | 9 | 0.0008 | 77.4353 | 2.9372 | 74.4981 | -1388320 | 4857.05 | 0.0060016 | 0.0032216 | 0.0032216 | 2.028e-05% | 0.0043195 | 34.08%
1 | 16 | 16 | 8 | 111327 | 44245.5 | 67082 |  | 0.53666 | 36000.0249 | 9 | 0.0007 | 77.4787 | 2.9394 | 74.5393 | -1424910 | 4853 | 0.0060103 | 0.0031605 | 0.0031605 | -0.0001129% | 0.0042931 | 35.84%
1 | 16 | 17 | 8 | 111327 | 45749 | 65578.4 |  | 0.54896 | 35999.984 | 8 | 0.0008 | 77.3681 | 2.9391 | 74.429 | -1420930 | 4853.96 | 0.0059881 | 0.00314 | 0.00314 | -0.0001142% | 0.0043104 | 37.27%
1 | 16 | 18 | 8 | 111327 | 46293.6 | 65033.8 |  | 0.55356 | 35999.9803 | 8 | 0.0007 | 77.2381 | 2.934 | 74.3041 | -1458240 | 4862.59 | 0.005962 | 0.0030492 | 0.0030492 | 7.439e-05% | 0.0042604 | 39.72%
1 | 16 | 19 | 8 | 111327 | 46489.9 | 64837.5 |  | 0.55523 | 35999.9845 | 8 | 0.0008 | 77.189 | 2.9324 | 74.2566 | -1435720 | 4866.02 | 0.0059522 | 0.0030915 | 0.0030915 | 0.000181% | 0.0042861 | 38.64%
1 | 16 | 20 | 8 | 111327 | 47138.3 | 64189.1 |  | 0.56084 | 36000.0074 | 8 | 0.0008 | 77.1258 | 2.9318 | 74.194 | -1474000 | 4866.69 | 0.0059395 | 0.003057 | 0.003057 | 0.0001383% | 0.0042775 | 39.92%
1 | 16 | 21 | 8 | 111327 | 47090.2 | 64237.3 |  | 0.56042 | 35999.9961 | 9 | 0.0009 | 77.0808 | 2.9303 | 74.1505 | -1437500 | 4869.52 | 0.0059304 | 0.0031113 | 0.0031113 | 2.424e-05% | 0.0043037 | 38.33%
1 | 16 | 22 | 8 | 111327 | 46887.1 | 64440.3 |  | 0.55866 | 36000.0247 | 11 | 0.0009 | 77.106 | 2.9419 | 74.1641 | -1434440 | 4849.73 | 0.0059557 | 0.0031313 | 0.0031313 | -0.0001736% | 0.0043208 | 37.99%
1 | 16 | 23 | 8 | 111327 | 46670.7 | 64656.7 |  | 0.55679 | 36000.01 | 12 | 0.001 | 77.1321 | 2.9465 | 74.1856 | -1397570 | 4842.07 | 0.0059609 | 0.0031988 | 0.0031987 | -4.164e-05% | 0.0043567 | 36.2%
1 | 16 | 24 | 8 | 111327 | 46617.7 | 64709.7 |  | 0.55633 | 36000.0121 | 12 | 0.001 | 77.148 | 2.9489 | 74.199 | -1395940 | 4837.42 | 0.0059641 | 0.0032024 | 0.0032024 | 1.852e-05% | 0.0043589 | 36.11%
1 | 17 | 1 | 2 | 111213 | 42667.5 | 68545 |  | 0.5252 | 35999.9711 | 13 | 0.0011 | 76.5173 | 2.9522 | 73.5651 | -1250490 | 4837.07 | 0.00584 | 0.0033505 | 0.0033505 | 0.0001053% | 0.0043056 | 28.51%
1 | 17 | 2 | 2 | 111217 | 41764.4 | 69452.9 |  | 0.51834 | 36000.0078 | 13 | 0.0011 | 75.9825 | 2.9581 | 73.0244 | -1200820 | 4825.94 | 0.0057355 | 0.0033328 | 0.0033328 | 9.861e-05% | 0.004235 | 27.07%
1 | 17 | 3 | 2 | 111215 | 41987 | 69228.4 |  | 0.52002 | 36000.0141 | 13 | 0.0012 | 76.0535 | 2.9576 | 73.0959 | -1179950 | 4826.99 | 0.0057493 | 0.0033836 | 0.0033836 | -9.125e-05% | 0.0042767 | 26.4%
1 | 17 | 4 | 2 | 111226 | 42008.1 | 69218.2 |  | 0.52009 | 35999.9705 | 13 | 0.0012 | 76.0289 | 2.9572 | 73.0717 | -1178780 | 4826.74 | 0.0057445 | 0.0033809 | 0.0033809 | -7.051e-05% | 0.0042736 | 26.4%
1 | 17 | 5 | 2 | 111231 | 41995.4 | 69235.2 |  | 0.51997 | 35999.95 | 14 | 0.0013 | 76.0321 | 2.9569 | 73.0752 | -1149730 | 4826.94 | 0.0057451 | 0.0034338 | 0.0034338 | 0.0002427% | 0.0043065 | 25.41%
1 | 17 | 6 | 2 | 114575 | 41790.1 | 72784.6 |  | 0.49461 | 35999.991 | 15 | 0.0013 | 76.0365 | 2.8724 | 73.1641 | -1117690 | 4823.55 | 0.005746 | 0.003547 | 0.003547 | 0.0001111% | 0.004349 | 22.61%
1 | 17 | 7 | 2 | 116316 | 44268.2 | 72048 |  | 0.49967 | 36000.008 | 15 | 0.0014 | 76.1315 | 2.836 | 73.2955 | -1125310 | 4811.33 | 0.0057646 | 0.0035837 | 0.0035837 | 9.483e-05% | 0.0044137 | 23.16%
1 | 17 | 8 | 2 | 116260 | 46748.5 | 69511 |  | 0.5179 | 36000.0249 | 15 | 0.0013 | 76.7259 | 2.8368 | 73.8891 | -1224640 | 4811.94 | 0.0058807 | 0.0035084 | 0.0035084 | 3.569e-05% | 0.0044623 | 27.19%
1 | 17 | 9 | 2 | 115884 | 46459 | 69425.5 |  | 0.51854 | 36000.0376 | 16 | 0.0013 | 77.0325 | 2.8447 | 74.1878 | -1240890 | 4814.73 | 0.0059409 | 0.0035344 | 0.0035344 | 0.0001024% | 0.0044992 | 27.3%
1 | 17 | 10 | 2 | 115372 | 44456.3 | 70915.7 |  | 0.50765 | 36000.0005 | 17 | 0.0014 | 77.1185 | 2.8505 | 74.268 | -1170310 | 4826.11 | 0.005938 | 0.0036343 | 0.0036343 | -8.282e-05% | 0.004522 | 24.42%
1 | 17 | 11 | 2 | 115416 | 44374.8 | 71041.4 |  | 0.50675 | 36000.0163 | 19 | 0.0014 | 77.1922 | 2.8534 | 74.3388 | -1170900 | 4818.53 | 0.0059528 | 0.0036457 | 0.0036457 | 6.195e-05% | 0.0045327 | 24.33%
1 | 17 | 12 | 2 | 115364 | 44027.6 | 71336.8 |  | 0.50465 | 36000.0448 | 21 | 0.0016 | 77.2183 | 2.8681 | 74.3502 | -1121140 | 4795.77 | 0.0059783 | 0.0037688 | 0.0037688 | -0.0001227% | 0.004612 | 22.37%
1 | 17 | 13 | 2 | 115294 | 43360.6 | 71933.7 |  | 0.50046 | 36000.0114 | 22 | 0.0015 | 77.2662 | 2.8738 | 74.3924 | -1128620 | 4788.11 | 0.0059879 | 0.0037419 | 0.0037419 | -0.0001052% | 0.0045866 | 22.57%
1 | 17 | 14 | 2 | 115296 | 43543.9 | 71752.5 |  | 0.50172 | 36000.0231 | 23 | 0.0017 | 77.2839 | 2.8764 | 74.4075 | -1086120 | 4783.91 | 0.0059915 | 0.0038383 | 0.0038383 | -7.303e-05% | 0.0046515 | 21.19%
1 | 17 | 15 | 2 | 115223 | 43188.4 | 72034.4 |  | 0.49976 | 35999.9838 | 22 | 0.0015 | 77.2913 | 2.8798 | 74.4115 | -1125780 | 4780.61 | 0.005993 | 0.0037476 | 0.0037476 | 0.000102% | 0.0045892 | 22.46%
1 | 17 | 16 | 2 | 115197 | 43412.4 | 71785.1 |  | 0.5015 | 36000.0123 | 22 | 0.0016 | 77.2876 | 2.8695 | 74.4181 | -1095610 | 4799.52 | 0.0059719 | 0.0037794 | 0.0037794 | 0.0001377% | 0.0046057 | 21.86%
1 | 17 | 17 | 2 | 115253 | 44380.6 | 70872.5 |  | 0.50796 | 36000.0407 | 21 | 0.0017 | 77.2271 | 2.8676 | 74.3594 | -1082700 | 4800.04 | 0.0059598 | 0.003796 | 0.003796 | 8.67e-05% | 0.0046292 | 21.95%
1 | 17 | 18 | 2 | 115265 | 45108.6 | 70156.1 |  | 0.51314 | 36000.0415 | 21 | 0.0017 | 77.1443 | 2.8643 | 74.28 | -1101930 | 4805.03 | 0.0059432 | 0.0037658 | 0.0037658 | 2.648e-05% | 0.0046179 | 22.63%
1 | 17 | 19 | 2 | 115237 | 45214.6 | 70022.9 |  | 0.51412 | 36000.0333 | 21 | 0.0015 | 77.1117 | 2.8637 | 74.248 | -1161350 | 4807.41 | 0.0059367 | 0.0036557 | 0.0036557 | 8.847e-05% | 0.0045506 | 24.48%
1 | 17 | 20 | 2 | 115166 | 45094.7 | 70071.7 |  | 0.51376 | 36000.0366 | 21 | 0.0018 | 77.1137 | 2.8652 | 74.2485 | -1066490 | 4808.79 | 0.005937 | 0.0038116 | 0.0038116 | -0.0001488% | 0.0046438 | 21.83%
1 | 17 | 21 | 2 | 111314 | 44392.1 | 66921.9 |  | 0.53794 | 36000.0338 | 21 | 0.0017 | 77.2362 | 2.9644 | 74.2718 | -1110030 | 4807.48 | 0.0059616 | 0.0036691 | 0.0036691 | -0.00015% | 0.0045834 | 24.92%
1 | 17 | 22 | 2 | 111321 | 45210.7 | 66110.7 |  | 0.54454 | 35999.9867 | 21 | 0.0018 | 77.2844 | 2.9603 | 74.3241 | -1120100 | 4815.05 | 0.0059713 | 0.0036999 | 0.0036998 | -8.061e-05% | 0.0046223 | 24.93%
1 | 17 | 23 | 2 | 111326 | 45202.1 | 66123.9 |  | 0.54443 | 36000.0332 | 21 | 0.0018 | 77.2706 | 2.959 | 74.3116 | -1119490 | 4816.59 | 0.0059685 | 0.003699 | 0.003699 | 4.078e-06% | 0.0046205 | 24.91%
1 | 17 | 24 | 2 | 111327 | 45209.5 | 66117.9 |  | 0.54448 | 36000.0064 | 21 | 0.0019 | 77.2735 | 2.959 | 74.3145 | -1087930 | 4816.68 | 0.0059691 | 0.0037536 | 0.0037535 | -4.546e-05% | 0.0046533 | 23.97%
1 | 18 | 1 | 3 | 111064 | 41590.9 | 69472.7 |  | 0.51819 | 35999.9889 | 22 | 0.0017 | 76.7096 | 2.9659 | 73.7436 | -1058360 | 4816.26 | 0.0058577 | 0.0037032 | 0.0037032 | -9.931e-05% | 0.00451 | 21.79%
1 | 18 | 2 | 3 | 111074 | 40806.9 | 70266.9 |  | 0.51233 | 35999.9814 | 21 | 0.0017 | 76.2136 | 2.9702 | 73.2434 | -1017310 | 4809.43 | 0.005761 | 0.0036804 | 0.0036804 | -1.355e-05% | 0.0044448 | 20.77%
1 | 18 | 3 | 3 | 111088 | 41060.7 | 70027.5 |  | 0.51408 | 36000.0173 | 21 | 0.0018 | 76.2652 | 2.9672 | 73.298 | -996263 | 4813.83 | 0.0057711 | 0.0037296 | 0.0037296 | 3.511e-05% | 0.0044842 | 20.23%
1 | 18 | 4 | 3 | 111096 | 41071.5 | 70024.2 |  | 0.51411 | 36000.0014 | 21 | 0.0018 | 76.2431 | 2.9668 | 73.2763 | -995112 | 4813.69 | 0.0057668 | 0.0037274 | 0.0037274 | 4.853e-05% | 0.0044814 | 20.23%
1 | 18 | 5 | 3 | 111101 | 41113.6 | 69987.2 |  | 0.51438 | 36000.0159 | 21 | 0.0018 | 76.2405 | 2.9666 | 73.2739 | -995579 | 4813.86 | 0.0057663 | 0.0037261 | 0.0037261 | 0.0001391% | 0.0044811 | 20.26%
1 | 18 | 6 | 3 | 114192 | 41071.6 | 73120.3 |  | 0.49234 | 36000.0485 | 20 | 0.0017 | 76.2021 | 2.8862 | 73.3159 | -998081 | 4813.97 | 0.0057588 | 0.0037605 | 0.0037605 | -0.0001241% | 0.0044792 | 19.11%
1 | 18 | 7 | 3 | 115551 | 43331.8 | 72219.7 |  | 0.49848 | 36000.0038 | 19 | 0.0015 | 76.2641 | 2.8543 | 73.4098 | -1088010 | 4810.2 | 0.0057709 | 0.0036419 | 0.0036419 | 0.0001641% | 0.0044403 | 21.92%
1 | 18 | 8 | 3 | 115572 | 45835.1 | 69737.1 |  | 0.51623 | 36000.0344 | 18 | 0.0015 | 76.7907 | 2.8514 | 73.9393 | -1152860 | 4815.29 | 0.0058734 | 0.0036158 | 0.0036158 | -0.0001169% | 0.0045111 | 24.76%
1 | 18 | 9 | 3 | 115079 | 45129 | 69950.1 |  | 0.51465 | 35999.9589 | 19 | 0.0016 | 77.1024 | 2.8606 | 74.2418 | -1134370 | 4820.51 | 0.0059348 | 0.0037039 | 0.0037039 | 4.473e-05% | 0.0045787 | 23.62%
1 | 18 | 10 | 3 | 114916 | 43988 | 70928.5 |  | 0.50755 | 36000.0439 | 20 | 0.0017 | 77.175 | 2.8678 | 74.3072 | -1079360 | 4814.54 | 0.0059493 | 0.0037926 | 0.0037926 | 1.281e-05% | 0.0046181 | 21.77%
1 | 18 | 11 | 3 | 114898 | 43636.6 | 71261.7 |  | 0.50518 | 36000.0569 | 20 | 0.0016 | 77.2381 | 2.8715 | 74.3666 | -1104750 | 4808.28 | 0.005962 | 0.0037584 | 0.0037584 | 1.272e-05% | 0.0045953 | 22.27%
1 | 18 | 12 | 3 | 114920 | 43796.6 | 71123.5 |  | 0.50616 | 36000.013 | 22 | 0.0018 | 77.2424 | 2.8717 | 74.3707 | -1060970 | 4807.34 | 0.0059629 | 0.0038558 | 0.0038558 | -0.0001713% | 0.0046588 | 20.83%
1 | 18 | 13 | 3 | 114998 | 42887.7 | 72110.2 |  | 0.49924 | 36000.0078 | 22 | 0.0017 | 77.2734 | 2.8729 | 74.4005 | -1064670 | 4801.22 | 0.0059691 | 0.0038378 | 0.0038378 | -8.899e-05% | 0.0046327 | 20.71%
1 | 18 | 14 | 3 | 114891 | 43499.2 | 71391.6 |  | 0.50426 | 35999.9996 | 22 | 0.0016 | 77.287 | 2.877 | 74.41 | -1114740 | 4799.06 | 0.0059718 | 0.0037673 | 0.0037673 | -8.713e-05% | 0.0046019 | 22.16%
1 | 18 | 15 | 3 | 114818 | 43399.1 | 71419.1 |  | 0.50407 | 36000.0115 | 23 | 0.0017 | 77.2672 | 2.878 | 74.3892 | -1072870 | 4800.95 | 0.0059678 | 0.0038166 | 0.0038166 | -5.934e-05% | 0.0046297 | 21.31%
1 | 18 | 16 | 3 | 114816 | 43354.1 | 71462.4 |  | 0.50376 | 36000.0415 | 23 | 0.0018 | 77.2753 | 2.8797 | 74.3956 | -1039180 | 4797.87 | 0.0059695 | 0.0038691 | 0.003869 | -0.0001424% | 0.0046621 | 20.5%
1 | 18 | 17 | 3 | 114865 | 44107.9 | 70757.1 |  | 0.50878 | 36000.0096 | 23 | 0.0018 | 77.2365 | 2.8785 | 74.358 | -1051950 | 4797.29 | 0.0059617 | 0.0038443 | 0.0038443 | -0.0001807% | 0.0046574 | 21.15%
1 | 18 | 18 | 3 | 114911 | 44709.1 | 70201.9 |  | 0.51281 | 36000.0257 | 22 | 0.0018 | 77.1693 | 2.8764 | 74.2929 | -1068560 | 4799.18 | 0.0059482 | 0.003821 | 0.003821 | -2.275e-05% | 0.0046486 | 21.66%
1 | 18 | 19 | 3 | 114900 | 44918.3 | 69981.7 |  | 0.51442 | 35999.9861 | 22 | 0.0019 | 77.1341 | 2.874 | 74.2601 | -1041610 | 4803.81 | 0.0059411 | 0.0038623 | 0.0038623 | 0.0001751% | 0.004675 | 21.04%
1 | 18 | 20 | 3 | 114879 | 44876.6 | 70002.3 |  | 0.51427 | 36000.0128 | 21 | 0.0019 | 77.1292 | 2.874 | 74.2552 | -1035460 | 4804.25 | 0.0059402 | 0.0038624 | 0.0038624 | 0.0001505% | 0.0046741 | 21.01%
1 | 18 | 21 | 3 | 111308 | 44240.3 | 67068.2 |  | 0.53677 | 35999.9965 | 22 | 0.002 | 77.246 | 2.9645 | 74.2815 | -1019820 | 4807.1 | 0.0059636 | 0.0038361 | 0.0038361 | 2.748e-05% | 0.0046817 | 22.04%
1 | 18 | 22 | 3 | 111318 | 44962.2 | 66355.9 |  | 0.54253 | 36000.0001 | 22 | 0.0019 | 77.297 | 2.9623 | 74.3347 | -1085210 | 4810.36 | 0.0059738 | 0.0037636 | 0.0037637 | 0.0001198% | 0.0046564 | 23.72%
1 | 18 | 23 | 3 | 111318 | 44959.1 | 66358.6 |  | 0.54251 | 36000.005 | 22 | 0.0019 | 77.2858 | 2.9615 | 74.3243 | -1085000 | 4812.35 | 0.0059716 | 0.0037627 | 0.0037627 | -1.73e-05% | 0.0046548 | 23.71%
1 | 18 | 24 | 3 | 111327 | 44984.9 | 66342.5 |  | 0.54264 | 36000.0279 | 22 | 0.002 | 77.2879 | 2.9612 | 74.3267 | -1053790 | 4812.43 | 0.005972 | 0.0038166 | 0.0038166 | -5.523e-05% | 0.0046876 | 22.82%
1 | 19 | 1 | 4 | 111039 | 41459.5 | 69579.4 |  | 0.5174 | 36000.0337 | 22 | 0.002 | 76.7263 | 2.9689 | 73.7574 | -970133 | 4812.05 | 0.0058609 | 0.0038633 | 0.0038633 | -9.202e-06% | 0.0046092 | 19.31%
1 | 19 | 2 | 4 | 111065 | 40703.7 | 70361.7 |  | 0.51164 | 36000.0009 | 22 | 0.0021 | 76.2308 | 2.9705 | 73.2603 | -902765 | 4807.81 | 0.0057644 | 0.0038895 | 0.0038895 | -1.83e-05% | 0.0045766 | 17.67%
1 | 19 | 3 | 4 | 111063 | 40906.3 | 70156.2 |  | 0.51314 | 36000.0226 | 22 | 0.0021 | 76.2878 | 2.9697 | 73.3181 | -908820 | 4809.05 | 0.0057755 | 0.0038894 | 0.0038894 | 1.33e-05% | 0.0045841 | 17.86%
1 | 19 | 4 | 4 | 111073 | 40930.3 | 70143.1 |  | 0.51324 | 35999.9641 | 22 | 0.0021 | 76.2682 | 2.9693 | 73.2989 | -908010 | 4809.14 | 0.0057717 | 0.0038872 | 0.0038872 | 4.909e-05% | 0.0045816 | 17.86%
1 | 19 | 5 | 4 | 111078 | 40964.8 | 70113.5 |  | 0.51345 | 35999.9869 | 22 | 0.0021 | 76.2663 | 2.9691 | 73.2972 | -908363 | 4809.31 | 0.0057713 | 0.0038862 | 0.0038863 | 0.0001321% | 0.0045814 | 17.89%
1 | 19 | 6 | 4 | 114093 | 40872.6 | 73220.5 |  | 0.49167 | 36000.0304 | 22 | 0.0021 | 76.2328 | 2.8906 | 73.3422 | -884935 | 4809.4 | 0.0057648 | 0.0039629 | 0.0039629 | -7.083e-05% | 0.0046084 | 16.29%
1 | 19 | 7 | 4 | 115261 | 42896.7 | 72364.3 |  | 0.49748 | 36000.0091 | 21 | 0.002 | 76.3157 | 2.8649 | 73.4508 | -941143 | 4802.73 | 0.0057809 | 0.0039 | 0.0039 | 3.976e-05% | 0.0046 | 17.95%
1 | 19 | 8 | 4 | 115241 | 45119.5 | 70121.9 |  | 0.51339 | 36000.0225 | 22 | 0.0021 | 76.8415 | 2.8631 | 73.9784 | -967630 | 4807.05 | 0.0058833 | 0.003941 | 0.003941 | -4.119e-05% | 0.0047015 | 19.3%
1 | 19 | 9 | 4 | 115131 | 45249.3 | 69882 |  | 0.51515 | 35999.9918 | 22 | 0.0021 | 77.1202 | 2.8667 | 74.2535 | -985736 | 4805.26 | 0.0059384 | 0.003961 | 0.003961 | 8.817e-05% | 0.0047382 | 19.62%
1 | 19 | 10 | 4 | 114856 | 44357 | 70499.4 |  | 0.51064 | 35999.9546 | 24 | 0.0023 | 77.1521 | 2.8743 | 74.2778 | -908238 | 4803.83 | 0.0059448 | 0.0040836 | 0.0040836 | 6.034e-05% | 0.0048024 | 17.6%
1 | 19 | 11 | 4 | 114798 | 43857.7 | 70940.6 |  | 0.50747 | 36000.0135 | 25 | 0.0024 | 77.2045 | 2.88 | 74.3245 | -874764 | 4795.68 | 0.0059553 | 0.0041511 | 0.0041511 | 6.922e-05% | 0.0048404 | 16.6%
1 | 19 | 12 | 4 | 114807 | 44655.3 | 70151.9 |  | 0.51317 | 35999.9908 | 26 | 0.0024 | 77.1944 | 2.8822 | 74.3122 | -892668 | 4791.04 | 0.0059532 | 0.0041298 | 0.0041298 | -7.936e-05% | 0.0048391 | 17.17%
1 | 19 | 13 | 4 | 114683 | 44737.9 | 69944.8 |  | 0.51469 | 35999.9591 | 27 | 0.0025 | 77.1773 | 2.8861 | 74.2912 | -854571 | 4789.95 | 0.0059498 | 0.0041742 | 0.0041742 | -2.424e-05% | 0.0048669 | 16.59%
1 | 19 | 14 | 4 | 114794 | 45396.1 | 69397.6 |  | 0.51875 | 36000.005 | 27 | 0.0025 | 77.1498 | 2.8847 | 74.2651 | -869403 | 4787.28 | 0.0059443 | 0.0041576 | 0.0041576 | -6.013e-06% | 0.0048641 | 16.99%
1 | 19 | 15 | 4 | 114657 | 45948 | 68708.9 |  | 0.52395 | 35999.9594 | 28 | 0.0029 | 77.0967 | 2.8778 | 74.2189 | -743976 | 4804.69 | 0.0059136 | 0.0043346 | 0.0043346 | 0.0001683% | 0.0049674 | 14.6%
1 | 19 | 16 | 4 | 114802 | 47140.8 | 67661.6 |  | 0.53206 | 36000.0309 | 29 | 0.0026 | 77.0401 | 2.8746 | 74.1655 | -839110 | 4802.35 | 0.0059023 | 0.0041453 | 0.0041453 | 8.643e-05% | 0.0048667 | 17.4%
1 | 19 | 17 | 4 | 114912 | 47545.7 | 67365.8 |  | 0.5344 | 36000.0141 | 29 | 0.0027 | 76.9856 | 2.8723 | 74.1133 | -813961 | 4803.3 | 0.0058915 | 0.004186 | 0.004186 | -9.905e-05% | 0.0048916 | 16.86%
1 | 19 | 18 | 4 | 114946 | 47046.1 | 67900 |  | 0.53019 | 36000.0368 | 28 | 0.0027 | 76.9861 | 2.8709 | 74.1152 | -816966 | 4803.91 | 0.0058916 | 0.0041994 | 0.0041994 | -4.366e-06% | 0.004892 | 16.49%
1 | 19 | 19 | 4 | 114943 | 47175 | 67768.4 |  | 0.53122 | 35999.9972 | 28 | 0.0026 | 76.9925 | 2.8698 | 74.1227 | -849615 | 4805.69 | 0.0058928 | 0.0041436 | 0.0041436 | 4.32e-06% | 0.0048615 | 17.33%
1 | 19 | 20 | 4 | 114866 | 47040.5 | 67825.1 |  | 0.53078 | 36000.0031 | 28 | 0.0026 | 76.9853 | 2.8621 | 74.1232 | -840769 | 4822.44 | 0.0058716 | 0.0041351 | 0.0041351 | -8.029e-07% | 0.0048463 | 17.2%
1 | 19 | 21 | 4 | 111308 | 46105.9 | 65202.5 |  | 0.55213 | 35999.9955 | 28 | 0.0027 | 77.0938 | 2.9535 | 74.1403 | -819100 | 4822.64 | 0.0058931 | 0.0041301 | 0.0041301 | -0.0001107% | 0.0048604 | 17.68%
1 | 19 | 22 | 4 | 111310 | 47662.4 | 63647.9 |  | 0.56561 | 36000.016 | 29 | 0.0028 | 77.085 | 2.9504 | 74.1346 | -824963 | 4827.57 | 0.0058914 | 0.0041429 | 0.0041429 | 9.731e-05% | 0.0048916 | 18.07%
1 | 19 | 23 | 4 | 111311 | 46807.8 | 64502.8 |  | 0.55812 | 35999.9802 | 28 | 0.0027 | 77.0724 | 2.9501 | 74.1223 | -844560 | 4827.95 | 0.0058889 | 0.0041091 | 0.0041091 | 9.296e-05% | 0.0048575 | 18.21%
1 | 19 | 24 | 4 | 111327 | 46866.5 | 64460.9 |  | 0.55848 | 35999.9945 | 28 | 0.0027 | 77.109 | 2.9489 | 74.1601 | -846644 | 4829.49 | 0.0058962 | 0.0041112 | 0.0041112 | -1.531e-05% | 0.0048626 | 18.28%
1 | 20 | 1 | 5 | 111315 | 43184 | 68131.1 |  | 0.52839 | 35999.9963 | 29 | 0.0028 | 76.415 | 2.9493 | 73.4657 | -731512 | 4829.36 | 0.0057612 | 0.0041965 | 0.0041965 | 0.000162% | 0.0048035 | 14.46%
1 | 20 | 2 | 5 | 111309 | 42212.4 | 69096.4 |  | 0.52101 | 35999.9845 | 29 | 0.0028 | 75.8295 | 2.9533 | 72.8762 | -687317 | 4822.27 | 0.0056489 | 0.0041646 | 0.0041646 | -8.279e-05% | 0.0047275 | 13.52%
1 | 20 | 3 | 5 | 111309 | 42474.3 | 68834.6 |  | 0.52299 | 36000.014 | 29 | 0.0028 | 75.9099 | 2.9523 | 72.9576 | -694693 | 4824.29 | 0.005664 | 0.0041662 | 0.0041662 | -5.789e-05% | 0.0047377 | 13.72%
1 | 20 | 4 | 5 | 111309 | 42468.8 | 68840.1 |  | 0.52295 | 35999.9991 | 29 | 0.0028 | 75.8877 | 2.9523 | 72.9354 | -693418 | 4824.29 | 0.0056599 | 0.0041643 | 0.0041643 | -3.404e-05% | 0.0047349 | 13.7%
1 | 20 | 5 | 5 | 111309 | 43075.9 | 68233 |  | 0.5276 | 36000.0037 | 30 | 0.0031 | 75.8152 | 2.9522 | 72.863 | -607194 | 4824.43 | 0.0056462 | 0.0043028 | 0.0043028 | 9.629e-05% | 0.0048227 | 12.08%
1 | 20 | 6 | 5 | 113884 | 42948.1 | 70936 |  | 0.5075 | 35999.9491 | 30 | 0.003 | 75.7145 | 2.8765 | 72.838 | -612832 | 4838.11 | 0.0056085 | 0.0042847 | 0.0042847 | 9.88e-05% | 0.0047839 | 11.65%
1 | 20 | 7 | 5 | 115453 | 46816.2 | 68636.5 |  | 0.5245 | 35999.9815 | 31 | 0.0031 | 75.825 | 2.8399 | 72.9851 | -620987 | 4834.17 | 0.0056291 | 0.0043026 | 0.0043026 | -8.7e-05% | 0.0048405 | 12.5%
1 | 20 | 8 | 5 | 115296 | 48040.6 | 67255.6 |  | 0.53527 | 36000.0395 | 29 | 0.0028 | 76.5092 | 2.8434 | 73.6658 | -762157 | 4834.48 | 0.0057601 | 0.0041756 | 0.0041756 | 4.929e-05% | 0.0048358 | 15.81%
1 | 20 | 9 | 5 | 115190 | 48585.2 | 66604.9 |  | 0.5405 | 36000.0151 | 29 | 0.0027 | 76.9062 | 2.8436 | 74.0626 | -824791 | 4839.73 | 0.0058366 | 0.0041413 | 0.0041413 | -5.944e-05% | 0.0048564 | 17.27%
1 | 20 | 10 | 5 | 114899 | 47744 | 67155.5 |  | 0.53607 | 36000.0489 | 29 | 0.0027 | 76.9209 | 2.8515 | 74.0694 | -807706 | 4838.89 | 0.0058395 | 0.0041565 | 0.0041565 | 8.651e-05% | 0.0048558 | 16.82%
1 | 20 | 11 | 5 | 114867 | 48435.3 | 66431.6 |  | 0.54191 | 36000.0148 | 30 | 0.003 | 76.9234 | 2.853 | 74.0704 | -723669 | 4837.53 | 0.00584 | 0.004301 | 0.004301 | -2.285e-05% | 0.0049499 | 15.09%
1 | 20 | 12 | 5 | 114888 | 48562.2 | 66325.9 |  | 0.54278 | 36000.0404 | 30 | 0.0031 | 76.8945 | 2.8533 | 74.0412 | -699756 | 4834.85 | 0.0058344 | 0.0043502 | 0.0043502 | 0.0001388% | 0.0049776 | 14.42%
1 | 20 | 13 | 5 | 114832 | 48409.8 | 66422.6 |  | 0.54198 | 35999.9864 | 30 | 0.0031 | 76.8966 | 2.8545 | 74.0421 | -690665 | 4834.85 | 0.0058348 | 0.0043526 | 0.0043526 | 4.955e-05% | 0.0049774 | 14.36%
1 | 20 | 14 | 5 | 114939 | 49558.9 | 65380.6 |  | 0.55062 | 35999.9967 | 31 | 0.0033 | 76.8582 | 2.8519 | 74.0063 | -644765 | 4834.62 | 0.0058274 | 0.0044357 | 0.0044358 | 7.808e-05% | 0.0050358 | 13.53%
1 | 20 | 15 | 5 | 114839 | 48476.7 | 66361.9 |  | 0.54248 | 36000.0035 | 30 | 0.0031 | 76.8607 | 2.8548 | 74.0059 | -688926 | 4833.29 | 0.0058279 | 0.0043481 | 0.0043481 | 0.0001169% | 0.0049727 | 14.37%
1 | 20 | 16 | 5 | 114770 | 49181.9 | 65588.4 |  | 0.54888 | 35999.9642 | 31 | 0.0033 | 76.863 | 2.8465 | 74.0165 | -628393 | 4851.06 | 0.0058088 | 0.0044318 | 0.0044318 | 2.067e-05% | 0.0050219 | 13.32%
1 | 20 | 17 | 5 | 115077 | 49957.5 | 65119.6 |  | 0.55283 | 36000.0033 | 31 | 0.0033 | 76.8046 | 2.8396 | 73.965 | -633633 | 4849.12 | 0.0057976 | 0.0044169 | 0.0044169 | -2.804e-05% | 0.0050163 | 13.57%
1 | 20 | 18 | 5 | 115182 | 50401.8 | 64780.1 |  | 0.55573 | 35999.9859 | 31 | 0.0033 | 76.7603 | 2.8363 | 73.924 | -642539 | 4850.54 | 0.0057891 | 0.0044058 | 0.0044058 | 5.478e-05% | 0.0050111 | 13.74%
1 | 20 | 19 | 5 | 115053 | 49392.4 | 65660.8 |  | 0.54827 | 35999.9781 | 30 | 0.0031 | 76.782 | 2.8388 | 73.9432 | -697980 | 4851.63 | 0.0057933 | 0.0043166 | 0.0043166 | 2.208e-05% | 0.0049505 | 14.69%
1 | 20 | 20 | 5 | 114972 | 49187.3 | 65785.1 |  | 0.54724 | 36000.0408 | 30 | 0.0031 | 76.8235 | 2.8402 | 73.9833 | -695077 | 4853.46 | 0.0058012 | 0.004323 | 0.004323 | -9.128e-05% | 0.0049554 | 14.63%
1 | 20 | 21 | 5 | 111308 | 47919 | 63389.5 |  | 0.56792 | 36000.0381 | 30 | 0.0031 | 76.9234 | 2.934 | 73.9894 | -700333 | 4852.9 | 0.0058204 | 0.0042755 | 0.0042755 | -5.901e-05% | 0.0049406 | 15.56%
1 | 20 | 22 | 5 | 111310 | 48630.5 | 62679.6 |  | 0.57435 | 36000.0283 | 30 | 0.0031 | 76.9316 | 2.9313 | 74.0003 | -724490 | 4857.83 | 0.005822 | 0.0042586 | 0.0042586 | -5.135e-05% | 0.0049417 | 16.04%
1 | 20 | 23 | 5 | 111309 | 48632.8 | 62676.5 |  | 0.57438 | 36000.0027 | 30 | 0.0033 | 76.9147 | 2.9303 | 73.9844 | -659084 | 4859.59 | 0.0058188 | 0.004372 | 0.004372 | -4.16e-05% | 0.0050041 | 14.46%
1 | 20 | 24 | 5 | 111327 | 48680.9 | 62646.5 |  | 0.57465 | 35999.9992 | 30 | 0.0031 | 76.9106 | 2.9297 | 73.9809 | -722813 | 4858.84 | 0.005818 | 0.0042561 | 0.0042561 | -2.602e-05% | 0.0049391 | 16.05%
1 | 21 | 1 | 6 | 111315 | 43305.4 | 68009.5 |  | 0.52934 | 36000.0127 | 29 | 0.003 | 76.2884 | 2.93 | 73.3584 | -660072 | 4859.84 | 0.0056984 | 0.00427 | 0.00427 | -0.0001325% | 0.0048257 | 13.01%
1 | 21 | 2 | 6 | 111309 | 42338.8 | 68970.1 |  | 0.52197 | 35999.9782 | 29 | 0.0031 | 75.777 | 2.9329 | 72.8441 | -592289 | 4855.26 | 0.0056014 | 0.0042957 | 0.0042957 | 5.605e-05% | 0.0047924 | 11.56%
1 | 21 | 3 | 6 | 111309 | 42591.2 | 68717.7 |  | 0.52388 | 35999.9661 | 29 | 0.0031 | 75.8628 | 2.932 | 72.9307 | -599355 | 4856.4 | 0.0056174 | 0.0042986 | 0.0042986 | 0.0001092% | 0.0048032 | 11.74%
1 | 21 | 4 | 6 | 111309 | 42096.7 | 69212.1 |  | 0.52014 | 36000.0509 | 28 | 0.0028 | 75.8974 | 2.9321 | 72.9653 | -684674 | 4856.33 | 0.0056238 | 0.004155 | 0.004155 | -0.0001097% | 0.0047105 | 13.37%
1 | 21 | 5 | 6 | 111264 | 41658.3 | 69606.1 |  | 0.5172 | 35999.9965 | 27 | 0.0028 | 76.0165 | 2.9323 | 73.0842 | -687506 | 4859.21 | 0.0056461 | 0.0041741 | 0.0041741 | -5.327e-05% | 0.0047253 | 13.2%
1 | 21 | 6 | 6 | 111272 | 41764.6 | 69507 |  | 0.51793 | 35999.969 | 27 | 0.0027 | 76.0635 | 2.9312 | 73.1323 | -720512 | 4860.48 | 0.0056552 | 0.0041246 | 0.0041246 | 0.0001153% | 0.0046991 | 13.93%
1 | 21 | 7 | 6 | 111309 | 43459.7 | 67848.8 |  | 0.53059 | 36000.0305 | 27 | 0.0027 | 76.3076 | 2.9303 | 73.3773 | -753468 | 4860.77 | 0.0057021 | 0.0041092 | 0.0041092 | 8.971e-06% | 0.0047311 | 15.14%
1 | 21 | 8 | 6 | 111327 | 44514.9 | 66812.5 |  | 0.53882 | 35999.9781 | 23 | 0.0022 | 76.9434 | 2.9288 | 74.0146 | -941009 | 4862.68 | 0.0058243 | 0.0038714 | 0.0038715 | 2.711e-05% | 0.0046523 | 20.17%
1 | 21 | 9 | 6 | 111327 | 43728.1 | 67599.3 |  | 0.53255 | 36000.0072 | 25 | 0.0024 | 77.4006 | 2.913 | 74.4876 | -892876 | 4891.07 | 0.0058947 | 0.0040336 | 0.0040336 | 2.2e-05% | 0.0047646 | 18.12%
1 | 21 | 10 | 6 | 111327 | 42737.9 | 68589.5 |  | 0.52486 | 36000.0221 | 26 | 0.0023 | 77.5669 | 2.9192 | 74.6477 | -916292 | 4879.35 | 0.0059276 | 0.0040236 | 0.0040236 | -7.824e-05% | 0.0047545 | 18.17%
1 | 21 | 11 | 6 | 111327 | 43301.5 | 68025.9 |  | 0.52921 | 35999.9865 | 28 | 0.0024 | 77.6427 | 2.9327 | 74.71 | -896196 | 4857 | 0.0059624 | 0.0040771 | 0.0040771 | 8.497e-05% | 0.0048104 | 17.99%
1 | 21 | 12 | 6 | 111327 | 43343.4 | 67984.1 |  | 0.52954 | 36000.0284 | 29 | 0.0023 | 77.6468 | 2.936 | 74.7108 | -924888 | 4851.07 | 0.0059632 | 0.0040234 | 0.0040234 | 0.0001073% | 0.0047786 | 18.77%
1 | 21 | 13 | 6 | 111327 | 45408 | 65919.4 |  | 0.54612 | 35999.9686 | 32 | 0.0027 | 77.5799 | 2.9378 | 74.6421 | -829034 | 4848.51 | 0.0059499 | 0.0041751 | 0.0041751 | -1.156e-05% | 0.004899 | 17.34%
1 | 21 | 14 | 6 | 111327 | 45981 | 65346.4 |  | 0.55091 | 35999.9852 | 32 | 0.0028 | 77.4741 | 2.9404 | 74.5337 | -798510 | 4842.85 | 0.005929 | 0.0042052 | 0.0042052 | 6.207e-05% | 0.0049172 | 16.93%
1 | 21 | 15 | 6 | 111327 | 46711 | 64616.4 |  | 0.55713 | 35999.9934 | 32 | 0.0025 | 77.4021 | 2.9393 | 74.4628 | -895412 | 4844.38 | 0.0059147 | 0.0040123 | 0.0040123 | 5.595e-05% | 0.0048105 | 19.89%
1 | 21 | 16 | 6 | 111327 | 46730.3 | 64597.1 |  | 0.5573 | 35999.9638 | 31 | 0.0025 | 77.341 | 2.9383 | 74.4027 | -892716 | 4847.84 | 0.0059026 | 0.0040063 | 0.0040064 | 7.875e-05% | 0.0048023 | 19.87%
1 | 21 | 17 | 6 | 111327 | 47094.9 | 64232.6 |  | 0.56046 | 36000.0599 | 30 | 0.0025 | 77.2781 | 2.9361 | 74.342 | -894735 | 4851.45 | 0.0058902 | 0.0039901 | 0.0039901 | -0.0001266% | 0.0047939 | 20.14%
1 | 21 | 18 | 6 | 111327 | 46657.2 | 64670.2 |  | 0.55667 | 35999.9602 | 29 | 0.0026 | 77.248 | 2.9335 | 74.3145 | -857122 | 4855.94 | 0.0058843 | 0.004056 | 0.004056 | 2.43e-05% | 0.0048222 | 18.89%
1 | 21 | 19 | 6 | 111327 | 46057 | 65270.5 |  | 0.55155 | 36000.0095 | 28 | 0.0025 | 77.2817 | 2.932 | 74.3497 | -885756 | 4857.84 | 0.0058909 | 0.0040206 | 0.0040207 | 4.939e-06% | 0.0047944 | 19.24%
1 | 21 | 20 | 6 | 111327 | 46570.9 | 64756.5 |  | 0.55593 | 36000.0163 | 28 | 0.0026 | 77.269 | 2.931 | 74.338 | -879050 | 4859.72 | 0.0058884 | 0.0040603 | 0.0040603 | -6.115e-05% | 0.004825 | 18.83%
1 | 21 | 21 | 6 | 111327 | 46641.4 | 64686 |  | 0.55654 | 36000.023 | 28 | 0.0027 | 77.2298 | 2.9303 | 74.2995 | -845254 | 4860.67 | 0.0058806 | 0.0041105 | 0.0041105 | 6.125e-05% | 0.0048521 | 18.04%
1 | 21 | 22 | 6 | 111327 | 46682.1 | 64645.3 |  | 0.55688 | 35999.9979 | 28 | 0.0028 | 77.2211 | 2.93 | 74.2911 | -813916 | 4860.7 | 0.0058789 | 0.0041643 | 0.0041643 | 1.608e-06% | 0.0048833 | 17.27%
1 | 21 | 23 | 6 | 111327 | 46709 | 64618.5 |  | 0.55712 | 36000.0002 | 28 | 0.0028 | 77.2156 | 2.9298 | 74.2858 | -813859 | 4860.43 | 0.0058778 | 0.0041631 | 0.0041631 | -9.391e-05% | 0.0048826 | 17.28%
1 | 21 | 24 | 6 | 111327 | 45932.1 | 65395.4 |  | 0.5505 | 36000.0369 | 27 | 0.0026 | 77.2487 | 2.9298 | 74.3189 | -868203 | 4860.54 | 0.0058844 | 0.0040763 | 0.0040763 | -0.0001134% | 0.0048223 | 18.3%
1 | 22 | 1 | 7 | 111224 | 42082 | 69142.2 |  | 0.52067 | 35999.9927 | 27 | 0.0026 | 76.682 | 2.9319 | 73.7501 | -788437 | 4862.36 | 0.005774 | 0.0041214 | 0.0041214 | 0.0001283% | 0.0047467 | 15.17%
1 | 22 | 2 | 7 | 111234 | 41264.7 | 69969.4 |  | 0.51451 | 36000.026 | 27 | 0.0027 | 76.1633 | 2.9342 | 73.2291 | -720543 | 4857.58 | 0.0056743 | 0.004144 | 0.004144 | 0.0001015% | 0.0047117 | 13.7%
1 | 22 | 3 | 7 | 111149 | 40993.1 | 70155.6 |  | 0.51314 | 35999.9954 | 26 | 0.0026 | 76.2796 | 2.9355 | 73.3441 | -753604 | 4859.04 | 0.0056967 | 0.0041077 | 0.0041076 | -3.05e-05% | 0.0046937 | 14.27%
1 | 22 | 4 | 7 | 111082 | 40592.6 | 70489.6 |  | 0.51071 | 35999.9551 | 25 | 0.0025 | 76.3605 | 2.9362 | 73.4243 | -783110 | 4861.12 | 0.0057123 | 0.0040717 | 0.0040717 | 0.0001734% | 0.0046712 | 14.72%
1 | 22 | 5 | 7 | 111091 | 40682.4 | 70408.2 |  | 0.5113 | 35999.9943 | 25 | 0.0026 | 76.4 | 2.935 | 73.4651 | -757903 | 4863.13 | 0.0057198 | 0.0041246 | 0.0041247 | 8.07e-05% | 0.0047088 | 14.16%
1 | 22 | 6 | 7 | 111093 | 40682.8 | 70410.1 |  | 0.51129 | 35999.98 | 25 | 0.0026 | 76.3966 | 2.9349 | 73.4617 | -757623 | 4862.64 | 0.0057192 | 0.0041244 | 0.0041244 | -1.588e-05% | 0.0047084 | 14.16%
1 | 22 | 7 | 7 | 111266 | 42219 | 69046.7 |  | 0.52139 | 35999.9827 | 24 | 0.0023 | 76.6242 | 2.9303 | 73.6939 | -875825 | 4862.66 | 0.0057629 | 0.0039574 | 0.0039574 | -8.139e-05% | 0.0046425 | 17.31%
1 | 22 | 8 | 7 | 111327 | 44302.5 | 67025 |  | 0.53711 | 35999.9988 | 24 | 0.0023 | 77.1493 | 2.9262 | 74.2231 | -921432 | 4868.25 | 0.0058647 | 0.0039501 | 0.0039501 | 6.447e-05% | 0.004712 | 19.29%
1 | 22 | 9 | 7 | 111327 | 44536.6 | 66790.9 |  | 0.539 | 36000.0279 | 24 | 0.0023 | 77.4436 | 2.9158 | 74.5277 | -935101 | 4885.65 | 0.0059032 | 0.0039611 | 0.0039611 | -2.946e-05% | 0.004738 | 19.61%
1 | 22 | 10 | 7 | 111327 | 44234.6 | 67092.8 |  | 0.53657 | 35999.9837 | 25 | 0.0024 | 77.4761 | 2.9261 | 74.55 | -905106 | 4868.36 | 0.0059294 | 0.0040356 | 0.0040356 | -3.915e-06% | 0.0047881 | 18.65%
1 | 22 | 11 | 7 | 111327 | 44012.6 | 67314.8 |  | 0.5348 | 35999.955 | 25 | 0.0023 | 77.5113 | 2.9286 | 74.5827 | -928982 | 4863.61 | 0.0059364 | 0.0039916 | 0.0039916 | -1.694e-05% | 0.0047605 | 19.26%
1 | 22 | 12 | 7 | 111327 | 43677.1 | 67650.4 |  | 0.53215 | 36000.0251 | 25 | 0.0025 | 77.5521 | 2.9291 | 74.623 | -867877 | 4863.17 | 0.0059445 | 0.0041115 | 0.0041115 | 6.862e-05% | 0.0048306 | 17.49%
1 | 22 | 13 | 7 | 111327 | 44467.6 | 66859.9 |  | 0.53844 | 35999.9777 | 26 | 0.0025 | 77.5424 | 2.9296 | 74.6128 | -877156 | 4861.22 | 0.0059425 | 0.0040889 | 0.0040889 | 0.0001856% | 0.0048293 | 18.11%
1 | 22 | 14 | 7 | 111327 | 45222.2 | 66105.2 |  | 0.54459 | 35999.9664 | 27 | 0.0025 | 77.4756 | 2.9304 | 74.5452 | -882976 | 4860.19 | 0.0059293 | 0.0040618 | 0.0040618 | 3.029e-05% | 0.0048204 | 18.68%
1 | 22 | 15 | 7 | 111327 | 44102.4 | 67225.1 |  | 0.53551 | 35999.9822 | 26 | 0.0023 | 77.5026 | 2.931 | 74.5716 | -928790 | 4859.44 | 0.0059346 | 0.0039882 | 0.0039882 | -1.517e-05% | 0.0047593 | 19.33%
1 | 22 | 16 | 7 | 111327 | 44410.2 | 66917.3 |  | 0.53798 | 36000.0352 | 26 | 0.0021 | 77.5363 | 2.9308 | 74.6055 | -994637 | 4860.39 | 0.0059413 | 0.0038748 | 0.0038748 | -6.999e-06% | 0.0046991 | 21.28%
1 | 22 | 17 | 7 | 111327 | 45462.9 | 65864.5 |  | 0.54658 | 36000.0208 | 27 | 0.0023 | 77.4607 | 2.9306 | 74.5301 | -945991 | 4861.74 | 0.0059263 | 0.0039443 | 0.0039443 | -0.0001024% | 0.0047537 | 20.52%
1 | 22 | 18 | 7 | 111327 | 44757.1 | 66570.3 |  | 0.54078 | 35999.9534 | 26 | 0.0022 | 77.4365 | 2.9307 | 74.5058 | -964215 | 4860.98 | 0.0059216 | 0.003909 | 0.003909 | 2.716e-05% | 0.0047181 | 20.7%
1 | 22 | 19 | 7 | 111327 | 44954 | 66373.4 |  | 0.54239 | 36000.0029 | 26 | 0.0023 | 77.4495 | 2.9297 | 74.5198 | -942198 | 4862.88 | 0.0059241 | 0.0039584 | 0.0039585 | 6.633e-05% | 0.0047522 | 20.05%
1 | 22 | 20 | 7 | 111327 | 45417.2 | 65910.2 |  | 0.5462 | 36000.0194 | 26 | 0.0022 | 77.412 | 2.9392 | 74.4728 | -998495 | 4846.78 | 0.0059365 | 0.0038957 | 0.0038956 | -1.732e-05% | 0.0047282 | 21.37%
1 | 22 | 21 | 7 | 111327 | 44693.1 | 66634.3 |  | 0.54026 | 35999.9802 | 25 | 0.0021 | 77.41 | 2.9386 | 74.4714 | -1016910 | 4848.35 | 0.0059362 | 0.0038636 | 0.0038636 | -3.815e-05% | 0.0046957 | 21.53%
1 | 22 | 22 | 7 | 111327 | 44739.8 | 66587.7 |  | 0.54064 | 36000.0407 | 25 | 0.0021 | 77.437 | 2.9377 | 74.4993 | -1019650 | 4850.02 | 0.0059415 | 0.0038646 | 0.0038646 | -8.317e-05% | 0.0046993 | 21.6%
1 | 22 | 23 | 7 | 111327 | 44738.9 | 66588.5 |  | 0.54063 | 36000.0071 | 25 | 0.0022 | 77.434 | 2.9377 | 74.4963 | -989077 | 4849.97 | 0.0059409 | 0.0039185 | 0.0039184 | -8.006e-05% | 0.0047312 | 20.74%
1 | 22 | 24 | 7 | 111327 | 44800.1 | 66527.4 |  | 0.54113 | 36000.0385 | 24 | 0.0022 | 77.4295 | 2.9377 | 74.4918 | -989623 | 4849.57 | 0.00594 | 0.0039162 | 0.0039162 | -1.947e-05% | 0.0047306 | 20.8%
1 | 23 | 1 | 1 | 111039 | 41364.1 | 69674.5 |  | 0.51669 | 36000.0477 | 24 | 0.0021 | 76.8662 | 2.9532 | 73.913 | -942054 | 4836.69 | 0.0058485 | 0.0039117 | 0.0039117 | 1.575e-05% | 0.0046332 | 18.44%
1 | 23 | 2 | 1 | 111062 | 40637.3 | 70424.4 |  | 0.51119 | 36000.0378 | 23 | 0.0019 | 76.3642 | 2.9548 | 73.4094 | -960787 | 4833.14 | 0.0057514 | 0.0037826 | 0.0037826 | -0.0001484% | 0.004503 | 19.04%
1 | 23 | 3 | 1 | 111065 | 40902.6 | 70162.8 |  | 0.51309 | 36000.0415 | 22 | 0.002 | 76.4109 | 2.9619 | 73.449 | -941527 | 4822.5 | 0.0057799 | 0.0038405 | 0.0038405 | 8.114e-07% | 0.0045547 | 18.6%
1 | 23 | 4 | 1 | 111089 | 40974.2 | 70114.7 |  | 0.51345 | 36000.0421 | 22 | 0.0019 | 76.3723 | 2.9594 | 73.4129 | -969416 | 4825.02 | 0.0057724 | 0.0037841 | 0.0037841 | -0.0001096% | 0.0045175 | 19.38%
1 | 23 | 5 | 1 | 111173 | 41339.9 | 69833.4 |  | 0.51551 | 36000.0255 | 26 | 0.0019 | 76.3303 | 2.957 | 73.3733 | -971905 | 4825.84 | 0.0057642 | 0.0037722 | 0.0037722 | -2.121e-05% | 0.0045129 | 19.64%
1 | 23 | 6 | 1 | 115031 | 41030.8 | 74000.5 |  | 0.48648 | 35999.9852 | 26 | 0.002 | 76.291 | 2.8641 | 73.4269 | -909623 | 4815.29 | 0.0057566 | 0.0039291 | 0.0039291 | 0.0002026% | 0.0045809 | 16.59%
1 | 23 | 7 | 1 | 115419 | 42126.9 | 73291.7 |  | 0.49119 | 36000.0035 | 25 | 0.002 | 76.4093 | 2.8685 | 73.5408 | -932899 | 4790.39 | 0.0057992 | 0.003933 | 0.0039331 | 7.907e-05% | 0.0046142 | 17.32%
1 | 23 | 8 | 1 | 115755 | 45298.7 | 70456.3 |  | 0.51096 | 35999.9988 | 26 | 0.002 | 76.9262 | 2.8584 | 74.0678 | -998282 | 4793.29 | 0.0058999 | 0.0039072 | 0.0039072 | 4.925e-05% | 0.004687 | 19.96%
1 | 23 | 9 | 1 | 115645 | 45209.7 | 70435.3 |  | 0.51111 | 36000.0453 | 26 | 0.0019 | 77.1499 | 2.8616 | 74.2883 | -1039710 | 4792.77 | 0.0059443 | 0.0038772 | 0.0038772 | 2.075e-05% | 0.0046853 | 20.84%
1 | 23 | 10 | 1 | 115532 | 44392.4 | 71139.5 |  | 0.50605 | 36000.0017 | 26 | 0.002 | 77.1839 | 2.8653 | 74.3186 | -990561 | 4791.61 | 0.0059511 | 0.0039517 | 0.0039517 | -3.629e-05% | 0.00472 | 19.44%
1 | 23 | 11 | 1 | 115501 | 43594.7 | 71906.4 |  | 0.50065 | 36000.0111 | 24 | 0.0023 | 77.2382 | 2.8669 | 74.3713 | -897255 | 4789.44 | 0.005962 | 0.0041286 | 0.0041286 | -9.628e-05% | 0.0048206 | 16.76%
1 | 23 | 12 | 1 | 115441 | 44017.6 | 71423.9 |  | 0.50403 | 36000.0026 | 25 | 0.0025 | 77.2486 | 2.8757 | 74.3729 | -858568 | 4775.71 | 0.0059844 | 0.0042281 | 0.0042281 | -5.924e-05% | 0.0048978 | 15.84%
1 | 23 | 13 | 1 | 115377 | 43727.8 | 71649.4 |  | 0.50245 | 36000.0261 | 24 | 0.0023 | 77.2429 | 2.8785 | 74.3644 | -901925 | 4772.92 | 0.0059832 | 0.0041326 | 0.0041326 | 5.169e-05% | 0.004834 | 16.97%
1 | 23 | 14 | 1 | 115314 | 43994.2 | 71319.3 |  | 0.50477 | 35999.9857 | 25 | 0.0025 | 77.2495 | 2.8885 | 74.361 | -861512 | 4759.9 | 0.006005 | 0.0042358 | 0.0042358 | -1.692e-05% | 0.0049108 | 15.94%
1 | 23 | 15 | 1 | 115262 | 43742.5 | 71519.6 |  | 0.50336 | 36000.0343 | 25 | 0.0026 | 77.2479 | 2.8911 | 74.3568 | -820428 | 4756.79 | 0.0060047 | 0.0042909 | 0.0042909 | -0.0001457% | 0.0049413 | 15.16%
1 | 23 | 16 | 1 | 115231 | 43843.7 | 71387 |  | 0.50429 | 35999.9644 | 24 | 0.0024 | 77.2518 | 2.8921 | 74.3597 | -874670 | 4755.97 | 0.0060054 | 0.0041872 | 0.0041872 | 4.409e-05% | 0.004879 | 16.52%
1 | 23 | 17 | 1 | 115187 | 44159.6 | 71027.3 |  | 0.50685 | 36000.045 | 25 | 0.0024 | 77.2322 | 2.8914 | 74.3407 | -882184 | 4759.74 | 0.0060015 | 0.0041761 | 0.0041761 | 4.781e-05% | 0.0048759 | 16.76%
1 | 23 | 18 | 1 | 115161 | 44403 | 70757.9 |  | 0.50878 | 35999.9921 | 25 | 0.0026 | 77.2103 | 2.8933 | 74.317 | -835734 | 4757.92 | 0.0059971 | 0.0042687 | 0.0042687 | -2.127e-05% | 0.0049351 | 15.61%
1 | 23 | 19 | 1 | 115180 | 44602.9 | 70576.6 |  | 0.51008 | 35999.9944 | 24 | 0.0025 | 77.1911 | 2.8923 | 74.2988 | -865799 | 4757.86 | 0.0059932 | 0.0042114 | 0.0042114 | -0.0001241% | 0.0049014 | 16.38%
1 | 23 | 20 | 1 | 115106 | 44521.6 | 70584 |  | 0.51003 | 35999.9575 | 24 | 0.0024 | 77.1867 | 2.8923 | 74.2944 | -889775 | 4761.58 | 0.0059923 | 0.0041601 | 0.0041601 | -0.0001363% | 0.0048688 | 17.03%
1 | 23 | 21 | 1 | 111255 | 43934.2 | 67321.1 |  | 0.53475 | 36000.0255 | 24 | 0.0024 | 77.3194 | 2.9923 | 74.3271 | -904708 | 4762.02 | 0.0060191 | 0.0040838 | 0.0040838 | 6.504e-05% | 0.004848 | 18.71%
1 | 23 | 22 | 1 | 111313 | 44731.8 | 66581.4 |  | 0.54069 | 35999.9637 | 24 | 0.0024 | 77.3822 | 2.987 | 74.3952 | -938738 | 4768.68 | 0.0060318 | 0.0040681 | 0.0040681 | -1.868e-05% | 0.0048572 | 19.4%
1 | 23 | 23 | 1 | 111317 | 44658.6 | 66658.4 |  | 0.54007 | 36000.0021 | 25 | 0.0025 | 77.3754 | 2.9861 | 74.3893 | -907747 | 4770.16 | 0.0060304 | 0.0041237 | 0.0041237 | -6.152e-05% | 0.0048887 | 18.55%
1 | 23 | 24 | 1 | 111327 | 44591.6 | 66735.8 |  | 0.53944 | 36000.0267 | 25 | 0.0025 | 77.3885 | 2.9877 | 74.4008 | -905540 | 4766.65 | 0.0060331 | 0.0041272 | 0.0041272 | 6.253e-05% | 0.0048906 | 18.5%
1 | 24 | 1 | 2 | 111137 | 42141.4 | 68995.6 |  | 0.52177 | 36000.0412 | 27 | 0.0028 | 76.7226 | 2.993 | 73.7296 | -749871 | 4766.33 | 0.0059002 | 0.0042826 | 0.0042826 | 5.051e-06% | 0.0048959 | 14.32%
1 | 24 | 2 | 2 | 111161 | 41253.1 | 69908.2 |  | 0.51496 | 35999.9966 | 27 | 0.0027 | 76.1408 | 2.9963 | 73.1445 | -734845 | 4758.75 | 0.005786 | 0.0041969 | 0.0041968 | -5.824e-06% | 0.0047866 | 14.05%
1 | 24 | 3 | 2 | 111254 | 42014.1 | 69240 |  | 0.51993 | 36000.0224 | 28 | 0.0029 | 76.1388 | 2.9826 | 73.1562 | -682755 | 4777.31 | 0.005766 | 0.0042759 | 0.0042759 | 6.907e-05% | 0.0048386 | 13.16%
1 | 24 | 4 | 2 | 111262 | 41934.5 | 69327.7 |  | 0.51927 | 36000.0028 | 28 | 0.003 | 76.067 | 2.9832 | 73.0838 | -648881 | 4775.35 | 0.005752 | 0.0043229 | 0.0043229 | 3.412e-05% | 0.0048615 | 12.46%
1 | 24 | 5 | 2 | 111268 | 41963.8 | 69304.5 |  | 0.51945 | 36000.0146 | 28 | 0.003 | 76.0787 | 2.9828 | 73.0959 | -649778 | 4775.26 | 0.0057542 | 0.0043236 | 0.0043236 | 7.171e-05% | 0.0048631 | 12.48%
1 | 24 | 6 | 2 | 114420 | 41870.1 | 72550.3 |  | 0.49621 | 36000.0393 | 28 | 0.003 | 76.0511 | 2.9007 | 73.1504 | -631725 | 4775.23 | 0.0057488 | 0.0043848 | 0.0043848 | 8.213e-05% | 0.004884 | 11.38%
1 | 24 | 7 | 2 | 115565 | 44268 | 71297 |  | 0.50493 | 35999.9942 | 28 | 0.003 | 76.1469 | 2.8657 | 73.2812 | -654337 | 4785.16 | 0.005748 | 0.0043605 | 0.0043605 | -6.394e-05% | 0.004892 | 12.19%
1 | 24 | 8 | 2 | 115506 | 47018 | 68488.4 |  | 0.52564 | 36000.0371 | 28 | 0.0029 | 76.723 | 2.8661 | 73.8569 | -741048 | 4787.04 | 0.0058603 | 0.0043042 | 0.0043042 | 5.943e-05% | 0.0049376 | 14.72%
1 | 24 | 9 | 2 | 115338 | 47255.2 | 68082.8 |  | 0.52877 | 36000.006 | 28 | 0.0029 | 77.0179 | 2.8693 | 74.1486 | -762060 | 4789.11 | 0.0059178 | 0.0043221 | 0.0043221 | -4.473e-05% | 0.0049759 | 15.13%
1 | 24 | 10 | 2 | 115075 | 46455.7 | 68619.5 |  | 0.52463 | 35999.9855 | 28 | 0.0029 | 77.0394 | 2.8765 | 74.1629 | -747072 | 4787.95 | 0.0059221 | 0.0043366 | 0.0043366 | -3.119e-05% | 0.0049767 | 14.76%
1 | 24 | 11 | 2 | 114998 | 46234 | 68764.3 |  | 0.52353 | 36000.0365 | 28 | 0.0029 | 77.0704 | 2.8791 | 74.1913 | -746591 | 4786.63 | 0.0059284 | 0.0043429 | 0.0043429 | -2.888e-05% | 0.0049803 | 14.68%
1 | 24 | 12 | 2 | 115041 | 47317.6 | 67723.1 |  | 0.53158 | 35999.9746 | 29 | 0.0031 | 77.0372 | 2.8784 | 74.1588 | -704212 | 4786.09 | 0.0059217 | 0.0044218 | 0.0044218 | -7.497e-05% | 0.0050387 | 13.95%
1 | 24 | 13 | 2 | 114934 | 47051.5 | 67882.6 |  | 0.53033 | 35999.9756 | 29 | 0.0031 | 77.0067 | 2.8718 | 74.1349 | -688832 | 4800.89 | 0.0058956 | 0.004413 | 0.004413 | 5.746e-05% | 0.00502 | 13.75%
1 | 24 | 14 | 2 | 115068 | 47592.6 | 67475.8 |  | 0.53353 | 36000.0262 | 29 | 0.0031 | 76.9924 | 2.8684 | 74.124 | -700892 | 4801.01 | 0.0058928 | 0.0044028 | 0.0044028 | -8.984e-05% | 0.0050191 | 14%
1 | 24 | 15 | 2 | 115062 | 47656 | 67406 |  | 0.53408 | 35999.9943 | 29 | 0.0031 | 76.9725 | 2.868 | 74.1045 | -692650 | 4801.99 | 0.0058889 | 0.0043994 | 0.0043994 | -7.655e-05% | 0.0050163 | 14.02%
1 | 24 | 16 | 2 | 114964 | 46664.4 | 68299.2 |  | 0.52709 | 36000.0302 | 28 | 0.003 | 77.006 | 2.8703 | 74.1357 | -711677 | 4802.29 | 0.0058955 | 0.0043693 | 0.0043693 | 6.318e-05% | 0.0049888 | 14.18%
1 | 24 | 17 | 2 | 115022 | 46991 | 68030.7 |  | 0.52917 | 36000.0096 | 28 | 0.0027 | 77.0118 | 2.8587 | 74.1531 | -805598 | 4819.53 | 0.0058768 | 0.0041957 | 0.0041957 | 7.659e-05% | 0.0048825 | 16.37%
1 | 24 | 18 | 2 | 114992 | 45602.3 | 69389.7 |  | 0.51881 | 36000.0009 | 26 | 0.0022 | 77.0436 | 2.8592 | 74.1844 | -949323 | 4821.58 | 0.0058831 | 0.0039723 | 0.0039723 | -2.498e-05% | 0.0047301 | 19.08%
1 | 24 | 19 | 2 | 114946 | 44892.5 | 70053.3 |  | 0.51389 | 36000.0406 | 24 | 0.0018 | 77.1029 | 2.8587 | 74.2442 | -1062330 | 4826.19 | 0.0058949 | 0.0037906 | 0.0037906 | 2.133e-05% | 0.0046124 | 21.68%
1 | 24 | 20 | 2 | 114982 | 45133.9 | 69848.5 |  | 0.5154 | 35999.9867 | 21 | 0.0016 | 77.1114 | 2.8556 | 74.2559 | -1120950 | 4831.64 | 0.0058966 | 0.0036821 | 0.0036821 | 7.065e-05% | 0.0045514 | 23.61%
1 | 24 | 21 | 2 | 111308 | 44575.6 | 66732.8 |  | 0.53946 | 36000.01 | 22 | 0.0016 | 77.1982 | 2.9346 | 74.2636 | -1135980 | 4857.71 | 0.0058941 | 0.0035776 | 0.0035776 | -0.0001861% | 0.0045053 | 25.93%
1 | 24 | 22 | 2 | 111320 | 45406 | 65913.6 |  | 0.54617 | 36000.0309 | 20 | 0.0015 | 77.2281 | 2.9319 | 74.2962 | -1206400 | 4862.58 | 0.0059 | 0.0034969 | 0.0034969 | -0.0001254% | 0.0044771 | 28.03%
1 | 24 | 23 | 2 | 111322 | 45703.6 | 65618.2 |  | 0.54863 | 36000.0474 | 18 | 0.0012 | 77.1842 | 2.927 | 74.2572 | -1304530 | 4871.28 | 0.0058913 | 0.0033175 | 0.0033175 | -0.0001266% | 0.0043742 | 31.85%
1 | 24 | 24 | 2 | 111327 | 45912.6 | 65414.8 |  | 0.55033 | 35999.9885 | 17 | 0.0011 | 77.1531 | 2.9225 | 74.2306 | -1338720 | 4880.08 | 0.0058851 | 0.0032517 | 0.0032517 | 8.198e-06% | 0.0043378 | 33.4%
1 | 25 | 1 | 3 | 111162 | 42349.4 | 68812.3 |  | 0.52316 | 35999.9805 | 15 | 0.001 | 76.5168 | 2.9245 | 73.5923 | -1265060 | 4884.59 | 0.0057615 | 0.0032705 | 0.0032705 | 9.817e-05% | 0.0042195 | 29.02%
1 | 25 | 2 | 3 | 111215 | 41777.1 | 69437.4 |  | 0.51845 | 35999.9589 | 13 | 0.001 | 75.9351 | 2.9224 | 73.0127 | -1221810 | 4885.6 | 0.0056498 | 0.0032391 | 0.0032391 | -6.752e-05% | 0.0041446 | 27.96%
1 | 25 | 3 | 3 | 111245 | 42354 | 68890.5 |  | 0.52257 | 35999.9708 | 7 | 0.0007 | 75.9083 | 2.9168 | 72.9915 | -1321480 | 4893.98 | 0.0056447 | 0.0030608 | 0.0030608 | 7.623e-05% | 0.0040446 | 32.14%
1 | 25 | 4 | 3 | 111309 | 42832 | 68477.1 |  | 0.52572 | 35999.9864 | 4 | 0.0007 | 75.7608 | 2.8939 | 72.8669 | -1327600 | 4931.52 | 0.0055984 | 0.0030232 | 0.0030232 | 0.0001569% | 0.0040141 | 32.78%
1 | 25 | 5 | 3 | 111309 | 43206.9 | 68102.1 |  | 0.52862 | 35999.9959 | 1 | 0.0006 | 75.6485 | 2.8869 | 72.7616 | -1362510 | 4943.81 | 0.0055774 | 0.0029463 | 0.0029463 | 6.968e-05% | 0.0039676 | 34.67%
1 | 25 | 6 | 3 | 113825 | 43323.5 | 70501.8 |  | 0.51062 | 35999.9816 | 0 | 0.0006 | 75.5432 | 2.8166 | 72.7266 | -1333980 | 4955.86 | 0.0055577 | 0.0030262 | 0.0030262 | 0.0001326% | 0.0039897 | 31.84%
1 | 25 | 7 | 3 | 116026 | 46943.8 | 69082 |  | 0.52112 | 36000.0118 | 0 | 0.0005 | 75.7023 | 2.7652 | 72.9371 | -1433740 | 4951.47 | 0.0055874 | 0.0029363 | 0.0029363 | 0.0001257% | 0.0040089 | 36.53%
1 | 25 | 8 | 3 | 116393 | 52803 | 63590.1 |  | 0.56613 | 36000.009 | -2 | 0.0005 | 76.3021 | 2.7456 | 73.5565 | -1593690 | 4972 | 0.0056821 | 0.0027484 | 0.0027484 | -0.0001178% | 0.0040793 | 48.43%
1 | 25 | 9 | 3 | 115106 | 47605.9 | 67499.7 |  | 0.53334 | 36000.02 | 0 | 0.0005 | 76.7331 | 2.7637 | 73.9694 | -1518880 | 4996.41 | 0.0057646 | 0.0029568 | 0.0029568 | -2.386e-05% | 0.0041181 | 39.27%
1 | 25 | 10 | 3 | 114859 | 45728.1 | 69131.3 |  | 0.52075 | 35999.9862 | 2 | 0.0005 | 76.9597 | 2.7826 | 74.1771 | -1469890 | 4971.17 | 0.005808 | 0.0030439 | 0.0030439 | 0.0001448% | 0.0041443 | 36.15%
1 | 25 | 11 | 3 | 115160 | 44489.7 | 70670 |  | 0.50941 | 36000.0047 | 4 | 0.0006 | 77.0732 | 2.7829 | 74.2903 | -1413910 | 4956.88 | 0.0058302 | 0.0031659 | 0.0031659 | -2.842e-05% | 0.0041952 | 32.51%
1 | 25 | 12 | 3 | 115460 | 44308.2 | 71151.5 |  | 0.50596 | 35999.9552 | 5 | 0.0007 | 77.1103 | 2.7822 | 74.3281 | -1390780 | 4944.12 | 0.0058375 | 0.0032381 | 0.0032381 | 0.0001632% | 0.0042356 | 30.81%
1 | 25 | 13 | 3 | 115579 | 43652.4 | 71926.7 |  | 0.50051 | 36000.0326 | 5 | 0.0006 | 77.1371 | 2.782 | 74.3551 | -1392330 | 4938.73 | 0.0058428 | 0.0032187 | 0.0032187 | -0.0001186% | 0.0042098 | 30.79%
1 | 25 | 14 | 3 | 115507 | 43846.1 | 71660.8 |  | 0.50237 | 36000.0211 | 6 | 0.0007 | 77.1534 | 2.7852 | 74.3682 | -1381650 | 4936.4 | 0.005846 | 0.0032608 | 0.0032608 | -1.64e-05% | 0.0042421 | 30.09%
1 | 25 | 15 | 3 | 115385 | 43550.5 | 71834.5 |  | 0.50115 | 36000.0033 | 6 | 0.0007 | 77.1621 | 2.7894 | 74.3727 | -1362470 | 4933.75 | 0.0058477 | 0.0032679 | 0.0032679 | -4.602e-06% | 0.0042416 | 29.8%
1 | 25 | 16 | 3 | 115119 | 44067.8 | 71051.3 |  | 0.50668 | 35999.9885 | 4 | 0.0007 | 77.1674 | 2.7961 | 74.3713 | -1368920 | 4933.12 | 0.0058487 | 0.00324 | 0.00324 | -9.223e-05% | 0.0042386 | 30.82%
1 | 25 | 17 | 3 | 114895 | 46219 | 68675.5 |  | 0.5242 | 35999.9718 | 1 | 0.0005 | 77.0632 | 2.7971 | 74.2661 | -1476520 | 4941.41 | 0.0058282 | 0.0030351 | 0.0030351 | 4.907e-05% | 0.0041587 | 37.02%
1 | 25 | 18 | 3 | 115442 | 48526.8 | 66915.2 |  | 0.538 | 36000.043 | -1 | 0.0005 | 76.8715 | 2.7651 | 74.1064 | -1532380 | 4976.71 | 0.0057719 | 0.0029356 | 0.0029356 | -1.569e-05% | 0.0041279 | 40.61%
1 | 25 | 19 | 3 | 115613 | 49284.4 | 66328.6 |  | 0.54275 | 35999.9803 | -2 | 0.0005 | 76.7758 | 2.7532 | 74.0226 | -1547490 | 4991.78 | 0.0057536 | 0.0029022 | 0.0029022 | 9.184e-05% | 0.0041177 | 41.88%
1 | 25 | 20 | 3 | 115548 | 49211.4 | 66336.5 |  | 0.54269 | 35999.9562 | -3 | 0.0004 | 76.7578 | 2.7513 | 74.0065 | -1571930 | 4998.32 | 0.0057502 | 0.0028467 | 0.0028467 | 0.0002412% | 0.0040833 | 43.44%
1 | 25 | 21 | 3 | 111327 | 47448.3 | 63879.1 |  | 0.56356 | 35999.9611 | -5 | 0.0004 | 76.8269 | 2.8536 | 73.9733 | -1570340 | 5002.22 | 0.0057634 | 0.0027408 | 0.0027408 | 0.0002827% | 0.004029 | 47%
1 | 25 | 22 | 3 | 111327 | 48440.9 | 62886.6 |  | 0.57246 | 36000.0001 | -7 | 0.0003 | 76.7628 | 2.8445 | 73.9183 | -1660390 | 5019.17 | 0.0057511 | 0.0026306 | 0.0026306 | 5.973e-05% | 0.0039884 | 51.62%
1 | 25 | 23 | 3 | 111327 | 48375 | 62952.4 |  | 0.57186 | 36000.0224 | -6 | 0.0004 | 76.719 | 2.8379 | 73.8811 | -1627150 | 5032 | 0.0057428 | 0.0026875 | 0.0026874 | -6.679e-05% | 0.0040151 | 49.4%
1 | 25 | 24 | 3 | 111327 | 48930.8 | 62396.6 |  | 0.57695 | 35999.968 | -8 | 0.0003 | 76.6861 | 2.8396 | 73.8465 | -1669670 | 5028.33 | 0.0057365 | 0.0025999 | 0.0025999 | -1.619e-05% | 0.0039785 | 53.03%
1 | 26 | 1 | 4 | 111315 | 44332.3 | 66983 |  | 0.53745 | 36000.0134 | -9 | 0.0004 | 75.9483 | 2.8346 | 73.1137 | -1483250 | 5038.66 | 0.0055959 | 0.0028034 | 0.0028034 | -9.198e-05% | 0.0039155 | 39.67%
1 | 26 | 2 | 4 | 111309 | 44070.6 | 67238.3 |  | 0.53541 | 35999.991 | -9 | 0.0003 | 75.2738 | 2.841 | 72.4328 | -1465550 | 5025.64 | 0.0054709 | 0.0027024 | 0.0027024 | -9.104e-05% | 0.0037985 | 40.56%
1 | 26 | 3 | 4 | 111309 | 44697.5 | 66611.5 |  | 0.54045 | 35999.9853 | -11 | 0.0003 | 75.2187 | 2.8393 | 72.3794 | -1477440 | 5029.68 | 0.0054607 | 0.0026716 | 0.0026716 | -8.885e-06% | 0.0037916 | 41.92%
1 | 26 | 4 | 4 | 111309 | 45073.1 | 66235.8 |  | 0.54351 | 36000.0184 | -11 | 0.0003 | 75.0912 | 2.8339 | 72.2573 | -1481490 | 5039.43 | 0.0054371 | 0.002645 | 0.002645 | -2.391e-05% | 0.0037756 | 42.75%
1 | 26 | 5 | 4 | 111309 | 45591 | 65717.9 |  | 0.5478 | 36000.0027 | -12 | 0.0003 | 74.9812 | 2.8325 | 72.1487 | -1487600 | 5042.26 | 0.0054168 | 0.0026139 | 0.0026138 | -0.000135% | 0.0037619 | 43.92%
1 | 26 | 6 | 4 | 113539 | 45571.8 | 67966.8 |  | 0.52967 | 35999.975 | -15 | 0.0003 | 74.9166 | 2.7734 | 72.1432 | -1455150 | 5048.83 | 0.0054052 | 0.0027011 | 0.0027011 | -2.557e-05% | 0.0037865 | 40.18%
1 | 26 | 7 | 4 | 116657 | 53727.7 | 62929.6 |  | 0.57207 | 36000.0104 | -13 | 0.0003 | 75.0137 | 2.6987 | 72.315 | -1629210 | 5049.02 | 0.0054227 | 0.0024922 | 0.0024922 | -0.0002258% | 0.0038419 | 54.16%
1 | 26 | 8 | 4 | 118080 | 65832.3 | 52247.9 |  | 0.68902 | 36000.0048 | -14 | 0.0003 | 75.4257 | 2.6587 | 72.767 | -2015910 | 5065.88 | 0.0054991 | 0.0019168 | 0.0019168 | 6.216e-05% | 0.003914 | 104.2%
1 | 26 | 9 | 4 | 115995 | 58338.4 | 57656.9 |  | 0.62438 | 35999.9882 | -11 | 0.0004 | 75.8906 | 2.6723 | 73.2183 | -1816190 | 5135.42 | 0.0055852 | 0.0023477 | 0.0023477 | 0.0001829% | 0.003976 | 69.36%
1 | 26 | 10 | 4 | 114910 | 49577.3 | 65332.7 |  | 0.55103 | 36000.0164 | -6 | 0.0005 | 76.4779 | 2.7229 | 73.755 | -1558040 | 5083.57 | 0.0056967 | 0.0028332 | 0.0028332 | -0.0001181% | 0.0040687 | 43.61%
1 | 26 | 11 | 4 | 115319 | 45566.5 | 69752.5 |  | 0.51611 | 35999.9628 | -6 | 0.0004 | 76.9063 | 2.7544 | 74.1519 | -1500320 | 5003.1 | 0.0057978 | 0.0030119 | 0.0030119 | 5.857e-05% | 0.0041127 | 36.55%
1 | 26 | 12 | 4 | 115619 | 45753.9 | 69865.3 |  | 0.51528 | 35999.9822 | -3 | 0.0005 | 77.0156 | 2.7589 | 74.2567 | -1485430 | 4980.49 | 0.0058188 | 0.0030781 | 0.0030781 | -1.496e-05% | 0.0041627 | 35.23%
1 | 26 | 13 | 4 | 115728 | 44686.9 | 71041.3 |  | 0.50675 | 35999.9657 | -1 | 0.0005 | 77.0473 | 2.7622 | 74.2852 | -1445670 | 4969.27 | 0.0058251 | 0.0031266 | 0.0031266 | 0.000216% | 0.0041686 | 33.33%
1 | 26 | 14 | 4 | 115711 | 44393.3 | 71318 |  | 0.50478 | 35999.9714 | 1 | 0.0005 | 77.0906 | 2.7683 | 74.3223 | -1453790 | 4958.58 | 0.0058336 | 0.0031413 | 0.0031413 | 0.0001595% | 0.0041742 | 32.88%
1 | 26 | 15 | 4 | 115515 | 43827.1 | 71687.8 |  | 0.50218 | 35999.9643 | 2 | 0.0005 | 77.1293 | 2.777 | 74.3523 | -1429030 | 4951.18 | 0.0058412 | 0.003159 | 0.003159 | 6.713e-05% | 0.0041767 | 32.21%
1 | 26 | 16 | 4 | 115159 | 44374.1 | 70785.2 |  | 0.50858 | 36000.0078 | 1 | 0.0005 | 77.1526 | 2.7973 | 74.3553 | -1437470 | 4930.27 | 0.0058654 | 0.0031366 | 0.0031366 | -0.0001671% | 0.0041881 | 33.52%
1 | 26 | 17 | 4 | 114908 | 46587.9 | 68320.3 |  | 0.52693 | 36000.0157 | -1 | 0.0005 | 77.0468 | 2.8005 | 74.2463 | -1487430 | 4935.62 | 0.0058444 | 0.0030283 | 0.0030283 | 0.0001397% | 0.0041701 | 37.7%
1 | 26 | 18 | 4 | 115462 | 48755.6 | 66706.8 |  | 0.53968 | 36000.059 | -2 | 0.0005 | 76.8696 | 2.7788 | 74.0908 | -1541020 | 4951.36 | 0.0058101 | 0.0029444 | 0.0029444 | 3.653e-05% | 0.0041545 | 41.1%
1 | 26 | 19 | 4 | 115643 | 49433.8 | 66208.8 |  | 0.54373 | 35999.9757 | -4 | 0.0004 | 76.7817 | 2.7687 | 74.013 | -1585640 | 4962.33 | 0.0057932 | 0.0028607 | 0.0028607 | 0.0001325% | 0.0041143 | 43.82%
1 | 26 | 20 | 4 | 115605 | 49472.1 | 66132.4 |  | 0.54436 | 35999.9655 | -4 | 0.0005 | 76.7686 | 2.7741 | 73.9945 | -1549730 | 4955.09 | 0.0058101 | 0.0029195 | 0.0029195 | -7.192e-05% | 0.0041565 | 42.37%
1 | 26 | 21 | 4 | 111327 | 47540.5 | 63786.9 |  | 0.56438 | 35999.9868 | -5 | 0.0004 | 76.8315 | 2.8799 | 73.9516 | -1575390 | 4955.89 | 0.0058222 | 0.002762 | 0.002762 | 5.833e-05% | 0.0040688 | 47.31%
1 | 26 | 22 | 4 | 111327 | 49139.4 | 62188 |  | 0.57889 | 36000.0113 | -10 | 0.0003 | 76.7226 | 2.8732 | 73.8494 | -1677350 | 4968.86 | 0.0058012 | 0.0026166 | 0.0026166 | -0.0001079% | 0.0040223 | 53.72%
1 | 26 | 23 | 4 | 111327 | 48847 | 62480.4 |  | 0.57618 | 36000.0194 | -7 | 0.0004 | 76.6578 | 2.8684 | 73.7894 | -1642130 | 4978.56 | 0.0058082 | 0.0026921 | 0.0026921 | -0.000134% | 0.0040594 | 50.79%
1 | 26 | 24 | 4 | 111327 | 49457 | 61870.5 |  | 0.58186 | 36000.031 | -9 | 0.0003 | 76.6406 | 2.8748 | 73.7659 | -1684240 | 4966.86 | 0.0058049 | 0.0026018 | 0.0026018 | -3.076e-05% | 0.0040248 | 54.69%
1 | 27 | 1 | 5 | 111315 | 44381.6 | 66933.8 |  | 0.53785 | 36000.0097 | -10 | 0.0003 | 75.9093 | 2.8696 | 73.0397 | -1516500 | 4977.15 | 0.0056639 | 0.002779 | 0.002779 | -7.823e-05% | 0.0039292 | 41.39%
1 | 27 | 2 | 5 | 111309 | 44332.2 | 66976.7 |  | 0.5375 | 35999.9762 | -10 | 0.0003 | 75.2236 | 2.8775 | 72.3461 | -1470630 | 4962.08 | 0.0055351 | 0.0027212 | 0.0027212 | -3.215e-05% | 0.0038419 | 41.18%
1 | 27 | 3 | 5 | 111309 | 43730.6 | 67578.2 |  | 0.53272 | 35999.9884 | -8 | 0.0004 | 75.3061 | 2.8849 | 72.4212 | -1433570 | 4950.03 | 0.0055693 | 0.0028155 | 0.0028155 | -0.0001473% | 0.0038974 | 38.43%
1 | 27 | 4 | 5 | 111309 | 43892.4 | 67416.4 |  | 0.53399 | 36000.0205 | -8 | 0.0004 | 75.3582 | 2.8903 | 72.4679 | -1436750 | 4939.82 | 0.0055791 | 0.0028135 | 0.0028135 | -0.0001729% | 0.0039041 | 38.76%
1 | 27 | 5 | 5 | 111309 | 43944.3 | 67364.5 |  | 0.53441 | 35999.993 | -8 | 0.0004 | 75.3265 | 2.8903 | 72.4362 | -1436060 | 4939.92 | 0.0055732 | 0.0028086 | 0.0028086 | 8.036e-05% | 0.0039 | 38.86%
1 | 27 | 6 | 5 | 113644 | 43970.5 | 69673.8 |  | 0.51669 | 36000.0344 | -9 | 0.0003 | 75.3137 | 2.8401 | 72.4736 | -1437200 | 4923.84 | 0.0055896 | 0.0028565 | 0.0028565 | 0.000178% | 0.003914 | 37.02%
1 | 27 | 7 | 5 | 116439 | 50044.2 | 66395.1 |  | 0.54221 | 36000.0208 | -8 | 0.0004 | 75.4449 | 2.7751 | 72.6698 | -1526800 | 4917.83 | 0.0056144 | 0.0027871 | 0.0027871 | -3.143e-05% | 0.0040023 | 43.6%
1 | 27 | 8 | 5 | 116885 | 57245.5 | 59639.2 |  | 0.60363 | 36000.0103 | -5 | 0.0005 | 76.0232 | 2.76 | 73.2632 | -1704300 | 4926.51 | 0.0057239 | 0.0025706 | 0.0025706 | -3.368e-05% | 0.004115 | 60.08%
1 | 27 | 9 | 5 | 115594 | 49536.9 | 66057.1 |  | 0.54498 | 35999.9965 | -4 | 0.0005 | 76.5629 | 2.7823 | 73.7806 | -1561280 | 4943.57 | 0.0058291 | 0.0029248 | 0.0029248 | -8.738e-05% | 0.0041694 | 42.55%
1 | 27 | 10 | 5 | 114951 | 46619 | 68331.5 |  | 0.52684 | 35999.9725 | -4 | 0.0005 | 76.9134 | 2.8168 | 74.0966 | -1494410 | 4907.22 | 0.0058974 | 0.0030538 | 0.0030538 | 0.0001112% | 0.004207 | 37.76%
1 | 27 | 11 | 5 | 115427 | 45267 | 70160 |  | 0.51311 | 36000.0081 | -2 | 0.0005 | 77.0546 | 2.821 | 74.2336 | -1466310 | 4878.57 | 0.0059453 | 0.0031513 | 0.0031513 | 1.23e-05% | 0.004247 | 34.77%
1 | 27 | 12 | 5 | 115808 | 44928.8 | 70879 |  | 0.50791 | 36000.0111 | 0 | 0.0005 | 77.1119 | 2.829 | 74.2829 | -1470370 | 4847.86 | 0.0059772 | 0.0031953 | 0.0031953 | 4.324e-05% | 0.0042746 | 33.78%
1 | 27 | 13 | 5 | 115730 | 43988.9 | 71741.6 |  | 0.5018 | 36000.0066 | 2 | 0.0006 | 77.1578 | 2.8361 | 74.3217 | -1407850 | 4838.53 | 0.0059864 | 0.0032835 | 0.0032835 | 0.0001219% | 0.0043109 | 31.29%
1 | 27 | 14 | 5 | 115259 | 44356.9 | 70901.8 |  | 0.50774 | 35999.9635 | 4 | 0.0007 | 77.1857 | 2.8528 | 74.3329 | -1402720 | 4829.1 | 0.0059921 | 0.0033051 | 0.0033051 | 9.244e-05% | 0.0043392 | 31.29%
1 | 27 | 15 | 5 | 114861 | 44482.7 | 70378.8 |  | 0.51152 | 36000.023 | 5 | 0.0007 | 77.1908 | 2.8746 | 74.3162 | -1393710 | 4809.01 | 0.0060136 | 0.0032956 | 0.0032956 | 7.919e-05% | 0.0043482 | 31.94%
1 | 27 | 16 | 5 | 114715 | 45563.5 | 69151.7 |  | 0.52059 | 35999.9601 | 5 | 0.0007 | 77.14 | 2.8793 | 74.2607 | -1407410 | 4807.34 | 0.0060033 | 0.0032425 | 0.0032424 | -5.484e-05% | 0.004339 | 33.82%
1 | 27 | 17 | 5 | 115065 | 46901.5 | 68163.4 |  | 0.52814 | 35999.9544 | 4 | 0.0008 | 77.0331 | 2.8682 | 74.1649 | -1402930 | 4811.61 | 0.0059817 | 0.003245 | 0.003245 | 7.528e-05% | 0.0043605 | 34.38%
1 | 27 | 18 | 5 | 115287 | 47702.2 | 67585 |  | 0.53266 | 36000.0289 | 5 | 0.0008 | 76.961 | 2.8587 | 74.1023 | -1430180 | 4818.28 | 0.0059673 | 0.0032149 | 0.0032149 | 3.525e-05% | 0.0043537 | 35.42%
1 | 27 | 19 | 5 | 115330 | 47802.3 | 67527.4 |  | 0.53312 | 36000.0049 | 6 | 0.0009 | 76.9374 | 2.8581 | 74.0793 | -1399790 | 4817.89 | 0.0059626 | 0.0032637 | 0.0032637 | 1.689e-05% | 0.0043823 | 34.28%
1 | 27 | 20 | 5 | 115276 | 47586.9 | 67689.2 |  | 0.53184 | 36000.0272 | 4 | 0.0008 | 76.9443 | 2.861 | 74.0833 | -1418450 | 4814.82 | 0.005964 | 0.0032176 | 0.0032176 | -6.009e-05% | 0.0043513 | 35.24%
1 | 27 | 21 | 5 | 111327 | 46276.2 | 65051.3 |  | 0.55341 | 36000.0399 | 5 | 0.0008 | 77.0243 | 2.9591 | 74.0652 | -1424810 | 4820.6 | 0.0059799 | 0.0031133 | 0.0031133 | -9.395e-05% | 0.0043049 | 38.27%
1 | 27 | 22 | 5 | 111327 | 47159.1 | 64168.3 |  | 0.56102 | 35999.9563 | 4 | 0.0007 | 76.9923 | 2.9561 | 74.0362 | -1503140 | 4826.48 | 0.0059735 | 0.0030149 | 0.0030149 | 7.884e-05% | 0.0042682 | 41.57%
1 | 27 | 23 | 5 | 111327 | 47407 | 63920.5 |  | 0.5632 | 36000.0256 | 4 | 0.0007 | 76.9426 | 2.9522 | 73.9904 | -1508380 | 4833.73 | 0.0059637 | 0.0029992 | 0.0029992 | -0.0001104% | 0.0042615 | 42.09%
1 | 27 | 24 | 5 | 111327 | 47436.4 | 63891 |  | 0.56346 | 35999.959 | 4 | 0.0007 | 76.921 | 2.9514 | 73.9696 | -1506240 | 4835.15 | 0.0059594 | 0.0029959 | 0.0029959 | 0.0001247% | 0.0042587 | 42.15%
1 | 28 | 1 | 6 | 111315 | 43421.9 | 67893.1 |  | 0.53024 | 35999.9768 | 3 | 0.0007 | 76.2376 | 2.9516 | 73.286 | -1377450 | 4835.44 | 0.0058249 | 0.0031074 | 0.0031074 | -6.422e-05% | 0.0041675 | 34.11%
1 | 28 | 2 | 6 | 111309 | 42741.3 | 68567.7 |  | 0.52503 | 36000.031 | 1 | 0.0006 | 75.6199 | 2.9553 | 72.6646 | -1356010 | 4828.65 | 0.0057055 | 0.003025 | 0.003025 | 0.0001633% | 0.0040542 | 34.03%
1 | 28 | 3 | 6 | 111309 | 43103.9 | 68205 |  | 0.52782 | 36000.0313 | 1 | 0.0006 | 75.636 | 2.9407 | 72.6953 | -1366100 | 4853.43 | 0.0056891 | 0.003003 | 0.003003 | -0.0001282% | 0.0040432 | 34.64%
1 | 28 | 4 | 6 | 111309 | 43114.3 | 68194.5 |  | 0.5279 | 36000.0129 | 2 | 0.0006 | 75.5978 | 2.9398 | 72.658 | -1364660 | 4855.08 | 0.0056818 | 0.0029991 | 0.0029991 | 5.933e-05% | 0.0040382 | 34.65%
1 | 28 | 5 | 6 | 111309 | 43137.9 | 68170.9 |  | 0.52808 | 35999.9616 | 1 | 0.0006 | 75.5953 | 2.9414 | 72.6539 | -1364160 | 4852.4 | 0.0056813 | 0.002998 | 0.002998 | 1.223e-05% | 0.0040379 | 34.69%
1 | 28 | 6 | 6 | 111309 | 43327.2 | 67981.7 |  | 0.52955 | 36000.0491 | 0 | 0.0006 | 75.5637 | 2.9396 | 72.6241 | -1367120 | 4855.47 | 0.0056753 | 0.0029877 | 0.0029877 | -0.0002135% | 0.0040338 | 35.02%
1 | 28 | 7 | 6 | 111327 | 45323.6 | 66003.8 |  | 0.54542 | 35999.9906 | -1 | 0.0005 | 75.8131 | 2.9367 | 72.8764 | -1456730 | 4859.45 | 0.0057228 | 0.0028742 | 0.0028742 | 0.0001339% | 0.0040339 | 40.35%
1 | 28 | 8 | 6 | 111327 | 51076.5 | 60250.9 |  | 0.5975 | 35999.973 | -1 | 0.0005 | 76.3225 | 2.9318 | 73.3907 | -1610270 | 4868.63 | 0.0058217 | 0.002642 | 0.002642 | 3.324e-05% | 0.0041008 | 55.22%
1 | 28 | 9 | 6 | 111327 | 46234 | 65093.4 |  | 0.55305 | 36000.0351 | -1 | 0.0005 | 76.8282 | 2.9202 | 73.908 | -1520630 | 4889.94 | 0.0059209 | 0.0029228 | 0.0029229 | 5.044e-05% | 0.0041679 | 42.6%
1 | 28 | 10 | 6 | 111327 | 45733.1 | 65594.4 |  | 0.54883 | 36000.0434 | 1 | 0.0006 | 77.1652 | 2.9333 | 74.2319 | -1490750 | 4865.63 | 0.0059879 | 0.0030309 | 0.0030309 | -7.702e-05% | 0.0042456 | 40.08%
1 | 28 | 11 | 6 | 111327 | 44307.6 | 67019.8 |  | 0.53716 | 36000.0207 | 1 | 0.0005 | 77.3138 | 2.9397 | 74.3741 | -1488060 | 4854.09 | 0.006018 | 0.003054 | 0.003054 | -0.0001695% | 0.0042336 | 38.63%
1 | 28 | 12 | 6 | 111327 | 43710.8 | 67616.6 |  | 0.53241 | 36000.0245 | 2 | 0.0006 | 77.4437 | 2.9434 | 74.5003 | -1451220 | 4847.83 | 0.0060442 | 0.0031456 | 0.0031456 | 3.347e-05% | 0.0042837 | 36.18%
1 | 28 | 13 | 6 | 111327 | 43700.1 | 67627.4 |  | 0.53233 | 36000.0262 | 2 | 0.0006 | 77.4736 | 2.947 | 74.5266 | -1450560 | 4841.14 | 0.0060503 | 0.0031489 | 0.0031489 | 0.0001228% | 0.0042878 | 36.17%
1 | 28 | 14 | 6 | 111327 | 43964.9 | 67362.6 |  | 0.53442 | 36000.0554 | 1 | 0.0006 | 77.4592 | 2.9472 | 74.512 | -1455290 | 4840.79 | 0.0060473 | 0.0031362 | 0.0031362 | -0.0002658% | 0.0042858 | 36.66%
1 | 28 | 15 | 6 | 111327 | 44566 | 66761.4 |  | 0.53923 | 36000.0168 | 1 | 0.0006 | 77.4016 | 2.9348 | 74.4668 | -1465650 | 4861.25 | 0.0060152 | 0.0030951 | 0.0030951 | -0.0001475% | 0.0042641 | 37.77%
1 | 28 | 16 | 6 | 111327 | 45716.9 | 65610.5 |  | 0.54869 | 36000.0221 | 1 | 0.0006 | 77.2989 | 2.9332 | 74.3657 | -1486140 | 4864.36 | 0.0059945 | 0.0030346 | 0.0030346 | -0.0001446% | 0.0042501 | 40.05%
1 | 28 | 17 | 6 | 111327 | 46748.3 | 64579.1 |  | 0.55746 | 36000.0068 | 0 | 0.0006 | 77.1559 | 2.9304 | 74.2255 | -1502800 | 4869.56 | 0.0059657 | 0.0029746 | 0.0029746 | -9.441e-05% | 0.0042306 | 42.23%
1 | 28 | 18 | 6 | 111327 | 47080.9 | 64246.6 |  | 0.56034 | 36000.0041 | 0 | 0.0005 | 77.06 | 2.9256 | 74.1344 | -1538490 | 4877.96 | 0.0059464 | 0.0028946 | 0.0028946 | -8.392e-05% | 0.0041852 | 44.59%
1 | 28 | 19 | 6 | 111327 | 47237.7 | 64089.7 |  | 0.56171 | 36000.0177 | 1 | 0.0006 | 77.0251 | 2.9245 | 74.1006 | -1515770 | 4880.59 | 0.0059394 | 0.0029402 | 0.0029402 | -0.0001624% | 0.0042128 | 43.28%
1 | 28 | 20 | 6 | 111327 | 47865.8 | 63461.6 |  | 0.56727 | 35999.9888 | 1 | 0.0006 | 76.966 | 2.9259 | 74.0401 | -1555040 | 4877.85 | 0.0059277 | 0.0029054 | 0.0029054 | 2.197e-05% | 0.0042049 | 44.72%
1 | 28 | 21 | 6 | 111327 | 47904.3 | 63423.1 |  | 0.56762 | 36000.0298 | 1 | 0.0006 | 76.9137 | 2.9243 | 73.9894 | -1551760 | 4880.81 | 0.0059175 | 0.0028992 | 0.0028992 | -0.0002197% | 0.0041979 | 44.8%
1 | 28 | 22 | 6 | 111327 | 47942.3 | 63385.1 |  | 0.56796 | 36000.0112 | 1 | 0.0006 | 76.9056 | 2.924 | 73.9816 | -1552380 | 4881.38 | 0.0059159 | 0.0028967 | 0.0028967 | -4.34e-05% | 0.0041969 | 44.89%
1 | 28 | 23 | 6 | 111327 | 47963.7 | 63363.7 |  | 0.56815 | 36000.0228 | 1 | 0.0006 | 76.8984 | 2.9239 | 73.9745 | -1552530 | 4881.61 | 0.0059145 | 0.0028951 | 0.0028951 | -2.819e-05% | 0.0041959 | 44.93%
1 | 28 | 24 | 6 | 111327 | 48091.9 | 63235.5 |  | 0.5693 | 35999.9702 | 0 | 0.0006 | 76.885 | 2.9238 | 73.9612 | -1554880 | 4881.75 | 0.0059118 | 0.0028878 | 0.0028878 | 0.0001314% | 0.0041941 | 45.24%
1 | 29 | 1 | 7 | 111315 | 43962.9 | 67352.5 |  | 0.5345 | 35999.9786 | -1 | 0.0005 | 76.1537 | 2.9218 | 73.2319 | -1447990 | 4885.68 | 0.0057689 | 0.0029527 | 0.0029527 | -7.854e-05% | 0.0040649 | 37.67%
1 | 29 | 2 | 7 | 111309 | 43143.3 | 68165.5 |  | 0.52813 | 36000.041 | -1 | 0.0005 | 75.5286 | 2.9262 | 72.6024 | -1392530 | 4878.05 | 0.0056494 | 0.0029299 | 0.0029299 | -6.459e-05% | 0.003984 | 35.98%
1 | 29 | 3 | 7 | 111309 | 43428.1 | 67880.8 |  | 0.53034 | 36000.0392 | -2 | 0.0005 | 75.5805 | 2.9255 | 72.655 | -1401750 | 4879.4 | 0.0056592 | 0.0029231 | 0.0029231 | -0.0002175% | 0.0039906 | 36.52%
1 | 29 | 4 | 7 | 111309 | 43554.6 | 67754.2 |  | 0.53133 | 36000.0423 | -2 | 0.0005 | 75.5201 | 2.9135 | 72.6066 | -1401550 | 4899.59 | 0.0056286 | 0.0029036 | 0.0029036 | -0.0001955% | 0.0039699 | 36.72%
1 | 29 | 5 | 7 | 111309 | 43661.5 | 67647.3 |  | 0.53217 | 35999.9989 | -3 | 0.0005 | 75.4908 | 2.9128 | 72.578 | -1402530 | 4900.95 | 0.0056231 | 0.0028967 | 0.0028967 | -0.0001966% | 0.0039662 | 36.92%
1 | 29 | 6 | 7 | 111309 | 43762 | 67546.8 |  | 0.53296 | 36000.0127 | -3 | 0.0005 | 75.4616 | 2.9106 | 72.551 | -1404120 | 4904.69 | 0.0056176 | 0.0028901 | 0.0028901 | -4.279e-05% | 0.0039624 | 37.1%
1 | 29 | 7 | 7 | 111327 | 46210.1 | 65117.3 |  | 0.55285 | 35999.9691 | -3 | 0.0004 | 75.7056 | 2.9097 | 72.7959 | -1504790 | 4905.35 | 0.0056637 | 0.0027537 | 0.0027537 | 6.785e-05% | 0.0039616 | 43.87%
1 | 29 | 8 | 7 | 111327 | 53440.2 | 57887.3 |  | 0.6219 | 36000.054 | -4 | 0.0004 | 76.1314 | 2.9065 | 73.2249 | -1700610 | 4911.99 | 0.005745 | 0.002421 | 0.002421 | -0.0002633% | 0.0040166 | 65.91%
1 | 29 | 9 | 7 | 111327 | 48660 | 62667.5 |  | 0.57446 | 36000.0347 | -3 | 0.0004 | 76.5655 | 2.8868 | 73.6787 | -1603160 | 4948.6 | 0.0058296 | 0.0027105 | 0.0027105 | -7.218e-05% | 0.0040738 | 50.3%
1 | 29 | 10 | 7 | 111327 | 47200.6 | 64126.8 |  | 0.56139 | 36000.016 | -3 | 0.0004 | 76.934 | 2.9026 | 74.0314 | -1579040 | 4919.13 | 0.0059014 | 0.002813 | 0.002813 | 4.567e-05% | 0.0041224 | 46.55%
1 | 29 | 11 | 7 | 111327 | 46575.4 | 64752.1 |  | 0.55597 | 36000.0308 | -1 | 0.0004 | 77.0656 | 2.9077 | 74.1579 | -1562430 | 4909.5 | 0.0059274 | 0.0028543 | 0.0028543 | -6.992e-05% | 0.00414 | 45.04%
1 | 29 | 12 | 7 | 111327 | 45867 | 65460.4 |  | 0.54995 | 36000.0124 | 1 | 0.0005 | 77.1687 | 2.9136 | 74.2551 | -1517710 | 4899.23 | 0.0059481 | 0.0029519 | 0.0029519 | 0.0001001% | 0.0041863 | 41.82%
1 | 29 | 13 | 7 | 111327 | 45048.4 | 66279.1 |  | 0.54316 | 36000.0234 | 2 | 0.0005 | 77.266 | 2.9194 | 74.3466 | -1501270 | 4888.6 | 0.0059676 | 0.0029978 | 0.0029978 | -2.271e-05% | 0.0041995 | 40.09%
1 | 29 | 14 | 7 | 111327 | 44203.5 | 67123.9 |  | 0.53632 | 35999.9572 | 4 | 0.0005 | 77.3697 | 2.9234 | 74.4462 | -1486170 | 4881.4 | 0.0059884 | 0.0030449 | 0.0030449 | 1.512e-05% | 0.0042136 | 38.38%
1 | 29 | 15 | 7 | 111327 | 44054.9 | 67272.6 |  | 0.53514 | 35999.9901 | 5 | 0.0006 | 77.4352 | 2.9293 | 74.5059 | -1453770 | 4871.21 | 0.0060015 | 0.003111 | 0.003111 | 4.791e-05% | 0.0042548 | 36.77%
1 | 29 | 16 | 7 | 111327 | 44236.7 | 67090.7 |  | 0.53659 | 35999.9974 | 5 | 0.0006 | 77.4362 | 2.9318 | 74.5044 | -1456240 | 4866.55 | 0.0060018 | 0.0031032 | 0.0031032 | 3.779e-05% | 0.004255 | 37.11%
1 | 29 | 17 | 7 | 111327 | 45332.2 | 65995.3 |  | 0.54549 | 36000.0402 | 4 | 0.0006 | 77.3611 | 2.9315 | 74.4296 | -1476050 | 4867.11 | 0.0059867 | 0.0030483 | 0.0030483 | -5.314e-05% | 0.0042448 | 39.25%
1 | 29 | 18 | 7 | 111327 | 46408.1 | 64919.3 |  | 0.55453 | 35999.9591 | 3 | 0.0006 | 77.2256 | 2.9272 | 74.2984 | -1494760 | 4874.73 | 0.0059595 | 0.0029875 | 0.0029875 | 1.916e-05% | 0.0042264 | 41.47%
1 | 29 | 19 | 7 | 111327 | 46918.7 | 64408.7 |  | 0.55893 | 36000.0191 | 2 | 0.0006 | 77.1187 | 2.9225 | 74.1962 | -1508700 | 4883.08 | 0.0059381 | 0.0029544 | 0.0029545 | 9.43e-05% | 0.0042119 | 42.56%
1 | 29 | 20 | 7 | 111327 | 47629 | 63698.4 |  | 0.56516 | 35999.9788 | 2 | 0.0005 | 77.0313 | 2.919 | 74.1123 | -1582960 | 4889.21 | 0.0059205 | 0.002857 | 0.002857 | -5.926e-05% | 0.0041677 | 45.87%
1 | 29 | 21 | 7 | 111327 | 47669.3 | 63658.1 |  | 0.56552 | 35999.9924 | 2 | 0.0005 | 76.9755 | 2.9171 | 74.0584 | -1579840 | 4893.26 | 0.0059095 | 0.0028503 | 0.0028503 | 3.916e-05% | 0.0041602 | 45.96%
1 | 29 | 22 | 7 | 111327 | 47785.5 | 63541.9 |  | 0.56656 | 35999.9812 | 0 | 0.0005 | 76.9585 | 2.9168 | 74.0417 | -1581890 | 4893.88 | 0.0059062 | 0.0028433 | 0.0028433 | 0.0001063% | 0.004158 | 46.24%
1 | 29 | 23 | 7 | 111327 | 47921.9 | 63405.5 |  | 0.56777 | 35999.9944 | 1 | 0.0005 | 76.936 | 2.9125 | 74.0235 | -1586430 | 4901.06 | 0.0059018 | 0.0028348 | 0.0028348 | 0.0001919% | 0.004155 | 46.57%
1 | 29 | 24 | 7 | 111327 | 47868.2 | 63459.3 |  | 0.56729 | 36000.0167 | 1 | 0.0005 | 76.9314 | 2.914 | 74.0174 | -1583930 | 4898.64 | 0.0059009 | 0.002837 | 0.002837 | 0.00015% | 0.0041544 | 46.44%
1 | 30 | 1 | 1 | 111315 | 43711.7 | 67603.7 |  | 0.53251 | 35999.9843 | 1 | 0.0006 | 76.242 | 2.9145 | 73.3275 | -1415830 | 4898.4 | 0.0057666 | 0.0030153 | 0.0030153 | 0.0001319% | 0.0040957 | 35.83%
1 | 30 | 2 | 1 | 111309 | 42892.1 | 68416.6 |  | 0.52619 | 35999.9939 | 0 | 0.0005 | 75.646 | 2.9306 | 72.7154 | -1391570 | 4870.23 | 0.0056717 | 0.0029504 | 0.0029504 | -5.769e-06% | 0.003999 | 35.54%
1 | 30 | 3 | 1 | 111309 | 43217.9 | 68090.9 |  | 0.5287 | 35999.9993 | 0 | 0.0005 | 75.6828 | 2.9284 | 72.7545 | -1401660 | 4874.48 | 0.0056787 | 0.0029407 | 0.0029407 | 6.297e-05% | 0.0040038 | 36.15%
1 | 30 | 4 | 1 | 111309 | 43251.9 | 68056.9 |  | 0.52897 | 35999.9903 | 0 | 0.0006 | 75.6385 | 2.9278 | 72.7107 | -1370300 | 4875.45 | 0.0056702 | 0.0029882 | 0.0029882 | 7.277e-06% | 0.0040304 | 34.88%
1 | 30 | 5 | 1 | 111309 | 43259.9 | 68048.8 |  | 0.52903 | 35999.9928 | 1 | 0.0006 | 75.6348 | 2.9275 | 72.7073 | -1370270 | 4875.49 | 0.0056695 | 0.0029876 | 0.0029876 | 0.000195% | 0.0040299 | 34.89%
1 | 30 | 6 | 1 | 114288 | 43128.2 | 71159.7 |  | 0.5059 | 35999.9769 | 1 | 0.0006 | 75.6386 | 2.8626 | 72.776 | -1335720 | 4856.1 | 0.0056896 | 0.0031147 | 0.0031147 | -0.0001265% | 0.0040864 | 31.2%
1 | 30 | 7 | 1 | 116692 | 46671.5 | 70020.7 |  | 0.51413 | 36000.0226 | 2 | 0.0007 | 75.801 | 2.8093 | 72.9917 | -1368780 | 4845.18 | 0.0057205 | 0.0031393 | 0.0031393 | -0.0001557% | 0.0041717 | 32.89%
1 | 30 | 8 | 1 | 116818 | 49283.9 | 67534.5 |  | 0.53306 | 36000.0081 | 3 | 0.0007 | 76.5227 | 2.8162 | 73.7065 | -1457700 | 4827.86 | 0.005881 | 0.0031192 | 0.0031192 | -0.0001402% | 0.0042844 | 37.35%
1 | 30 | 9 | 1 | 116595 | 49369.9 | 67224.7 |  | 0.53552 | 36000.0369 | 4 | 0.0008 | 76.8646 | 2.8314 | 74.0332 | -1452220 | 4811.4 | 0.0059687 | 0.0032008 | 0.0032008 | 6.398e-05% | 0.0043728 | 36.62%
1 | 30 | 10 | 1 | 116229 | 48350.5 | 67878.7 |  | 0.53036 | 36000.0116 | 6 | 0.0009 | 76.905 | 2.8526 | 74.0524 | -1390460 | 4789.92 | 0.0059973 | 0.0032939 | 0.0032939 | 2.62e-05% | 0.0044185 | 34.14%
1 | 30 | 11 | 1 | 116001 | 47699.2 | 68302.2 |  | 0.52707 | 36000.0406 | 9 | 0.001 | 76.9575 | 2.8633 | 74.0942 | -1349350 | 4780.61 | 0.0060077 | 0.0033683 | 0.0033683 | -0.0002666% | 0.0044536 | 32.22%
1 | 30 | 12 | 1 | 115812 | 47081.1 | 68730.4 |  | 0.52378 | 35999.9526 | 13 | 0.0013 | 77.0085 | 2.8841 | 74.1244 | -1263870 | 4753.23 | 0.0060387 | 0.0035566 | 0.0035566 | 1.395e-05% | 0.0045657 | 28.37%
1 | 30 | 13 | 1 | 115494 | 45821.5 | 69672.9 |  | 0.5167 | 36000.0571 | 17 | 0.0017 | 77.0955 | 2.9201 | 74.1754 | -1119060 | 4705.86 | 0.0060987 | 0.0038259 | 0.0038259 | -0.0001879% | 0.0047276 | 23.57%
1 | 30 | 14 | 1 | 115462 | 45387.7 | 70074.3 |  | 0.51374 | 35999.9709 | 22 | 0.0022 | 77.1595 | 2.9401 | 74.2194 | -981912 | 4672.87 | 0.0061332 | 0.0041126 | 0.0041126 | 5.884e-05% | 0.0049069 | 19.31%
1 | 30 | 15 | 1 | 115140 | 44236.5 | 70903.3 |  | 0.50773 | 36000.0161 | 24 | 0.0026 | 77.2237 | 2.9579 | 74.2657 | -845517 | 4655.26 | 0.0061465 | 0.0043458 | 0.0043458 | -8.889e-05% | 0.0050377 | 15.92%
1 | 30 | 16 | 1 | 115333 | 45834.7 | 69498.6 |  | 0.518 | 35999.9968 | 27 | 0.003 | 77.2157 | 2.968 | 74.2477 | -747642 | 4629.78 | 0.0061664 | 0.0045262 | 0.0045262 | 5.05e-05% | 0.005178 | 14.4%
1 | 30 | 17 | 1 | 115680 | 49013.1 | 66666.8 |  | 0.54 | 36000.0053 | 30 | 0.0034 | 77.0555 | 2.9626 | 74.0929 | -655647 | 4622.77 | 0.0061331 | 0.0046572 | 0.0046572 | 5.439e-05% | 0.0052826 | 13.43%
1 | 30 | 18 | 1 | 115877 | 50392.7 | 65484.8 |  | 0.54975 | 36000.0069 | 31 | 0.0038 | 76.9125 | 2.9691 | 73.9434 | -549422 | 4603.67 | 0.0061255 | 0.004847 | 0.004847 | 6.528e-05% | 0.005403 | 11.47%
1 | 30 | 19 | 1 | 116196 | 52711.2 | 63484.5 |  | 0.56707 | 36000.0284 | 33 | 0.0039 | 76.781 | 2.9712 | 73.8098 | -532750 | 4586.28 | 0.0061204 | 0.0048613 | 0.0048613 | 1.165e-05% | 0.0054324 | 11.75%
1 | 30 | 20 | 1 | 116283 | 53706.8 | 62576.3 |  | 0.5753 | 36000.0202 | 34 | 0.0038 | 76.6622 | 2.9699 | 73.6924 | -561338 | 4584.78 | 0.0060962 | 0.0047752 | 0.0047752 | -0.0001051% | 0.0053853 | 12.78%
1 | 30 | 21 | 1 | 111309 | 47486.5 | 63822 |  | 0.56407 | 36000.0117 | 30 | 0.0036 | 76.9251 | 3.103 | 73.8221 | -598373 | 4584.86 | 0.0061496 | 0.0047115 | 0.0047115 | -3.404e-05% | 0.005325 | 13.02%
1 | 30 | 22 | 1 | 111257 | 44732.6 | 66524 |  | 0.54116 | 35999.9948 | 20 | 0.002 | 77.2515 | 3.0992 | 74.1523 | -1067760 | 4593.17 | 0.0062175 | 0.0039352 | 0.0039351 | -5.638e-05% | 0.0048528 | 23.32%
1 | 30 | 23 | 1 | 111327 | 45629.7 | 65697.7 |  | 0.54796 | 35999.9745 | 15 | 0.0016 | 77.3185 | 3.0728 | 74.2457 | -1208880 | 4636.18 | 0.0062095 | 0.0036837 | 0.0036837 | -5.366e-05% | 0.0047189 | 28.1%
1 | 30 | 24 | 1 | 111327 | 46080 | 65247.4 |  | 0.55175 | 35999.992 | 13 | 0.0013 | 77.2383 | 3.062 | 74.1763 | -1305290 | 4654.74 | 0.0061928 | 0.0034932 | 0.0034932 | -0.0001106% | 0.0046106 | 31.99%
1 | 31 | 1 | 2 | 111089 | 42361.4 | 68728 |  | 0.5238 | 36000.0013 | 12 | 0.0013 | 76.581 | 3.0635 | 73.5175 | -1201330 | 4664.03 | 0.0060583 | 0.0035659 | 0.0035659 | -6.414e-05% | 0.0045163 | 26.65%
1 | 31 | 2 | 2 | 111137 | 41584 | 69552.5 |  | 0.5176 | 36000.0262 | 13 | 0.0013 | 76.0241 | 3.0636 | 72.9605 | -1155360 | 4661.23 | 0.0059456 | 0.0035411 | 0.0035411 | -0.0001273% | 0.0044408 | 25.41%
1 | 31 | 3 | 2 | 111125 | 41803.5 | 69321.4 |  | 0.51932 | 35999.9894 | 12 | 0.0012 | 76.0766 | 3.0543 | 73.0224 | -1188460 | 4676.24 | 0.0059353 | 0.0034762 | 0.0034762 | 9.295e-05% | 0.0044013 | 26.61%
1 | 31 | 4 | 2 | 111154 | 41892.2 | 69261.5 |  | 0.51977 | 36000.0499 | 12 | 0.0012 | 76.0425 | 3.0514 | 72.9911 | -1188930 | 4679.99 | 0.0059285 | 0.0034708 | 0.0034708 | -5.905e-05% | 0.004397 | 26.69%
1 | 31 | 5 | 2 | 111155 | 41879.6 | 69275.7 |  | 0.51966 | 35999.9488 | 13 | 0.0013 | 76.0396 | 3.0511 | 72.9885 | -1160550 | 4680.44 | 0.0059279 | 0.0035229 | 0.003523 | 4.05e-05% | 0.004429 | 25.72%
1 | 31 | 6 | 2 | 114054 | 41762 | 72292 |  | 0.49798 | 35999.9702 | 12 | 0.0013 | 76.0216 | 2.9753 | 73.0463 | -1130950 | 4677.24 | 0.0059242 | 0.0036215 | 0.0036215 | 0.0001653% | 0.0044647 | 23.28%
1 | 31 | 7 | 2 | 115938 | 44694.9 | 71243.5 |  | 0.50531 | 36000.053 | 12 | 0.0013 | 76.1272 | 2.9194 | 73.2078 | -1175890 | 4688.4 | 0.0059248 | 0.0035878 | 0.0035878 | -0.0002113% | 0.0044887 | 25.11%
1 | 31 | 8 | 2 | 116011 | 47241.6 | 68769.1 |  | 0.52349 | 36000.0049 | 11 | 0.0012 | 76.7371 | 2.9164 | 73.8207 | -1278800 | 4690.6 | 0.0060474 | 0.0035098 | 0.0035098 | 5.596e-06% | 0.0045432 | 29.44%
1 | 31 | 9 | 2 | 115798 | 47492.4 | 68305.2 |  | 0.52705 | 36000.0507 | 12 | 0.0013 | 77.0247 | 2.9086 | 74.1161 | -1272950 | 4712.57 | 0.0060841 | 0.0035627 | 0.0035626 | -0.0001407% | 0.0045968 | 29.03%
1 | 31 | 10 | 2 | 115286 | 46016.9 | 69269.4 |  | 0.51971 | 35999.9999 | 13 | 0.0014 | 77.0734 | 2.9234 | 74.15 | -1209750 | 4709.07 | 0.0060941 | 0.0036545 | 0.0036545 | 0.0001012% | 0.0046283 | 26.65%
1 | 31 | 11 | 2 | 114857 | 44226.4 | 70630.7 |  | 0.50969 | 35999.9734 | 14 | 0.0013 | 77.1951 | 2.9378 | 74.2573 | -1215490 | 4702.71 | 0.0061192 | 0.0036629 | 0.0036629 | 6.016e-05% | 0.0046087 | 25.82%
1 | 31 | 12 | 2 | 115046 | 44933 | 70112.6 |  | 0.51346 | 36000.0156 | 14 | 0.0013 | 77.2093 | 2.9272 | 74.2821 | -1236690 | 4711.87 | 0.0061009 | 0.0036358 | 0.0036358 | -0.0001444% | 0.0045986 | 26.48%
1 | 31 | 13 | 2 | 114913 | 44606.4 | 70306.8 |  | 0.51204 | 36000.0345 | 14 | 0.0013 | 77.1945 | 2.9298 | 74.2647 | -1218710 | 4713.37 | 0.0060979 | 0.0036412 | 0.0036412 | -0.0001601% | 0.0045948 | 26.19%
1 | 31 | 14 | 2 | 114987 | 44963 | 70023.8 |  | 0.51411 | 36000.0058 | 14 | 0.0013 | 77.1923 | 2.9281 | 74.2642 | -1237000 | 4712.97 | 0.0060974 | 0.003631 | 0.003631 | -0.0001761% | 0.0045954 | 26.56%
1 | 31 | 15 | 2 | 114867 | 44763.8 | 70103.1 |  | 0.51353 | 35999.9748 | 14 | 0.0013 | 77.1756 | 2.9207 | 74.2549 | -1219440 | 4729.94 | 0.0060729 | 0.0036219 | 0.0036219 | 0.0001978% | 0.0045771 | 26.37%
1 | 31 | 16 | 2 | 115072 | 45458.3 | 69613.3 |  | 0.51714 | 35999.9612 | 14 | 0.0013 | 77.1557 | 2.9154 | 74.2403 | -1224110 | 4730.17 | 0.0060688 | 0.0036027 | 0.0036027 | 7.063e-05% | 0.0045769 | 27.04%
1 | 31 | 17 | 2 | 115112 | 45835 | 69277 |  | 0.51965 | 36000.0009 | 14 | 0.0013 | 77.1082 | 2.9037 | 74.2045 | -1231770 | 4747.85 | 0.0060382 | 0.003576 | 0.003576 | -6.646e-06% | 0.0045564 | 27.42%
1 | 31 | 18 | 2 | 115335 | 46618.7 | 68716.5 |  | 0.52389 | 36000.0246 | 14 | 0.0014 | 77.0627 | 2.8972 | 74.1655 | -1225370 | 4749.46 | 0.0060289 | 0.0036039 | 0.0036039 | 1.677e-05% | 0.0045841 | 27.2%
1 | 31 | 19 | 2 | 115384 | 46859.6 | 68524.8 |  | 0.52536 | 35999.9834 | 13 | 0.0013 | 77.0293 | 2.8949 | 74.1344 | -1257520 | 4750.97 | 0.0060221 | 0.0035413 | 0.0035413 | 0.000168% | 0.0045488 | 28.45%
1 | 31 | 20 | 2 | 115249 | 46643.1 | 68605.4 |  | 0.52474 | 35999.9976 | 14 | 0.0014 | 77.0312 | 2.8962 | 74.135 | -1219820 | 4755.06 | 0.0060225 | 0.0035969 | 0.0035969 | -0.000164% | 0.0045786 | 27.29%
1 | 31 | 21 | 2 | 111317 | 45300.8 | 66016.4 |  | 0.54532 | 35999.9972 | 15 | 0.0014 | 77.146 | 3.0003 | 74.1457 | -1223970 | 4751.58 | 0.0060459 | 0.0035124 | 0.0035124 | -0.0001111% | 0.0045434 | 29.35%
1 | 31 | 22 | 2 | 111324 | 46006.5 | 65318 |  | 0.55115 | 36000.0157 | 16 | 0.0015 | 77.171 | 2.9982 | 74.1728 | -1233190 | 4755.34 | 0.006051 | 0.0035427 | 0.0035427 | -0.0001608% | 0.0045793 | 29.26%
1 | 31 | 23 | 2 | 111327 | 45779.2 | 65547.9 |  | 0.54922 | 36000.021 | 19 | 0.0016 | 77.1687 | 2.9887 | 74.18 | -1196350 | 4770.11 | 0.0060298 | 0.0035969 | 0.0035969 | -4.077e-05% | 0.0045973 | 27.81%
1 | 31 | 24 | 2 | 111327 | 45301.9 | 66025.6 |  | 0.54524 | 36000.0622 | 23 | 0.0019 | 77.223 | 2.9946 | 74.2284 | -1096500 | 4760.22 | 0.0060408 | 0.0037831 | 0.0037831 | -7.17e-05% | 0.0047018 | 24.29%