## Sheet1
|  | a | b | c | d | e | f |  | LOAD |  | SST | SDT | DT
COOL | 100% | 1 | 43 | 1849 | 120 | 14400 | 5160 |  | 100% | COOL | 43 | 120 | 77 | At cooling SST & SDT, input cooling rating EIR
HEAT | 100% | 1 | 34 | 1156 | 104 | 10816 | 3536 |  |  | HEAT | 34 | 104 | 70 | At heating SST & SDT, operating COP equate to rated heating COP
COOL | FPLR | 1 | 1 | 1 | 77 | 5929 | 77
HEAT | FPLR | 1 | 1 | 1 | 70 | 4900 | 70
RATIO | FPLR | 1 | 1
[8 empty] | COOL | HEAT
| VRF044-Cap-fSST&SDT | 0.74825 | 0.018886 | 0.00012763 | -0.0024022 | -4.62e-06 | -7.356e-05 | 1.062 | 0.978
| VRF044-EIR-fSST&SDT | 0.6772 | 0.000183 | 0.00027715 | -0.0068486 | 0.00017005 | -0.0003656 | 0.93791 | 0.83805
| VRF044-EIR-fPLR | 0.013543 | 0.64481 | 0.33137 | 0.00097278 | 1.23e-06 | -0.00093943 | 0.99958 | 0.99808
| VRF-HP-Resys-Cycle-fPLR | 0.8976 | 0.1024 |  |  |  |  | 1 | 1
[8 empty] | 0.99561 | 0.81804
[8 empty] | COOL | HEAT
[7 empty] | EER | 10
[7 empty] | COP | 2.9308 | 3.56
0.82327
The energy consumption at cooling rated SST & SDT is COP-2.93
The energy consumption at heating rated SST & SDT is COP-3.56
Cooling EER-10 and Heating COP-3.56 at rated condition have been used to calibrated the energy consumption curve at full load