## Calculations
Rated Capacity [kW]: | 160 | T_CHW_Rated_Ein: | 21 |  |  | m_Dot_CHW [kg/h]: | 46100 |  | T_HW_Rated_Ein: | 90 |  | m_Dot_HW [kg/h]: | 9700
COP_Rated: | 0.8 | T_CHW_Rated_Aus: | 16 |  |  | Cp_CHW [kJ/kg*K]: | 4.19 |  | T_HW_Rated_Aus: | 75 |  | Cp_HW [kJ/kg*K]: | 4.19
cooling required for T_CHW_Rated: | 965795 | [7 empty] | Heating resulted from T_HW_Rated: | 609645
|  | CHW Set | ECWT | IHWT | Multipliers | Available Cooling Capacity | Fraction of Capacity | Fraction of design load |  | IHWT | Heat Input (Cooling Mode) [kW] | Fraction of Design Energy Input
|  | 16 | 30 | 60 |  | 0 | 0 | 0 |  | 60 | 110 | 0.64956
|  | 16 | 30 | 70 |  | 0 | 0 | 0 |  | 70 | 125 | 0.73813
|  | 16 | 30 | 80 |  | 0 | 0 | 0 |  | 80 | 170 | 1.0039
|  | 16 | 30 | 90 | 1.08 | 622080 | 0.64411 | 0.64411 |  | 90 | 200 | 1.181
|  | 16 | 30 | 100 |  | 0 | 0 | 0 |  | 100 | 225 | 1.3286
|  | 16 |  | 60 |  | 0 | 0 | 0
|  | 16 |  | 70 |  | 0 | 0 | 0
|  | 16 |  | 80 |  | 0 | 0 | 0
|  | 16 |  | 90 |  | 0 | 0 | 0
|  | 16 |  | 100 |  | 0 | 0 | 0
16
16
16

## Data File
0 | 0.1 | 0.2 | 0.3 | 0.4 | 0.5 | 0.6 | 0.7 | 0.8 | 0.9 | 1 | !Fraction of Design Load
5.556 | 6.111 | 6.667 | 7.222 | 7.778 | 8.889 | 10 |  |  |  |  | !Chilled Water Setpoint (C)
0: 26.667; 0.1: 29.444; 0.2: 32.222 | !Entering Cooling Water Temperature (C)
0: 108.89; 0.1: 111.67; 0.2: 113.89; 0.3: 115; 0.4: 116.11 | !Inlet Hot Water Temperature (C) | Load | CHW Set | ECWT | IHWT
0: 0.9878; 0.1: 0 | !Capacity and Design Energy Input Fraction at | 0 | 5.556 | 26.667 | 108.89
0: 1.0367; 0.1: 0 | !Capacity and Design Energy Input Fraction at | 0 | 5.556 | 26.667 | 111.67
0: 1.0837; 0.1: 0 | !Capacity and Design Energy Input Fraction at | 0 | 5.556 | 26.667 | 113.89
0: 1.1041; 0.1: 0 | !Capacity and Design Energy Input Fraction at | 0 | 5.556 | 26.667 | 115
0: 1.1265; 0.1: 0 | !Capacity and Design Energy Input Fraction at | 0 | 5.556 | 26.667 | 116.11
0: 0.8612; 0.1: 0 | !Capacity and Design Energy Input Fraction at | 0 | 5.556 | 29.444 | 108.89
0: 0.9102; 0.1: 0 | !Capacity and Design Energy Input Fraction at | 0 | 5.556 | 29.444 | 111.67
0: 0.9571; 0.1: 0 | !Capacity and Design Energy Input Fraction at | 0 | 5.556 | 29.444 | 113.89
0: 0.9796; 0.1: 0 | !Capacity and Design Energy Input Fraction at | 0 | 5.556 | 29.444 | 115
0: 1; 0.1: 0 | !Capacity and Design Energy Input Fraction at | 0 | 5.556 | 29.444 | 116.11
0: 0.7347; 0.1: 0 | !Capacity and Design Energy Input Fraction at | 0 | 5.556 | 32.222 | 108.89
0: 0.7857; 0.1: 0 | !Capacity and Design Energy Input Fraction at | 0 | 5.556 | 32.222 | 111.67
0: 0.8327; 0.1: 0 | !Capacity and Design Energy Input Fraction at | 0 | 5.556 | 32.222 | 113.89
0: 0.8531; 0.1: 0 | !Capacity and Design Energy Input Fraction at | 0 | 5.556 | 32.222 | 115
0: 0.8735; 0.1: 0 | !Capacity and Design Energy Input Fraction at | 0 | 5.556 | 32.222 | 116.11
0: 1.0102; 0.1: 0 | !Capacity and Design Energy Input Fraction at | 0 | 6.111 | 26.667 | 108.89
0: 1.0592; 0.1: 0 | !Capacity and Design Energy Input Fraction at | 0 | 6.111 | 26.667 | 111.67
0: 1.1061; 0.1: 0 | !Capacity and Design Energy Input Fraction at | 0 | 6.111 | 26.667 | 113.89
0: 1.1286; 0.1: 0 | !Capacity and Design Energy Input Fraction at | 0 | 6.111 | 26.667 | 115
0: 1.149; 0.1: 0 | !Capacity and Design Energy Input Fraction at | 0 | 6.111 | 26.667 | 116.11
0: 0.8837; 0.1: 0 | !Capacity and Design Energy Input Fraction at | 0 | 6.111 | 29.444 | 108.89
0: 0.9327; 0.1: 0 | !Capacity and Design Energy Input Fraction at | 0 | 6.111 | 29.444 | 111.67
0: 0.9776; 0.1: 0 | !Capacity and Design Energy Input Fraction at | 0 | 6.111 | 29.444 | 113.89
0: 1; 0.1: 0 | !Capacity and Design Energy Input Fraction at | 0 | 6.111 | 29.444 | 115
0: 1.0224; 0.1: 0 | !Capacity and Design Energy Input Fraction at | 0 | 6.111 | 29.444 | 116.11
0: 0.7571; 0.1: 0 | !Capacity and Design Energy Input Fraction at | 0 | 6.111 | 32.222 | 108.89
0: 0.8061; 0.1: 0 | !Capacity and Design Energy Input Fraction at | 0 | 6.111 | 32.222 | 111.67
0: 0.8531; 0.1: 0 | !Capacity and Design Energy Input Fraction at | 0 | 6.111 | 32.222 | 113.89
0: 0.8735; 0.1: 0 | !Capacity and Design Energy Input Fraction at | 0 | 6.111 | 32.222 | 115
0: 0.8959; 0.1: 0 | !Capacity and Design Energy Input Fraction at | 0 | 6.111 | 32.222 | 116.11
0: 1.0306; 0.1: 0 | !Capacity and Design Energy Input Fraction at | 0 | 6.667 | 26.667 | 108.89
0: 1.0816; 0.1: 0 | !Capacity and Design Energy Input Fraction at | 0 | 6.667 | 26.667 | 111.67
0: 1.1286; 0.1: 0 | !Capacity and Design Energy Input Fraction at | 0 | 6.667 | 26.667 | 113.89
0: 1.151; 0.1: 0 | !Capacity and Design Energy Input Fraction at | 0 | 6.667 | 26.667 | 115
0: 1.1714; 0.1: 0 | !Capacity and Design Energy Input Fraction at | 0 | 6.667 | 26.667 | 116.11
0: 0.9041; 0.1: 0 | !Capacity and Design Energy Input Fraction at | 0 | 6.667 | 29.444 | 108.89
0: 0.9531; 0.1: 0 | !Capacity and Design Energy Input Fraction at | 0 | 6.667 | 29.444 | 111.67
0: 1; 0.1: 0 | !Capacity and Design Energy Input Fraction at | 0 | 6.667 | 29.444 | 113.89
0: 1.0224; 0.1: 0 | !Capacity and Design Energy Input Fraction at | 0 | 6.667 | 29.444 | 115
0: 1.0449; 0.1: 0 | !Capacity and Design Energy Input Fraction at | 0 | 6.667 | 29.444 | 116.11
0: 0.7776; 0.1: 0 | !Capacity and Design Energy Input Fraction at | 0 | 6.667 | 32.222 | 108.89
0: 0.8265; 0.1: 0 | !Capacity and Design Energy Input Fraction at | 0 | 6.667 | 32.222 | 111.67
0: 0.8735; 0.1: 0 | !Capacity and Design Energy Input Fraction at | 0 | 6.667 | 32.222 | 113.89
0: 0.8959; 0.1: 0 | !Capacity and Design Energy Input Fraction at | 0 | 6.667 | 32.222 | 115
0: 0.9163; 0.1: 0 | !Capacity and Design Energy Input Fraction at | 0 | 6.667 | 32.222 | 116.11
0: 1.0531; 0.1: 0 | !Capacity and Design Energy Input Fraction at | 0 | 7.222 | 26.667 | 108.89
0: 1.1041; 0.1: 0 | !Capacity and Design Energy Input Fraction at | 0 | 7.222 | 26.667 | 111.67
0: 1.151; 0.1: 0 | !Capacity and Design Energy Input Fraction at | 0 | 7.222 | 26.667 | 113.89
0: 1.1735; 0.1: 0 | !Capacity and Design Energy Input Fraction at | 0 | 7.222 | 26.667 | 115
0: 1.1959; 0.1: 0 | !Capacity and Design Energy Input Fraction at | 0 | 7.222 | 26.667 | 116.11
0: 0.9245; 0.1: 0 | !Capacity and Design Energy Input Fraction at | 0 | 7.222 | 29.444 | 108.89
0: 0.9755; 0.1: 0 | !Capacity and Design Energy Input Fraction at | 0 | 7.222 | 29.444 | 111.67
0: 1.0224; 0.1: 0 | !Capacity and Design Energy Input Fraction at | 0 | 7.222 | 29.444 | 113.89
0: 1.0449; 0.1: 0 | !Capacity and Design Energy Input Fraction at | 0 | 7.222 | 29.444 | 115
0: 1.0673; 0.1: 0 | !Capacity and Design Energy Input Fraction at | 0 | 7.222 | 29.444 | 116.11
0: 0.798; 0.1: 0 | !Capacity and Design Energy Input Fraction at | 0 | 7.222 | 32.222 | 108.89
0: 0.8469; 0.1: 0 | !Capacity and Design Energy Input Fraction at | 0 | 7.222 | 32.222 | 111.67
0: 0.8939; 0.1: 0 | !Capacity and Design Energy Input Fraction at | 0 | 7.222 | 32.222 | 113.89
0: 0.9163; 0.1: 0 | !Capacity and Design Energy Input Fraction at | 0 | 7.222 | 32.222 | 115
0: 0.9388; 0.1: 0 | !Capacity and Design Energy Input Fraction at | 0 | 7.222 | 32.222 | 116.11
0: 1.0755; 0.1: 0 | !Capacity and Design Energy Input Fraction at | 0 | 7.778 | 26.667 | 108.89
0: 1.1265; 0.1: 0 | !Capacity and Design Energy Input Fraction at | 0 | 7.778 | 26.667 | 111.67
0: 1.1755; 0.1: 0 | !Capacity and Design Energy Input Fraction at | 0 | 7.778 | 26.667 | 113.89
0: 1.198; 0.1: 0 | !Capacity and Design Energy Input Fraction at | 0 | 7.778 | 26.667 | 115
0: 1.2184; 0.1: 0 | !Capacity and Design Energy Input Fraction at | 0 | 7.778 | 26.667 | 116.11
0: 0.9469; 0.1: 0 | !Capacity and Design Energy Input Fraction at | 0 | 7.778 | 29.444 | 108.89
0: 0.998; 0.1: 0 | !Capacity and Design Energy Input Fraction at | 0 | 7.778 | 29.444 | 111.67
0: 1.0449; 0.1: 0 | !Capacity and Design Energy Input Fraction at | 0 | 7.778 | 29.444 | 113.89
0: 1.0673; 0.1: 0 | !Capacity and Design Energy Input Fraction at | 0 | 7.778 | 29.444 | 115
0: 1.0898; 0.1: 0 | !Capacity and Design Energy Input Fraction at | 0 | 7.778 | 29.444 | 116.11
0: 0.8184; 0.1: 0 | !Capacity and Design Energy Input Fraction at | 0 | 7.778 | 32.222 | 108.89
0: 0.8694; 0.1: 0 | !Capacity and Design Energy Input Fraction at | 0 | 7.778 | 32.222 | 111.67
0: 0.9163; 0.1: 0 | !Capacity and Design Energy Input Fraction at | 0 | 7.778 | 32.222 | 113.89
0: 0.9388; 0.1: 0 | !Capacity and Design Energy Input Fraction at | 0 | 7.778 | 32.222 | 115
0: 0.9592; 0.1: 0 | !Capacity and Design Energy Input Fraction at | 0 | 7.778 | 32.222 | 116.11
0: 1.1204; 0.1: 0 | !Capacity and Design Energy Input Fraction at | 0 | 8.889 | 26.667 | 108.89
0: 1.1735; 0.1: 0 | !Capacity and Design Energy Input Fraction at | 0 | 8.889 | 26.667 | 111.67
0: 1.2204; 0.1: 0 | !Capacity and Design Energy Input Fraction at | 0 | 8.889 | 26.667 | 113.89
0: 1.2449; 0.1: 0 | !Capacity and Design Energy Input Fraction at | 0 | 8.889 | 26.667 | 115
0: 1.2673; 0.1: 0 | !Capacity and Design Energy Input Fraction at | 0 | 8.889 | 26.667 | 116.11
0: 0.9898; 0.1: 0 | !Capacity and Design Energy Input Fraction at | 0 | 8.889 | 29.444 | 108.89
0: 1.0408; 0.1: 0 | !Capacity and Design Energy Input Fraction at | 0 | 8.889 | 29.444 | 111.67
0: 1.0898; 0.1: 0 | !Capacity and Design Energy Input Fraction at | 0 | 8.889 | 29.444 | 113.89
0: 1.1122; 0.1: 0 | !Capacity and Design Energy Input Fraction at | 0 | 8.889 | 29.444 | 115
0: 1.1347; 0.1: 0 | !Capacity and Design Energy Input Fraction at | 0 | 8.889 | 29.444 | 116.11
0: 0.8592; 0.1: 0 | !Capacity and Design Energy Input Fraction at | 0 | 8.889 | 32.222 | 108.89
0: 0.9102; 0.1: 0 | !Capacity and Design Energy Input Fraction at | 0 | 8.889 | 32.222 | 111.67
0: 0.9592; 0.1: 0 | !Capacity and Design Energy Input Fraction at | 0 | 8.889 | 32.222 | 113.89
0: 0.9816; 0.1: 0 | !Capacity and Design Energy Input Fraction at | 0 | 8.889 | 32.222 | 115
0: 1.0041; 0.1: 0 | !Capacity and Design Energy Input Fraction at | 0 | 8.889 | 32.222 | 116.11
0: 1.1673; 0.1: 0 | !Capacity and Design Energy Input Fraction at | 0 | 10 | 26667 | 108.89
0: 1.2204; 0.1: 0 | !Capacity and Design Energy Input Fraction at | 0 | 10 | 26667 | 111.67
0: 1.2694; 0.1: 0 | !Capacity and Design Energy Input Fraction at | 0 | 10 | 26667 | 113.89
0: 1.2898; 0.1: 0 | !Capacity and Design Energy Input Fraction at | 0 | 10 | 26667 | 115
0: 1.2898; 0.1: 0 | !Capacity and Design Energy Input Fraction at | 0 | 10 | 26667 | 116.11
0: 1.0347; 0.1: 0 | !Capacity and Design Energy Input Fraction at | 0 | 10 | 29444 | 108.89
0: 1.0857; 0.1: 0 | !Capacity and Design Energy Input Fraction at | 0 | 10 | 29444 | 111.67
0: 1.1347; 0.1: 0 | !Capacity and Design Energy Input Fraction at | 0 | 10 | 29444 | 113.89
0: 1.1592; 0.1: 0 | !Capacity and Design Energy Input Fraction at | 0 | 10 | 29444 | 115
0: 1.1796; 0.1: 0 | !Capacity and Design Energy Input Fraction at | 0 | 10 | 29444 | 116.11
0: 0.902; 0.1: 0 | !Capacity and Design Energy Input Fraction at | 0 | 10 | 32222 | 108.89
0: 0.9531; 0.1: 0 | !Capacity and Design Energy Input Fraction at | 0 | 10 | 32222 | 111.67
0: 1.002; 0.1: 0 | !Capacity and Design Energy Input Fraction at | 0 | 10 | 32222 | 113.89
0: 1.0245; 0.1: 0 | !Capacity and Design Energy Input Fraction at | 0 | 10 | 32222 | 115
0: 1.0469; 0.1: 0 | !Capacity and Design Energy Input Fraction at | 0 | 10 | 32222 | 116.11
0: 0.9878; 0.1: 0.099 | !Capacity and Design Energy Input Fraction at | 0.1 | 5.556 | 26.667 | 108.89
0: 1.0367; 0.1: 0.099 | !Capacity and Design Energy Input Fraction at | 0.1 | 5.556 | 26.667 | 111.67
0: 1.0837; 0.1: 0.099 | !Capacity and Design Energy Input Fraction at | 0.1 | 5.556 | 26.667 | 113.89
0: 1.1041; 0.1: 0.099 | !Capacity and Design Energy Input Fraction at | 0.1 | 5.556 | 26.667 | 115
0: 1.1265; 0.1: 0.099 | !Capacity and Design Energy Input Fraction at | 0.1 | 5.556 | 26.667 | 116.11
0: 0.8612; 0.1: 0.102 | !Capacity and Design Energy Input Fraction at | 0.1 | 5.556 | 29.444 | 108.89
0: 0.9102; 0.1: 0.102 | !Capacity and Design Energy Input Fraction at | 0.1 | 5.556 | 29.444 | 111.67
0: 0.9571; 0.1: 0.102 | !Capacity and Design Energy Input Fraction at | 0.1 | 5.556 | 29.444 | 113.89
0: 0.9796; 0.1: 0.102 | !Capacity and Design Energy Input Fraction at | 0.1 | 5.556 | 29.444 | 115
0: 1; 0.1: 0.102 | !Capacity and Design Energy Input Fraction at | 0.1 | 5.556 | 29.444 | 116.11
0: 0.7347; 0.1: 0.104 | !Capacity and Design Energy Input Fraction at | 0.1 | 5.556 | 32.222 | 108.89
0: 0.7857; 0.1: 0.104 | !Capacity and Design Energy Input Fraction at | 0.1 | 5.556 | 32.222 | 111.67
0: 0.8327; 0.1: 0.104 | !Capacity and Design Energy Input Fraction at | 0.1 | 5.556 | 32.222 | 113.89
0: 0.8531; 0.1: 0.104 | !Capacity and Design Energy Input Fraction at | 0.1 | 5.556 | 32.222 | 115
0: 0.8735; 0.1: 0.104 | !Capacity and Design Energy Input Fraction at | 0.1 | 5.556 | 32.222 | 116.11
0: 1.0102; 0.1: 0.098 | !Capacity and Design Energy Input Fraction at | 0.1 | 6.111 | 26.667 | 108.89
0: 1.0592; 0.1: 0.098 | !Capacity and Design Energy Input Fraction at | 0.1 | 6.111 | 26.667 | 111.67
0: 1.1061; 0.1: 0.098 | !Capacity and Design Energy Input Fraction at | 0.1 | 6.111 | 26.667 | 113.89
0: 1.1286; 0.1: 0.098 | !Capacity and Design Energy Input Fraction at | 0.1 | 6.111 | 26.667 | 115
0: 1.149; 0.1: 0.098 | !Capacity and Design Energy Input Fraction at | 0.1 | 6.111 | 26.667 | 116.11
0: 0.8837; 0.1: 0.101 | !Capacity and Design Energy Input Fraction at | 0.1 | 6.111 | 29.444 | 108.89
0: 0.9327; 0.1: 0.101 | !Capacity and Design Energy Input Fraction at | 0.1 | 6.111 | 29.444 | 111.67
0: 0.9776; 0.1: 0.101 | !Capacity and Design Energy Input Fraction at | 0.1 | 6.111 | 29.444 | 113.89
0: 1; 0.1: 0.101 | !Capacity and Design Energy Input Fraction at | 0.1 | 6.111 | 29.444 | 115
0: 1.0224; 0.1: 0.101 | !Capacity and Design Energy Input Fraction at | 0.1 | 6.111 | 29.444 | 116.11
0: 0.7571; 0.1: 0.104 | !Capacity and Design Energy Input Fraction at | 0.1 | 6.111 | 32.222 | 108.89
0: 0.8061; 0.1: 0.104 | !Capacity and Design Energy Input Fraction at | 0.1 | 6.111 | 32.222 | 111.67
0: 0.8531; 0.1: 0.104 | !Capacity and Design Energy Input Fraction at | 0.1 | 6.111 | 32.222 | 113.89
0: 0.8735; 0.1: 0.104 | !Capacity and Design Energy Input Fraction at | 0.1 | 6.111 | 32.222 | 115
0: 0.8959; 0.1: 0.104 | !Capacity and Design Energy Input Fraction at | 0.1 | 6.111 | 32.222 | 116.11
0: 1.0306; 0.1: 0.098 | !Capacity and Design Energy Input Fraction at | 0.1 | 6.667 | 26.667 | 108.89
0: 1.0816; 0.1: 0.098 | !Capacity and Design Energy Input Fraction at | 0.1 | 6.667 | 26.667 | 111.67
0: 1.1286; 0.1: 0.098 | !Capacity and Design Energy Input Fraction at | 0.1 | 6.667 | 26.667 | 113.89
0: 1.151; 0.1: 0.098 | !Capacity and Design Energy Input Fraction at | 0.1 | 6.667 | 26.667 | 115
0: 1.1714; 0.1: 0.098 | !Capacity and Design Energy Input Fraction at | 0.1 | 6.667 | 26.667 | 116.11
0: 0.9041; 0.1: 0.1 | !Capacity and Design Energy Input Fraction at | 0.1 | 6.667 | 29.444 | 108.89
0: 0.9531; 0.1: 0.1 | !Capacity and Design Energy Input Fraction at | 0.1 | 6.667 | 29.444 | 111.67
0: 1; 0.1: 0.1 | !Capacity and Design Energy Input Fraction at | 0.1 | 6.667 | 29.444 | 113.89
0: 1.0224; 0.1: 0.1 | !Capacity and Design Energy Input Fraction at | 0.1 | 6.667 | 29.444 | 115
0: 1.0449; 0.1: 0.1 | !Capacity and Design Energy Input Fraction at | 0.1 | 6.667 | 29.444 | 116.11
0: 0.7776; 0.1: 0.103 | !Capacity and Design Energy Input Fraction at | 0.1 | 6.667 | 32.222 | 108.89
0: 0.8265; 0.1: 0.103 | !Capacity and Design Energy Input Fraction at | 0.1 | 6.667 | 32.222 | 111.67
0: 0.8735; 0.1: 0.103 | !Capacity and Design Energy Input Fraction at | 0.1 | 6.667 | 32.222 | 113.89
0: 0.8959; 0.1: 0.103 | !Capacity and Design Energy Input Fraction at | 0.1 | 6.667 | 32.222 | 115
0: 0.9163; 0.1: 0.103 | !Capacity and Design Energy Input Fraction at | 0.1 | 6.667 | 32.222 | 116.11
0: 1.0531; 0.1: 0.097 | !Capacity and Design Energy Input Fraction at | 0.1 | 7.222 | 26.667 | 108.89
0: 1.1041; 0.1: 0.097 | !Capacity and Design Energy Input Fraction at | 0.1 | 7.222 | 26.667 | 111.67
0: 1.151; 0.1: 0.097 | !Capacity and Design Energy Input Fraction at | 0.1 | 7.222 | 26.667 | 113.89
0: 1.1735; 0.1: 0.097 | !Capacity and Design Energy Input Fraction at | 0.1 | 7.222 | 26.667 | 115
0: 1.1959; 0.1: 0.097 | !Capacity and Design Energy Input Fraction at | 0.1 | 7.222 | 26.667 | 116.11
0: 0.9245; 0.1: 0.099 | !Capacity and Design Energy Input Fraction at | 0.1 | 7.222 | 29.444 | 108.89
0: 0.9755; 0.1: 0.099 | !Capacity and Design Energy Input Fraction at | 0.1 | 7.222 | 29.444 | 111.67
0: 1.0224; 0.1: 0.099 | !Capacity and Design Energy Input Fraction at | 0.1 | 7.222 | 29.444 | 113.89
0: 1.0449; 0.1: 0.099 | !Capacity and Design Energy Input Fraction at | 0.1 | 7.222 | 29.444 | 115
0: 1.0673; 0.1: 0.099 | !Capacity and Design Energy Input Fraction at | 0.1 | 7.222 | 29.444 | 116.11
0: 0.798; 0.1: 0.102 | !Capacity and Design Energy Input Fraction at | 0.1 | 7.222 | 32.222 | 108.89
0: 0.8469; 0.1: 0.102 | !Capacity and Design Energy Input Fraction at | 0.1 | 7.222 | 32.222 | 111.67
0: 0.8939; 0.1: 0.102 | !Capacity and Design Energy Input Fraction at | 0.1 | 7.222 | 32.222 | 113.89
0: 0.9163; 0.1: 0.102 | !Capacity and Design Energy Input Fraction at | 0.1 | 7.222 | 32.222 | 115
0: 0.9388; 0.1: 0.102 | !Capacity and Design Energy Input Fraction at | 0.1 | 7.222 | 32.222 | 116.11
0: 1.0755; 0.1: 0.096 | !Capacity and Design Energy Input Fraction at | 0.1 | 7.778 | 26.667 | 108.89
0: 1.1265; 0.1: 0.096 | !Capacity and Design Energy Input Fraction at | 0.1 | 7.778 | 26.667 | 111.67
0: 1.1755; 0.1: 0.096 | !Capacity and Design Energy Input Fraction at | 0.1 | 7.778 | 26.667 | 113.89
0: 1.198; 0.1: 0.096 | !Capacity and Design Energy Input Fraction at | 0.1 | 7.778 | 26.667 | 115
0: 1.2184; 0.1: 0.096 | !Capacity and Design Energy Input Fraction at | 0.1 | 7.778 | 26.667 | 116.11
0: 0.9469; 0.1: 0.098 | !Capacity and Design Energy Input Fraction at | 0.1 | 7.778 | 29.444 | 108.89
0: 0.998; 0.1: 0.098 | !Capacity and Design Energy Input Fraction at | 0.1 | 7.778 | 29.444 | 111.67
0: 1.0449; 0.1: 0.098 | !Capacity and Design Energy Input Fraction at | 0.1 | 7.778 | 29.444 | 113.89
0: 1.0673; 0.1: 0.098 | !Capacity and Design Energy Input Fraction at | 0.1 | 7.778 | 29.444 | 115
0: 1.0898; 0.1: 0.098 | !Capacity and Design Energy Input Fraction at | 0.1 | 7.778 | 29.444 | 116.11
0: 0.8184; 0.1: 0.101 | !Capacity and Design Energy Input Fraction at | 0.1 | 7.778 | 32.222 | 108.89
0: 0.8694; 0.1: 0.101 | !Capacity and Design Energy Input Fraction at | 0.1 | 7.778 | 32.222 | 111.67
0: 0.9163; 0.1: 0.101 | !Capacity and Design Energy Input Fraction at | 0.1 | 7.778 | 32.222 | 113.89
0: 0.9388; 0.1: 0.101 | !Capacity and Design Energy Input Fraction at | 0.1 | 7.778 | 32.222 | 115
0: 0.9592; 0.1: 0.101 | !Capacity and Design Energy Input Fraction at | 0.1 | 7.778 | 32.222 | 116.11
0: 1.1204; 0.1: 0.095 | !Capacity and Design Energy Input Fraction at | 0.1 | 8.889 | 26.667 | 108.89
0: 1.1735; 0.1: 0.095 | !Capacity and Design Energy Input Fraction at | 0.1 | 8.889 | 26.667 | 111.67
0: 1.2204; 0.1: 0.095 | !Capacity and Design Energy Input Fraction at | 0.1 | 8.889 | 26.667 | 113.89
0: 1.2449; 0.1: 0.095 | !Capacity and Design Energy Input Fraction at | 0.1 | 8.889 | 26.667 | 115
0: 1.2673; 0.1: 0.095 | !Capacity and Design Energy Input Fraction at | 0.1 | 8.889 | 26.667 | 116.11
0: 0.9898; 0.1: 0.097 | !Capacity and Design Energy Input Fraction at | 0.1 | 8.889 | 29.444 | 108.89
0: 1.0408; 0.1: 0.097 | !Capacity and Design Energy Input Fraction at | 0.1 | 8.889 | 29.444 | 111.67
0: 1.0898; 0.1: 0.097 | !Capacity and Design Energy Input Fraction at | 0.1 | 8.889 | 29.444 | 113.89
0: 1.1122; 0.1: 0.097 | !Capacity and Design Energy Input Fraction at | 0.1 | 8.889 | 29.444 | 115
0: 1.1347; 0.1: 0.097 | !Capacity and Design Energy Input Fraction at | 0.1 | 8.889 | 29.444 | 116.11
0: 0.8592; 0.1: 0.1 | !Capacity and Design Energy Input Fraction at | 0.1 | 8.889 | 32.222 | 108.89
0: 0.9102; 0.1: 0.1 | !Capacity and Design Energy Input Fraction at | 0.1 | 8.889 | 32.222 | 111.67
0: 0.9592; 0.1: 0.1 | !Capacity and Design Energy Input Fraction at | 0.1 | 8.889 | 32.222 | 113.89
0: 0.9816; 0.1: 0.1 | !Capacity and Design Energy Input Fraction at | 0.1 | 8.889 | 32.222 | 115
0: 1.0041; 0.1: 0.1 | !Capacity and Design Energy Input Fraction at | 0.1 | 8.889 | 32.222 | 116.11
0: 1.1673; 0.1: 0.094 | !Capacity and Design Energy Input Fraction at | 0.1 | 10 | 26.667 | 108.89
0: 1.2204; 0.1: 0.094 | !Capacity and Design Energy Input Fraction at | 0.1 | 10 | 26.667 | 111.67
0: 1.2694; 0.1: 0.094 | !Capacity and Design Energy Input Fraction at | 0.1 | 10 | 26.667 | 113.89
0: 1.2898; 0.1: 0.094 | !Capacity and Design Energy Input Fraction at | 0.1 | 10 | 26.667 | 115
0: 1.2898; 0.1: 0.094 | !Capacity and Design Energy Input Fraction at | 0.1 | 10 | 26.667 | 116.11
0: 1.0347; 0.1: 0.096 | !Capacity and Design Energy Input Fraction at | 0.1 | 10 | 29.444 | 108.89
0: 1.0857; 0.1: 0.096 | !Capacity and Design Energy Input Fraction at | 0.1 | 10 | 29.444 | 111.67
0: 1.1347; 0.1: 0.096 | !Capacity and Design Energy Input Fraction at | 0.1 | 10 | 29.444 | 113.89
0: 1.1592; 0.1: 0.096 | !Capacity and Design Energy Input Fraction at | 0.1 | 10 | 29.444 | 115
0: 1.1796; 0.1: 0.096 | !Capacity and Design Energy Input Fraction at | 0.1 | 10 | 29.444 | 116.11
0: 0.902; 0.1: 0.098 | !Capacity and Design Energy Input Fraction at | 0.1 | 10 | 32.222 | 108.89
0: 0.9531; 0.1: 0.098 | !Capacity and Design Energy Input Fraction at | 0.1 | 10 | 32.222 | 111.67
0: 1.002; 0.1: 0.098 | !Capacity and Design Energy Input Fraction at | 0.1 | 10 | 32.222 | 113.89
0: 1.0245; 0.1: 0.098 | !Capacity and Design Energy Input Fraction at | 0.1 | 10 | 32.222 | 115
0: 1.0469; 0.1: 0.098 | !Capacity and Design Energy Input Fraction at | 0.1 | 10 | 32.222 | 116.11
0: 0.9878; 0.1: 0.198 | !Capacity and Design Energy Input Fraction at | 0.2 | 5.556 | 26.667 | 108.89
0: 1.0367; 0.1: 0.198 | !Capacity and Design Energy Input Fraction at | 0.2 | 5.556 | 26.667 | 111.67
0: 1.0837; 0.1: 0.198 | !Capacity and Design Energy Input Fraction at | 0.2 | 5.556 | 26.667 | 113.89
0: 1.1041; 0.1: 0.198 | !Capacity and Design Energy Input Fraction at | 0.2 | 5.556 | 26.667 | 115
0: 1.1265; 0.1: 0.198 | !Capacity and Design Energy Input Fraction at | 0.2 | 5.556 | 26.667 | 116.11
0: 0.8612; 0.1: 0.204 | !Capacity and Design Energy Input Fraction at | 0.2 | 5.556 | 29.444 | 108.89
0: 0.9102; 0.1: 0.204 | !Capacity and Design Energy Input Fraction at | 0.2 | 5.556 | 29.444 | 111.67
0: 0.9571; 0.1: 0.204 | !Capacity and Design Energy Input Fraction at | 0.2 | 5.556 | 29.444 | 113.89
0: 0.9796; 0.1: 0.204 | !Capacity and Design Energy Input Fraction at | 0.2 | 5.556 | 29.444 | 115
0: 1; 0.1: 0.204 | !Capacity and Design Energy Input Fraction at | 0.2 | 5.556 | 29.444 | 116.11
0: 0.7347; 0.1: 0.208 | !Capacity and Design Energy Input Fraction at | 0.2 | 5.556 | 32.222 | 108.89
0: 0.7857; 0.1: 0.208 | !Capacity and Design Energy Input Fraction at | 0.2 | 5.556 | 32.222 | 111.67
0: 0.8327; 0.1: 0.208 | !Capacity and Design Energy Input Fraction at | 0.2 | 5.556 | 32.222 | 113.89
0: 0.8531; 0.1: 0.208 | !Capacity and Design Energy Input Fraction at | 0.2 | 5.556 | 32.222 | 115
0: 0.8735; 0.1: 0.208 | !Capacity and Design Energy Input Fraction at | 0.2 | 5.556 | 32.222 | 116.11
0: 1.0102; 0.1: 0.196 | !Capacity and Design Energy Input Fraction at | 0.2 | 6.111 | 26.667 | 108.89
0: 1.0592; 0.1: 0.196 | !Capacity and Design Energy Input Fraction at | 0.2 | 6.111 | 26.667 | 111.67
0: 1.1061; 0.1: 0.196 | !Capacity and Design Energy Input Fraction at | 0.2 | 6.111 | 26.667 | 113.89
0: 1.1286; 0.1: 0.196 | !Capacity and Design Energy Input Fraction at | 0.2 | 6.111 | 26.667 | 115
0: 1.149; 0.1: 0.196 | !Capacity and Design Energy Input Fraction at | 0.2 | 6.111 | 26.667 | 116.11
0: 0.8837; 0.1: 0.202 | !Capacity and Design Energy Input Fraction at | 0.2 | 6.111 | 29.444 | 108.89
0: 0.9327; 0.1: 0.202 | !Capacity and Design Energy Input Fraction at | 0.2 | 6.111 | 29.444 | 111.67
0: 0.9776; 0.1: 0.202 | !Capacity and Design Energy Input Fraction at | 0.2 | 6.111 | 29.444 | 113.89
0: 1; 0.1: 0.202 | !Capacity and Design Energy Input Fraction at | 0.2 | 6.111 | 29.444 | 115
0: 1.0224; 0.1: 0.202 | !Capacity and Design Energy Input Fraction at | 0.2 | 6.111 | 29.444 | 116.11
0: 0.7571; 0.1: 0.208 | !Capacity and Design Energy Input Fraction at | 0.2 | 6.111 | 32.222 | 108.89
0: 0.8061; 0.1: 0.208 | !Capacity and Design Energy Input Fraction at | 0.2 | 6.111 | 32.222 | 111.67
0: 0.8531; 0.1: 0.208 | !Capacity and Design Energy Input Fraction at | 0.2 | 6.111 | 32.222 | 113.89
0: 0.8735; 0.1: 0.208 | !Capacity and Design Energy Input Fraction at | 0.2 | 6.111 | 32.222 | 115
0: 0.8959; 0.1: 0.208 | !Capacity and Design Energy Input Fraction at | 0.2 | 6.111 | 32.222 | 116.11
0: 1.0306; 0.1: 0.196 | !Capacity and Design Energy Input Fraction at | 0.2 | 6.667 | 26.667 | 108.89
0: 1.0816; 0.1: 0.196 | !Capacity and Design Energy Input Fraction at | 0.2 | 6.667 | 26.667 | 111.67
0: 1.1286; 0.1: 0.196 | !Capacity and Design Energy Input Fraction at | 0.2 | 6.667 | 26.667 | 113.89
0: 1.151; 0.1: 0.196 | !Capacity and Design Energy Input Fraction at | 0.2 | 6.667 | 26.667 | 115
0: 1.1714; 0.1: 0.196 | !Capacity and Design Energy Input Fraction at | 0.2 | 6.667 | 26.667 | 116.11
0: 0.9041; 0.1: 0.2 | !Capacity and Design Energy Input Fraction at | 0.2 | 6.667 | 29.444 | 108.89
0: 0.9531; 0.1: 0.2 | !Capacity and Design Energy Input Fraction at | 0.2 | 6.667 | 29.444 | 111.67
0: 1; 0.1: 0.2 | !Capacity and Design Energy Input Fraction at | 0.2 | 6.667 | 29.444 | 113.89
0: 1.0224; 0.1: 0.2 | !Capacity and Design Energy Input Fraction at | 0.2 | 6.667 | 29.444 | 115
0: 1.0449; 0.1: 0.2 | !Capacity and Design Energy Input Fraction at | 0.2 | 6.667 | 29.444 | 116.11
0: 0.7776; 0.1: 0.206 | !Capacity and Design Energy Input Fraction at | 0.2 | 6.667 | 32.222 | 108.89
0: 0.8265; 0.1: 0.206 | !Capacity and Design Energy Input Fraction at | 0.2 | 6.667 | 32.222 | 111.67
0: 0.8735; 0.1: 0.206 | !Capacity and Design Energy Input Fraction at | 0.2 | 6.667 | 32.222 | 113.89
0: 0.8959; 0.1: 0.206 | !Capacity and Design Energy Input Fraction at | 0.2 | 6.667 | 32.222 | 115
0: 0.9163; 0.1: 0.206 | !Capacity and Design Energy Input Fraction at | 0.2 | 6.667 | 32.222 | 116.11
0: 1.0531; 0.1: 0.194 | !Capacity and Design Energy Input Fraction at | 0.2 | 7.222 | 26.667 | 108.89
0: 1.1041; 0.1: 0.194 | !Capacity and Design Energy Input Fraction at | 0.2 | 7.222 | 26.667 | 111.67
0: 1.151; 0.1: 0.194 | !Capacity and Design Energy Input Fraction at | 0.2 | 7.222 | 26.667 | 113.89
0: 1.1735; 0.1: 0.194 | !Capacity and Design Energy Input Fraction at | 0.2 | 7.222 | 26.667 | 115
0: 1.1959; 0.1: 0.194 | !Capacity and Design Energy Input Fraction at | 0.2 | 7.222 | 26.667 | 116.11
0: 0.9245; 0.1: 0.198 | !Capacity and Design Energy Input Fraction at | 0.2 | 7.222 | 29.444 | 108.89
0: 0.9755; 0.1: 0.198 | !Capacity and Design Energy Input Fraction at | 0.2 | 7.222 | 29.444 | 111.67
0: 1.0224; 0.1: 0.198 | !Capacity and Design Energy Input Fraction at | 0.2 | 7.222 | 29.444 | 113.89
0: 1.0449; 0.1: 0.198 | !Capacity and Design Energy Input Fraction at | 0.2 | 7.222 | 29.444 | 115
0: 1.0673; 0.1: 0.198 | !Capacity and Design Energy Input Fraction at | 0.2 | 7.222 | 29.444 | 116.11
0: 0.798; 0.1: 0.204 | !Capacity and Design Energy Input Fraction at | 0.2 | 7.222 | 32.222 | 108.89
0: 0.8469; 0.1: 0.204 | !Capacity and Design Energy Input Fraction at | 0.2 | 7.222 | 32.222 | 111.67
0: 0.8939; 0.1: 0.204 | !Capacity and Design Energy Input Fraction at | 0.2 | 7.222 | 32.222 | 113.89
0: 0.9163; 0.1: 0.204 | !Capacity and Design Energy Input Fraction at | 0.2 | 7.222 | 32.222 | 115
0: 0.9388; 0.1: 0.204 | !Capacity and Design Energy Input Fraction at | 0.2 | 7.222 | 32.222 | 116.11
0: 1.0755; 0.1: 0.192 | !Capacity and Design Energy Input Fraction at | 0.2 | 7.778 | 26.667 | 108.89
0: 1.1265; 0.1: 0.192 | !Capacity and Design Energy Input Fraction at | 0.2 | 7.778 | 26.667 | 111.67
0: 1.1755; 0.1: 0.192 | !Capacity and Design Energy Input Fraction at | 0.2 | 7.778 | 26.667 | 113.89
0: 1.198; 0.1: 0.192 | !Capacity and Design Energy Input Fraction at | 0.2 | 7.778 | 26.667 | 115
0: 1.2184; 0.1: 0.192 | !Capacity and Design Energy Input Fraction at | 0.2 | 7.778 | 26.667 | 116.11
0: 0.9469; 0.1: 0.196 | !Capacity and Design Energy Input Fraction at | 0.2 | 7.778 | 29.444 | 108.89
0: 0.998; 0.1: 0.196 | !Capacity and Design Energy Input Fraction at | 0.2 | 7.778 | 29.444 | 111.67
0: 1.0449; 0.1: 0.196 | !Capacity and Design Energy Input Fraction at | 0.2 | 7.778 | 29.444 | 113.89
0: 1.0673; 0.1: 0.196 | !Capacity and Design Energy Input Fraction at | 0.2 | 7.778 | 29.444 | 115
0: 1.0898; 0.1: 0.196 | !Capacity and Design Energy Input Fraction at | 0.2 | 7.778 | 29.444 | 116.11
0: 0.8184; 0.1: 0.202 | !Capacity and Design Energy Input Fraction at | 0.2 | 7.778 | 32.222 | 108.89
0: 0.8694; 0.1: 0.202 | !Capacity and Design Energy Input Fraction at | 0.2 | 7.778 | 32.222 | 111.67
0: 0.9163; 0.1: 0.202 | !Capacity and Design Energy Input Fraction at | 0.2 | 7.778 | 32.222 | 113.89
0: 0.9388; 0.1: 0.202 | !Capacity and Design Energy Input Fraction at | 0.2 | 7.778 | 32.222 | 115
0: 0.9592; 0.1: 0.202 | !Capacity and Design Energy Input Fraction at | 0.2 | 7.778 | 32.222 | 116.11
0: 1.1204; 0.1: 0.19 | !Capacity and Design Energy Input Fraction at | 0.2 | 8.889 | 26.667 | 108.89
0: 1.1735; 0.1: 0.19 | !Capacity and Design Energy Input Fraction at | 0.2 | 8.889 | 26.667 | 111.67
0: 1.2204; 0.1: 0.19 | !Capacity and Design Energy Input Fraction at | 0.2 | 8.889 | 26.667 | 113.89
0: 1.2449; 0.1: 0.19 | !Capacity and Design Energy Input Fraction at | 0.2 | 8.889 | 26.667 | 115
0: 1.2673; 0.1: 0.19 | !Capacity and Design Energy Input Fraction at | 0.2 | 8.889 | 26.667 | 116.11
0: 0.9898; 0.1: 0.194 | !Capacity and Design Energy Input Fraction at | 0.2 | 8.889 | 29.444 | 108.89
0: 1.0408; 0.1: 0.194 | !Capacity and Design Energy Input Fraction at | 0.2 | 8.889 | 29.444 | 111.67
0: 1.0898; 0.1: 0.194 | !Capacity and Design Energy Input Fraction at | 0.2 | 8.889 | 29.444 | 113.89
0: 1.1122; 0.1: 0.194 | !Capacity and Design Energy Input Fraction at | 0.2 | 8.889 | 29.444 | 115
0: 1.1347; 0.1: 0.194 | !Capacity and Design Energy Input Fraction at | 0.2 | 8.889 | 29.444 | 116.11
0: 0.8592; 0.1: 0.2 | !Capacity and Design Energy Input Fraction at | 0.2 | 8.889 | 32.222 | 108.89
0: 0.9102; 0.1: 0.2 | !Capacity and Design Energy Input Fraction at | 0.2 | 8.889 | 32.222 | 111.67
0: 0.9592; 0.1: 0.2 | !Capacity and Design Energy Input Fraction at | 0.2 | 8.889 | 32.222 | 113.89
0: 0.9816; 0.1: 0.2 | !Capacity and Design Energy Input Fraction at | 0.2 | 8.889 | 32.222 | 115
0: 1.0041; 0.1: 0.2 | !Capacity and Design Energy Input Fraction at | 0.2 | 8.889 | 32.222 | 116.11
0: 1.1673; 0.1: 0.188 | !Capacity and Design Energy Input Fraction at | 0.2 | 10 | 26.667 | 108.89
0: 1.2204; 0.1: 0.188 | !Capacity and Design Energy Input Fraction at | 0.2 | 10 | 26.667 | 111.67
0: 1.2694; 0.1: 0.188 | !Capacity and Design Energy Input Fraction at | 0.2 | 10 | 26.667 | 113.89
0: 1.2898; 0.1: 0.188 | !Capacity and Design Energy Input Fraction at | 0.2 | 10 | 26.667 | 115
0: 1.2898; 0.1: 0.188 | !Capacity and Design Energy Input Fraction at | 0.2 | 10 | 26.667 | 116.11
0: 1.0347; 0.1: 0.192 | !Capacity and Design Energy Input Fraction at | 0.2 | 10 | 29.444 | 108.89
0: 1.0857; 0.1: 0.192 | !Capacity and Design Energy Input Fraction at | 0.2 | 10 | 29.444 | 111.67
0: 1.1347; 0.1: 0.192 | !Capacity and Design Energy Input Fraction at | 0.2 | 10 | 29.444 | 113.89
0: 1.1592; 0.1: 0.192 | !Capacity and Design Energy Input Fraction at | 0.2 | 10 | 29.444 | 115
0: 1.1796; 0.1: 0.192 | !Capacity and Design Energy Input Fraction at | 0.2 | 10 | 29.444 | 116.11
0: 0.902; 0.1: 0.196 | !Capacity and Design Energy Input Fraction at | 0.2 | 10 | 32.222 | 108.89
0: 0.9531; 0.1: 0.196 | !Capacity and Design Energy Input Fraction at | 0.2 | 10 | 32.222 | 111.67
0: 1.002; 0.1: 0.196 | !Capacity and Design Energy Input Fraction at | 0.2 | 10 | 32.222 | 113.89
0: 1.0245; 0.1: 0.196 | !Capacity and Design Energy Input Fraction at | 0.2 | 10 | 32.222 | 115
0: 1.0469; 0.1: 0.196 | !Capacity and Design Energy Input Fraction at | 0.2 | 10 | 32.222 | 116.11
0: 0.9878; 0.1: 0.297 | !Capacity and Design Energy Input Fraction at | 0.3 | 5.556 | 26.667 | 108.89
0: 1.0367; 0.1: 0.297 | !Capacity and Design Energy Input Fraction at | 0.3 | 5.556 | 26.667 | 111.67
0: 1.0837; 0.1: 0.297 | !Capacity and Design Energy Input Fraction at | 0.3 | 5.556 | 26.667 | 113.89
0: 1.1041; 0.1: 0.297 | !Capacity and Design Energy Input Fraction at | 0.3 | 5.556 | 26.667 | 115
0: 1.1265; 0.1: 0.297 | !Capacity and Design Energy Input Fraction at | 0.3 | 5.556 | 26.667 | 116.11
0: 0.8612; 0.1: 0.306 | !Capacity and Design Energy Input Fraction at | 0.3 | 5.556 | 29.444 | 108.89
0: 0.9102; 0.1: 0.306 | !Capacity and Design Energy Input Fraction at | 0.3 | 5.556 | 29.444 | 111.67
0: 0.9571; 0.1: 0.306 | !Capacity and Design Energy Input Fraction at | 0.3 | 5.556 | 29.444 | 113.89
0: 0.9796; 0.1: 0.306 | !Capacity and Design Energy Input Fraction at | 0.3 | 5.556 | 29.444 | 115
0: 1; 0.1: 0.306 | !Capacity and Design Energy Input Fraction at | 0.3 | 5.556 | 29.444 | 116.11
0: 0.7347; 0.1: 0.312 | !Capacity and Design Energy Input Fraction at | 0.3 | 5.556 | 32.222 | 108.89
0: 0.7857; 0.1: 0.312 | !Capacity and Design Energy Input Fraction at | 0.3 | 5.556 | 32.222 | 111.67
0: 0.8327; 0.1: 0.312 | !Capacity and Design Energy Input Fraction at | 0.3 | 5.556 | 32.222 | 113.89
0: 0.8531; 0.1: 0.312 | !Capacity and Design Energy Input Fraction at | 0.3 | 5.556 | 32.222 | 115
0: 0.8735; 0.1: 0.312 | !Capacity and Design Energy Input Fraction at | 0.3 | 5.556 | 32.222 | 116.11
0: 1.0102; 0.1: 0.294 | !Capacity and Design Energy Input Fraction at | 0.3 | 6.111 | 26.667 | 108.89
0: 1.0592; 0.1: 0.294 | !Capacity and Design Energy Input Fraction at | 0.3 | 6.111 | 26.667 | 111.67
0: 1.1061; 0.1: 0.294 | !Capacity and Design Energy Input Fraction at | 0.3 | 6.111 | 26.667 | 113.89
0: 1.1286; 0.1: 0.294 | !Capacity and Design Energy Input Fraction at | 0.3 | 6.111 | 26.667 | 115
0: 1.149; 0.1: 0.294 | !Capacity and Design Energy Input Fraction at | 0.3 | 6.111 | 26.667 | 116.11
0: 0.8837; 0.1: 0.303 | !Capacity and Design Energy Input Fraction at | 0.3 | 6.111 | 29.444 | 108.89
0: 0.9327; 0.1: 0.303 | !Capacity and Design Energy Input Fraction at | 0.3 | 6.111 | 29.444 | 111.67
0: 0.9776; 0.1: 0.303 | !Capacity and Design Energy Input Fraction at | 0.3 | 6.111 | 29.444 | 113.89
0: 1; 0.1: 0.303 | !Capacity and Design Energy Input Fraction at | 0.3 | 6.111 | 29.444 | 115
0: 1.0224; 0.1: 0.303 | !Capacity and Design Energy Input Fraction at | 0.3 | 6.111 | 29.444 | 116.11
0: 0.7571; 0.1: 0.312 | !Capacity and Design Energy Input Fraction at | 0.3 | 6.111 | 32.222 | 108.89
0: 0.8061; 0.1: 0.312 | !Capacity and Design Energy Input Fraction at | 0.3 | 6.111 | 32.222 | 111.67
0: 0.8531; 0.1: 0.312 | !Capacity and Design Energy Input Fraction at | 0.3 | 6.111 | 32.222 | 113.89
0: 0.8735; 0.1: 0.312 | !Capacity and Design Energy Input Fraction at | 0.3 | 6.111 | 32.222 | 115
0: 0.8959; 0.1: 0.312 | !Capacity and Design Energy Input Fraction at | 0.3 | 6.111 | 32.222 | 116.11
0: 1.0306; 0.1: 0.294 | !Capacity and Design Energy Input Fraction at | 0.3 | 6.667 | 26.667 | 108.89
0: 1.0816; 0.1: 0.294 | !Capacity and Design Energy Input Fraction at | 0.3 | 6.667 | 26.667 | 111.67
0: 1.1286; 0.1: 0.294 | !Capacity and Design Energy Input Fraction at | 0.3 | 6.667 | 26.667 | 113.89
0: 1.151; 0.1: 0.294 | !Capacity and Design Energy Input Fraction at | 0.3 | 6.667 | 26.667 | 115
0: 1.1714; 0.1: 0.294 | !Capacity and Design Energy Input Fraction at | 0.3 | 6.667 | 26.667 | 116.11
0: 0.9041; 0.1: 0.3 | !Capacity and Design Energy Input Fraction at | 0.3 | 6.667 | 29.444 | 108.89
0: 0.9531; 0.1: 0.3 | !Capacity and Design Energy Input Fraction at | 0.3 | 6.667 | 29.444 | 111.67
0: 1; 0.1: 0.3 | !Capacity and Design Energy Input Fraction at | 0.3 | 6.667 | 29.444 | 113.89
0: 1.0224; 0.1: 0.3 | !Capacity and Design Energy Input Fraction at | 0.3 | 6.667 | 29.444 | 115
0: 1.0449; 0.1: 0.3 | !Capacity and Design Energy Input Fraction at | 0.3 | 6.667 | 29.444 | 116.11
0: 0.7776; 0.1: 0.309 | !Capacity and Design Energy Input Fraction at | 0.3 | 6.667 | 32.222 | 108.89
0: 0.8265; 0.1: 0.309 | !Capacity and Design Energy Input Fraction at | 0.3 | 6.667 | 32.222 | 111.67
0: 0.8735; 0.1: 0.309 | !Capacity and Design Energy Input Fraction at | 0.3 | 6.667 | 32.222 | 113.89
0: 0.8959; 0.1: 0.309 | !Capacity and Design Energy Input Fraction at | 0.3 | 6.667 | 32.222 | 115
0: 0.9163; 0.1: 0.309 | !Capacity and Design Energy Input Fraction at | 0.3 | 6.667 | 32.222 | 116.11
0: 1.0531; 0.1: 0.291 | !Capacity and Design Energy Input Fraction at | 0.3 | 7.222 | 26.667 | 108.89
0: 1.1041; 0.1: 0.291 | !Capacity and Design Energy Input Fraction at | 0.3 | 7.222 | 26.667 | 111.67
0: 1.151; 0.1: 0.291 | !Capacity and Design Energy Input Fraction at | 0.3 | 7.222 | 26.667 | 113.89
0: 1.1735; 0.1: 0.291 | !Capacity and Design Energy Input Fraction at | 0.3 | 7.222 | 26.667 | 115
0: 1.1959; 0.1: 0.291 | !Capacity and Design Energy Input Fraction at | 0.3 | 7.222 | 26.667 | 116.11
0: 0.9245; 0.1: 0.297 | !Capacity and Design Energy Input Fraction at | 0.3 | 7.222 | 29.444 | 108.89
0: 0.9755; 0.1: 0.297 | !Capacity and Design Energy Input Fraction at | 0.3 | 7.222 | 29.444 | 111.67
0: 1.0224; 0.1: 0.297 | !Capacity and Design Energy Input Fraction at | 0.3 | 7.222 | 29.444 | 113.89
0: 1.0449; 0.1: 0.297 | !Capacity and Design Energy Input Fraction at | 0.3 | 7.222 | 29.444 | 115
0: 1.0673; 0.1: 0.297 | !Capacity and Design Energy Input Fraction at | 0.3 | 7.222 | 29.444 | 116.11
0: 0.798; 0.1: 0.306 | !Capacity and Design Energy Input Fraction at | 0.3 | 7.222 | 32.222 | 108.89
0: 0.8469; 0.1: 0.306 | !Capacity and Design Energy Input Fraction at | 0.3 | 7.222 | 32.222 | 111.67
0: 0.8939; 0.1: 0.306 | !Capacity and Design Energy Input Fraction at | 0.3 | 7.222 | 32.222 | 113.89
0: 0.9163; 0.1: 0.306 | !Capacity and Design Energy Input Fraction at | 0.3 | 7.222 | 32.222 | 115
0: 0.9388; 0.1: 0.306 | !Capacity and Design Energy Input Fraction at | 0.3 | 7.222 | 32.222 | 116.11
0: 1.0755; 0.1: 0.288 | !Capacity and Design Energy Input Fraction at | 0.3 | 7.778 | 26.667 | 108.89
0: 1.1265; 0.1: 0.288 | !Capacity and Design Energy Input Fraction at | 0.3 | 7.778 | 26.667 | 111.67
0: 1.1755; 0.1: 0.288 | !Capacity and Design Energy Input Fraction at | 0.3 | 7.778 | 26.667 | 113.89
0: 1.198; 0.1: 0.288 | !Capacity and Design Energy Input Fraction at | 0.3 | 7.778 | 26.667 | 115
0: 1.2184; 0.1: 0.288 | !Capacity and Design Energy Input Fraction at | 0.3 | 7.778 | 26.667 | 116.11
0: 0.9469; 0.1: 0.294 | !Capacity and Design Energy Input Fraction at | 0.3 | 7.778 | 29.444 | 108.89
0: 0.998; 0.1: 0.294 | !Capacity and Design Energy Input Fraction at | 0.3 | 7.778 | 29.444 | 111.67
0: 1.0449; 0.1: 0.294 | !Capacity and Design Energy Input Fraction at | 0.3 | 7.778 | 29.444 | 113.89
0: 1.0673; 0.1: 0.294 | !Capacity and Design Energy Input Fraction at | 0.3 | 7.778 | 29.444 | 115
0: 1.0898; 0.1: 0.294 | !Capacity and Design Energy Input Fraction at | 0.3 | 7.778 | 29.444 | 116.11
0: 0.8184; 0.1: 0.303 | !Capacity and Design Energy Input Fraction at | 0.3 | 7.778 | 32.222 | 108.89
0: 0.8694; 0.1: 0.303 | !Capacity and Design Energy Input Fraction at | 0.3 | 7.778 | 32.222 | 111.67
0: 0.9163; 0.1: 0.303 | !Capacity and Design Energy Input Fraction at | 0.3 | 7.778 | 32.222 | 113.89
0: 0.9388; 0.1: 0.303 | !Capacity and Design Energy Input Fraction at | 0.3 | 7.778 | 32.222 | 115
0: 0.9592; 0.1: 0.303 | !Capacity and Design Energy Input Fraction at | 0.3 | 7.778 | 32.222 | 116.11
0: 1.1204; 0.1: 0.285 | !Capacity and Design Energy Input Fraction at | 0.3 | 8.889 | 26.667 | 108.89
0: 1.1735; 0.1: 0.285 | !Capacity and Design Energy Input Fraction at | 0.3 | 8.889 | 26.667 | 111.67
0: 1.2204; 0.1: 0.285 | !Capacity and Design Energy Input Fraction at | 0.3 | 8.889 | 26.667 | 113.89
0: 1.2449; 0.1: 0.285 | !Capacity and Design Energy Input Fraction at | 0.3 | 8.889 | 26.667 | 115
0: 1.2673; 0.1: 0.285 | !Capacity and Design Energy Input Fraction at | 0.3 | 8.889 | 26.667 | 116.11
0: 0.9898; 0.1: 0.291 | !Capacity and Design Energy Input Fraction at | 0.3 | 8.889 | 29.444 | 108.89
0: 1.0408; 0.1: 0.291 | !Capacity and Design Energy Input Fraction at | 0.3 | 8.889 | 29.444 | 111.67
0: 1.0898; 0.1: 0.291 | !Capacity and Design Energy Input Fraction at | 0.3 | 8.889 | 29.444 | 113.89
0: 1.1122; 0.1: 0.291 | !Capacity and Design Energy Input Fraction at | 0.3 | 8.889 | 29.444 | 115
0: 1.1347; 0.1: 0.291 | !Capacity and Design Energy Input Fraction at | 0.3 | 8.889 | 29.444 | 116.11
0: 0.8592; 0.1: 0.3 | !Capacity and Design Energy Input Fraction at | 0.3 | 8.889 | 32.222 | 108.89
0: 0.9102; 0.1: 0.3 | !Capacity and Design Energy Input Fraction at | 0.3 | 8.889 | 32.222 | 111.67
0: 0.9592; 0.1: 0.3 | !Capacity and Design Energy Input Fraction at | 0.3 | 8.889 | 32.222 | 113.89
0: 0.9816; 0.1: 0.3 | !Capacity and Design Energy Input Fraction at | 0.3 | 8.889 | 32.222 | 115
0: 1.0041; 0.1: 0.3 | !Capacity and Design Energy Input Fraction at | 0.3 | 8.889 | 32.222 | 116.11
0: 1.1673; 0.1: 0.282 | !Capacity and Design Energy Input Fraction at | 0.3 | 10 | 26.667 | 108.89
0: 1.2204; 0.1: 0.282 | !Capacity and Design Energy Input Fraction at | 0.3 | 10 | 26.667 | 111.67
0: 1.2694; 0.1: 0.282 | !Capacity and Design Energy Input Fraction at | 0.3 | 10 | 26.667 | 113.89
0: 1.2898; 0.1: 0.282 | !Capacity and Design Energy Input Fraction at | 0.3 | 10 | 26.667 | 115
0: 1.2898; 0.1: 0.282 | !Capacity and Design Energy Input Fraction at | 0.3 | 10 | 26.667 | 116.11
0: 1.0347; 0.1: 0.288 | !Capacity and Design Energy Input Fraction at | 0.3 | 10 | 29.444 | 108.89
0: 1.0857; 0.1: 0.288 | !Capacity and Design Energy Input Fraction at | 0.3 | 10 | 29.444 | 111.67
0: 1.1347; 0.1: 0.288 | !Capacity and Design Energy Input Fraction at | 0.3 | 10 | 29.444 | 113.89
0: 1.1592; 0.1: 0.288 | !Capacity and Design Energy Input Fraction at | 0.3 | 10 | 29.444 | 115
0: 1.1796; 0.1: 0.288 | !Capacity and Design Energy Input Fraction at | 0.3 | 10 | 29.444 | 116.11
0: 0.902; 0.1: 0.294 | !Capacity and Design Energy Input Fraction at | 0.3 | 10 | 32.222 | 108.89
0: 0.9531; 0.1: 0.294 | !Capacity and Design Energy Input Fraction at | 0.3 | 10 | 32.222 | 111.67
0: 1.002; 0.1: 0.294 | !Capacity and Design Energy Input Fraction at | 0.3 | 10 | 32.222 | 113.89
0: 1.0245; 0.1: 0.294 | !Capacity and Design Energy Input Fraction at | 0.3 | 10 | 32.222 | 115
0: 1.0469; 0.1: 0.294 | !Capacity and Design Energy Input Fraction at | 0.3 | 10 | 32.222 | 116.11
0: 0.9878; 0.1: 0.396 | !Capacity and Design Energy Input Fraction at | 0.4 | 5.556 | 26.667 | 108.89
0: 1.0367; 0.1: 0.396 | !Capacity and Design Energy Input Fraction at | 0.4 | 5.556 | 26.667 | 111.67
0: 1.0837; 0.1: 0.396 | !Capacity and Design Energy Input Fraction at | 0.4 | 5.556 | 26.667 | 113.89
0: 1.1041; 0.1: 0.396 | !Capacity and Design Energy Input Fraction at | 0.4 | 5.556 | 26.667 | 115
0: 1.1265; 0.1: 0.396 | !Capacity and Design Energy Input Fraction at | 0.4 | 5.556 | 26.667 | 116.11
0: 0.8612; 0.1: 0.408 | !Capacity and Design Energy Input Fraction at | 0.4 | 5.556 | 29.444 | 108.89
0: 0.9102; 0.1: 0.408 | !Capacity and Design Energy Input Fraction at | 0.4 | 5.556 | 29.444 | 111.67
0: 0.9571; 0.1: 0.408 | !Capacity and Design Energy Input Fraction at | 0.4 | 5.556 | 29.444 | 113.89
0: 0.9796; 0.1: 0.408 | !Capacity and Design Energy Input Fraction at | 0.4 | 5.556 | 29.444 | 115
0: 1; 0.1: 0.408 | !Capacity and Design Energy Input Fraction at | 0.4 | 5.556 | 29.444 | 116.11
0: 0.7347; 0.1: 0.416 | !Capacity and Design Energy Input Fraction at | 0.4 | 5.556 | 32.222 | 108.89
0: 0.7857; 0.1: 0.416 | !Capacity and Design Energy Input Fraction at | 0.4 | 5.556 | 32.222 | 111.67
0: 0.8327; 0.1: 0.416 | !Capacity and Design Energy Input Fraction at | 0.4 | 5.556 | 32.222 | 113.89
0: 0.8531; 0.1: 0.416 | !Capacity and Design Energy Input Fraction at | 0.4 | 5.556 | 32.222 | 115
0: 0.8735; 0.1: 0.416 | !Capacity and Design Energy Input Fraction at | 0.4 | 5.556 | 32.222 | 116.11
0: 1.0102; 0.1: 0.392 | !Capacity and Design Energy Input Fraction at | 0.4 | 6.111 | 26.667 | 108.89
0: 1.0592; 0.1: 0.392 | !Capacity and Design Energy Input Fraction at | 0.4 | 6.111 | 26.667 | 111.67
0: 1.1061; 0.1: 0.392 | !Capacity and Design Energy Input Fraction at | 0.4 | 6.111 | 26.667 | 113.89
0: 1.1286; 0.1: 0.392 | !Capacity and Design Energy Input Fraction at | 0.4 | 6.111 | 26.667 | 115
0: 1.149; 0.1: 0.392 | !Capacity and Design Energy Input Fraction at | 0.4 | 6.111 | 26.667 | 116.11
0: 0.8837; 0.1: 0.404 | !Capacity and Design Energy Input Fraction at | 0.4 | 6.111 | 29.444 | 108.89
0: 0.9327; 0.1: 0.404 | !Capacity and Design Energy Input Fraction at | 0.4 | 6.111 | 29.444 | 111.67
0: 0.9776; 0.1: 0.404 | !Capacity and Design Energy Input Fraction at | 0.4 | 6.111 | 29.444 | 113.89
0: 1; 0.1: 0.404 | !Capacity and Design Energy Input Fraction at | 0.4 | 6.111 | 29.444 | 115
0: 1.0224; 0.1: 0.404 | !Capacity and Design Energy Input Fraction at | 0.4 | 6.111 | 29.444 | 116.11
0: 0.7571; 0.1: 0.416 | !Capacity and Design Energy Input Fraction at | 0.4 | 6.111 | 32.222 | 108.89
0: 0.8061; 0.1: 0.416 | !Capacity and Design Energy Input Fraction at | 0.4 | 6.111 | 32.222 | 111.67
0: 0.8531; 0.1: 0.416 | !Capacity and Design Energy Input Fraction at | 0.4 | 6.111 | 32.222 | 113.89
0: 0.8735; 0.1: 0.416 | !Capacity and Design Energy Input Fraction at | 0.4 | 6.111 | 32.222 | 115
0: 0.8959; 0.1: 0.416 | !Capacity and Design Energy Input Fraction at | 0.4 | 6.111 | 32.222 | 116.11
0: 1.0306; 0.1: 0.392 | !Capacity and Design Energy Input Fraction at | 0.4 | 6.667 | 26.667 | 108.89
0: 1.0816; 0.1: 0.392 | !Capacity and Design Energy Input Fraction at | 0.4 | 6.667 | 26.667 | 111.67
0: 1.1286; 0.1: 0.392 | !Capacity and Design Energy Input Fraction at | 0.4 | 6.667 | 26.667 | 113.89
0: 1.151; 0.1: 0.392 | !Capacity and Design Energy Input Fraction at | 0.4 | 6.667 | 26.667 | 115
0: 1.1714; 0.1: 0.392 | !Capacity and Design Energy Input Fraction at | 0.4 | 6.667 | 26.667 | 116.11
0: 0.9041; 0.1: 0.4 | !Capacity and Design Energy Input Fraction at | 0.4 | 6.667 | 29.444 | 108.89
0: 0.9531; 0.1: 0.4 | !Capacity and Design Energy Input Fraction at | 0.4 | 6.667 | 29.444 | 111.67
0: 1; 0.1: 0.4 | !Capacity and Design Energy Input Fraction at | 0.4 | 6.667 | 29.444 | 113.89
0: 1.0224; 0.1: 0.4 | !Capacity and Design Energy Input Fraction at | 0.4 | 6.667 | 29.444 | 115
0: 1.0449; 0.1: 0.4 | !Capacity and Design Energy Input Fraction at | 0.4 | 6.667 | 29.444 | 116.11
0: 0.7776; 0.1: 0.412 | !Capacity and Design Energy Input Fraction at | 0.4 | 6.667 | 32.222 | 108.89
0: 0.8265; 0.1: 0.412 | !Capacity and Design Energy Input Fraction at | 0.4 | 6.667 | 32.222 | 111.67
0: 0.8735; 0.1: 0.412 | !Capacity and Design Energy Input Fraction at | 0.4 | 6.667 | 32.222 | 113.89
0: 0.8959; 0.1: 0.412 | !Capacity and Design Energy Input Fraction at | 0.4 | 6.667 | 32.222 | 115
0: 0.9163; 0.1: 0.412 | !Capacity and Design Energy Input Fraction at | 0.4 | 6.667 | 32.222 | 116.11
0: 1.0531; 0.1: 0.388 | !Capacity and Design Energy Input Fraction at | 0.4 | 7.222 | 26.667 | 108.89
0: 1.1041; 0.1: 0.388 | !Capacity and Design Energy Input Fraction at | 0.4 | 7.222 | 26.667 | 111.67
0: 1.151; 0.1: 0.388 | !Capacity and Design Energy Input Fraction at | 0.4 | 7.222 | 26.667 | 113.89
0: 1.1735; 0.1: 0.388 | !Capacity and Design Energy Input Fraction at | 0.4 | 7.222 | 26.667 | 115
0: 1.1959; 0.1: 0.388 | !Capacity and Design Energy Input Fraction at | 0.4 | 7.222 | 26.667 | 116.11
0: 0.9245; 0.1: 0.396 | !Capacity and Design Energy Input Fraction at | 0.4 | 7.222 | 29.444 | 108.89
0: 0.9755; 0.1: 0.396 | !Capacity and Design Energy Input Fraction at | 0.4 | 7.222 | 29.444 | 111.67
0: 1.0224; 0.1: 0.396 | !Capacity and Design Energy Input Fraction at | 0.4 | 7.222 | 29.444 | 113.89
0: 1.0449; 0.1: 0.396 | !Capacity and Design Energy Input Fraction at | 0.4 | 7.222 | 29.444 | 115
0: 1.0673; 0.1: 0.396 | !Capacity and Design Energy Input Fraction at | 0.4 | 7.222 | 29.444 | 116.11
0: 0.798; 0.1: 0.408 | !Capacity and Design Energy Input Fraction at | 0.4 | 7.222 | 32.222 | 108.89
0: 0.8469; 0.1: 0.408 | !Capacity and Design Energy Input Fraction at | 0.4 | 7.222 | 32.222 | 111.67
0: 0.8939; 0.1: 0.408 | !Capacity and Design Energy Input Fraction at | 0.4 | 7.222 | 32.222 | 113.89
0: 0.9163; 0.1: 0.408 | !Capacity and Design Energy Input Fraction at | 0.4 | 7.222 | 32.222 | 115
0: 0.9388; 0.1: 0.408 | !Capacity and Design Energy Input Fraction at | 0.4 | 7.222 | 32.222 | 116.11
0: 1.0755; 0.1: 0.384 | !Capacity and Design Energy Input Fraction at | 0.4 | 7.778 | 26.667 | 108.89
0: 1.1265; 0.1: 0.384 | !Capacity and Design Energy Input Fraction at | 0.4 | 7.778 | 26.667 | 111.67
0: 1.1755; 0.1: 0.384 | !Capacity and Design Energy Input Fraction at | 0.4 | 7.778 | 26.667 | 113.89
0: 1.198; 0.1: 0.384 | !Capacity and Design Energy Input Fraction at | 0.4 | 7.778 | 26.667 | 115
0: 1.2184; 0.1: 0.384 | !Capacity and Design Energy Input Fraction at | 0.4 | 7.778 | 26.667 | 116.11
0: 0.9469; 0.1: 0.392 | !Capacity and Design Energy Input Fraction at | 0.4 | 7.778 | 29.444 | 108.89
0: 0.998; 0.1: 0.392 | !Capacity and Design Energy Input Fraction at | 0.4 | 7.778 | 29.444 | 111.67
0: 1.0449; 0.1: 0.392 | !Capacity and Design Energy Input Fraction at | 0.4 | 7.778 | 29.444 | 113.89
0: 1.0673; 0.1: 0.392 | !Capacity and Design Energy Input Fraction at | 0.4 | 7.778 | 29.444 | 115
0: 1.0898; 0.1: 0.392 | !Capacity and Design Energy Input Fraction at | 0.4 | 7.778 | 29.444 | 116.11
0: 0.8184; 0.1: 0.404 | !Capacity and Design Energy Input Fraction at | 0.4 | 7.778 | 32.222 | 108.89
0: 0.8694; 0.1: 0.404 | !Capacity and Design Energy Input Fraction at | 0.4 | 7.778 | 32.222 | 111.67
0: 0.9163; 0.1: 0.404 | !Capacity and Design Energy Input Fraction at | 0.4 | 7.778 | 32.222 | 113.89
0: 0.9388; 0.1: 0.404 | !Capacity and Design Energy Input Fraction at | 0.4 | 7.778 | 32.222 | 115
0: 0.9592; 0.1: 0.404 | !Capacity and Design Energy Input Fraction at | 0.4 | 7.778 | 32.222 | 116.11
0: 1.1204; 0.1: 0.38 | !Capacity and Design Energy Input Fraction at | 0.4 | 8.889 | 26.667 | 108.89
0: 1.1735; 0.1: 0.38 | !Capacity and Design Energy Input Fraction at | 0.4 | 8.889 | 26.667 | 111.67
0: 1.2204; 0.1: 0.38 | !Capacity and Design Energy Input Fraction at | 0.4 | 8.889 | 26.667 | 113.89
0: 1.2449; 0.1: 0.38 | !Capacity and Design Energy Input Fraction at | 0.4 | 8.889 | 26.667 | 115
0: 1.2673; 0.1: 0.38 | !Capacity and Design Energy Input Fraction at | 0.4 | 8.889 | 26.667 | 116.11
0: 0.9898; 0.1: 0.388 | !Capacity and Design Energy Input Fraction at | 0.4 | 8.889 | 29.444 | 108.89
0: 1.0408; 0.1: 0.388 | !Capacity and Design Energy Input Fraction at | 0.4 | 8.889 | 29.444 | 111.67
0: 1.0898; 0.1: 0.388 | !Capacity and Design Energy Input Fraction at | 0.4 | 8.889 | 29.444 | 113.89
0: 1.1122; 0.1: 0.388 | !Capacity and Design Energy Input Fraction at | 0.4 | 8.889 | 29.444 | 115
0: 1.1347; 0.1: 0.388 | !Capacity and Design Energy Input Fraction at | 0.4 | 8.889 | 29.444 | 116.11
0: 0.8592; 0.1: 0.4 | !Capacity and Design Energy Input Fraction at | 0.4 | 8.889 | 32.222 | 108.89
0: 0.9102; 0.1: 0.4 | !Capacity and Design Energy Input Fraction at | 0.4 | 8.889 | 32.222 | 111.67
0: 0.9592; 0.1: 0.4 | !Capacity and Design Energy Input Fraction at | 0.4 | 8.889 | 32.222 | 113.89
0: 0.9816; 0.1: 0.4 | !Capacity and Design Energy Input Fraction at | 0.4 | 8.889 | 32.222 | 115
0: 1.0041; 0.1: 0.4 | !Capacity and Design Energy Input Fraction at | 0.4 | 8.889 | 32.222 | 116.11
0: 1.1673; 0.1: 0.376 | !Capacity and Design Energy Input Fraction at | 0.4 | 10 | 26.667 | 108.89
0: 1.2204; 0.1: 0.376 | !Capacity and Design Energy Input Fraction at | 0.4 | 10 | 26.667 | 111.67
0: 1.2694; 0.1: 0.376 | !Capacity and Design Energy Input Fraction at | 0.4 | 10 | 26.667 | 113.89
0: 1.2898; 0.1: 0.376 | !Capacity and Design Energy Input Fraction at | 0.4 | 10 | 26.667 | 115
0: 1.2898; 0.1: 0.376 | !Capacity and Design Energy Input Fraction at | 0.4 | 10 | 26.667 | 116.11
0: 1.0347; 0.1: 0.384 | !Capacity and Design Energy Input Fraction at | 0.4 | 10 | 29.444 | 108.89
0: 1.0857; 0.1: 0.384 | !Capacity and Design Energy Input Fraction at | 0.4 | 10 | 29.444 | 111.67
0: 1.1347; 0.1: 0.384 | !Capacity and Design Energy Input Fraction at | 0.4 | 10 | 29.444 | 113.89
0: 1.1592; 0.1: 0.384 | !Capacity and Design Energy Input Fraction at | 0.4 | 10 | 29.444 | 115
0: 1.1796; 0.1: 0.384 | !Capacity and Design Energy Input Fraction at | 0.4 | 10 | 29.444 | 116.11
0: 0.902; 0.1: 0.392 | !Capacity and Design Energy Input Fraction at | 0.4 | 10 | 32.222 | 108.89
0: 0.9531; 0.1: 0.392 | !Capacity and Design Energy Input Fraction at | 0.4 | 10 | 32.222 | 111.67
0: 1.002; 0.1: 0.392 | !Capacity and Design Energy Input Fraction at | 0.4 | 10 | 32.222 | 113.89
0: 1.0245; 0.1: 0.392 | !Capacity and Design Energy Input Fraction at | 0.4 | 10 | 32.222 | 115
0: 1.0469; 0.1: 0.392 | !Capacity and Design Energy Input Fraction at | 0.4 | 10 | 32.222 | 116.11
0: 0.9878; 0.1: 0.495 | !Capacity and Design Energy Input Fraction at | 0.5 | 5.556 | 26.667 | 108.89
0: 1.0367; 0.1: 0.495 | !Capacity and Design Energy Input Fraction at | 0.5 | 5.556 | 26.667 | 111.67
0: 1.0837; 0.1: 0.495 | !Capacity and Design Energy Input Fraction at | 0.5 | 5.556 | 26.667 | 113.89
0: 1.1041; 0.1: 0.495 | !Capacity and Design Energy Input Fraction at | 0.5 | 5.556 | 26.667 | 115
0: 1.1265; 0.1: 0.495 | !Capacity and Design Energy Input Fraction at | 0.5 | 5.556 | 26.667 | 116.11
0: 0.8612; 0.1: 0.51 | !Capacity and Design Energy Input Fraction at | 0.5 | 5.556 | 29.444 | 108.89
0: 0.9102; 0.1: 0.51 | !Capacity and Design Energy Input Fraction at | 0.5 | 5.556 | 29.444 | 111.67
0: 0.9571; 0.1: 0.51 | !Capacity and Design Energy Input Fraction at | 0.5 | 5.556 | 29.444 | 113.89
0: 0.9796; 0.1: 0.51 | !Capacity and Design Energy Input Fraction at | 0.5 | 5.556 | 29.444 | 115
0: 1; 0.1: 0.51 | !Capacity and Design Energy Input Fraction at | 0.5 | 5.556 | 29.444 | 116.11
0: 0.7347; 0.1: 0.52 | !Capacity and Design Energy Input Fraction at | 0.5 | 5.556 | 32.222 | 108.89
0: 0.7857; 0.1: 0.52 | !Capacity and Design Energy Input Fraction at | 0.5 | 5.556 | 32.222 | 111.67
0: 0.8327; 0.1: 0.52 | !Capacity and Design Energy Input Fraction at | 0.5 | 5.556 | 32.222 | 113.89
0: 0.8531; 0.1: 0.52 | !Capacity and Design Energy Input Fraction at | 0.5 | 5.556 | 32.222 | 115
0: 0.8735; 0.1: 0.52 | !Capacity and Design Energy Input Fraction at | 0.5 | 5.556 | 32.222 | 116.11
0: 1.0102; 0.1: 0.49 | !Capacity and Design Energy Input Fraction at | 0.5 | 6.111 | 26.667 | 108.89
0: 1.0592; 0.1: 0.49 | !Capacity and Design Energy Input Fraction at | 0.5 | 6.111 | 26.667 | 111.67
0: 1.1061; 0.1: 0.49 | !Capacity and Design Energy Input Fraction at | 0.5 | 6.111 | 26.667 | 113.89
0: 1.1286; 0.1: 0.49 | !Capacity and Design Energy Input Fraction at | 0.5 | 6.111 | 26.667 | 115
0: 1.149; 0.1: 0.49 | !Capacity and Design Energy Input Fraction at | 0.5 | 6.111 | 26.667 | 116.11
0: 0.8837; 0.1: 0.505 | !Capacity and Design Energy Input Fraction at | 0.5 | 6.111 | 29.444 | 108.89
0: 0.9327; 0.1: 0.505 | !Capacity and Design Energy Input Fraction at | 0.5 | 6.111 | 29.444 | 111.67
0: 0.9776; 0.1: 0.505 | !Capacity and Design Energy Input Fraction at | 0.5 | 6.111 | 29.444 | 113.89
0: 1; 0.1: 0.505 | !Capacity and Design Energy Input Fraction at | 0.5 | 6.111 | 29.444 | 115
0: 1.0224; 0.1: 0.505 | !Capacity and Design Energy Input Fraction at | 0.5 | 6.111 | 29.444 | 116.11
0: 0.7571; 0.1: 0.52 | !Capacity and Design Energy Input Fraction at | 0.5 | 6.111 | 32.222 | 108.89
0: 0.8061; 0.1: 0.52 | !Capacity and Design Energy Input Fraction at | 0.5 | 6.111 | 32.222 | 111.67
0: 0.8531; 0.1: 0.52 | !Capacity and Design Energy Input Fraction at | 0.5 | 6.111 | 32.222 | 113.89
0: 0.8735; 0.1: 0.52 | !Capacity and Design Energy Input Fraction at | 0.5 | 6.111 | 32.222 | 115
0: 0.8959; 0.1: 0.52 | !Capacity and Design Energy Input Fraction at | 0.5 | 6.111 | 32.222 | 116.11
0: 1.0306; 0.1: 0.49 | !Capacity and Design Energy Input Fraction at | 0.5 | 6.667 | 26.667 | 108.89
0: 1.0816; 0.1: 0.49 | !Capacity and Design Energy Input Fraction at | 0.5 | 6.667 | 26.667 | 111.67
0: 1.1286; 0.1: 0.49 | !Capacity and Design Energy Input Fraction at | 0.5 | 6.667 | 26.667 | 113.89
0: 1.151; 0.1: 0.49 | !Capacity and Design Energy Input Fraction at | 0.5 | 6.667 | 26.667 | 115
0: 1.1714; 0.1: 0.49 | !Capacity and Design Energy Input Fraction at | 0.5 | 6.667 | 26.667 | 116.11
0: 0.9041; 0.1: 0.5 | !Capacity and Design Energy Input Fraction at | 0.5 | 6.667 | 29.444 | 108.89
0: 0.9531; 0.1: 0.5 | !Capacity and Design Energy Input Fraction at | 0.5 | 6.667 | 29.444 | 111.67
0: 1; 0.1: 0.5 | !Capacity and Design Energy Input Fraction at | 0.5 | 6.667 | 29.444 | 113.89
0: 1.0224; 0.1: 0.5 | !Capacity and Design Energy Input Fraction at | 0.5 | 6.667 | 29.444 | 115
0: 1.0449; 0.1: 0.5 | !Capacity and Design Energy Input Fraction at | 0.5 | 6.667 | 29.444 | 116.11
0: 0.7776; 0.1: 0.515 | !Capacity and Design Energy Input Fraction at | 0.5 | 6.667 | 32.222 | 108.89
0: 0.8265; 0.1: 0.515 | !Capacity and Design Energy Input Fraction at | 0.5 | 6.667 | 32.222 | 111.67
0: 0.8735; 0.1: 0.515 | !Capacity and Design Energy Input Fraction at | 0.5 | 6.667 | 32.222 | 113.89
0: 0.8959; 0.1: 0.515 | !Capacity and Design Energy Input Fraction at | 0.5 | 6.667 | 32.222 | 115
0: 0.9163; 0.1: 0.515 | !Capacity and Design Energy Input Fraction at | 0.5 | 6.667 | 32.222 | 116.11
0: 1.0531; 0.1: 0.485 | !Capacity and Design Energy Input Fraction at | 0.5 | 7.222 | 26.667 | 108.89
0: 1.1041; 0.1: 0.485 | !Capacity and Design Energy Input Fraction at | 0.5 | 7.222 | 26.667 | 111.67
0: 1.151; 0.1: 0.485 | !Capacity and Design Energy Input Fraction at | 0.5 | 7.222 | 26.667 | 113.89
0: 1.1735; 0.1: 0.485 | !Capacity and Design Energy Input Fraction at | 0.5 | 7.222 | 26.667 | 115
0: 1.1959; 0.1: 0.485 | !Capacity and Design Energy Input Fraction at | 0.5 | 7.222 | 26.667 | 116.11
0: 0.9245; 0.1: 0.495 | !Capacity and Design Energy Input Fraction at | 0.5 | 7.222 | 29.444 | 108.89
0: 0.9755; 0.1: 0.495 | !Capacity and Design Energy Input Fraction at | 0.5 | 7.222 | 29.444 | 111.67
0: 1.0224; 0.1: 0.495 | !Capacity and Design Energy Input Fraction at | 0.5 | 7.222 | 29.444 | 113.89
0: 1.0449; 0.1: 0.495 | !Capacity and Design Energy Input Fraction at | 0.5 | 7.222 | 29.444 | 115
0: 1.0673; 0.1: 0.495 | !Capacity and Design Energy Input Fraction at | 0.5 | 7.222 | 29.444 | 116.11
0: 0.798; 0.1: 0.51 | !Capacity and Design Energy Input Fraction at | 0.5 | 7.222 | 32.222 | 108.89
0: 0.8469; 0.1: 0.51 | !Capacity and Design Energy Input Fraction at | 0.5 | 7.222 | 32.222 | 111.67
0: 0.8939; 0.1: 0.51 | !Capacity and Design Energy Input Fraction at | 0.5 | 7.222 | 32.222 | 113.89
0: 0.9163; 0.1: 0.51 | !Capacity and Design Energy Input Fraction at | 0.5 | 7.222 | 32.222 | 115
0: 0.9388; 0.1: 0.51 | !Capacity and Design Energy Input Fraction at | 0.5 | 7.222 | 32.222 | 116.11
0: 1.0755; 0.1: 0.48 | !Capacity and Design Energy Input Fraction at | 0.5 | 7.778 | 26.667 | 108.89
0: 1.1265; 0.1: 0.48 | !Capacity and Design Energy Input Fraction at | 0.5 | 7.778 | 26.667 | 111.67
0: 1.1755; 0.1: 0.48 | !Capacity and Design Energy Input Fraction at | 0.5 | 7.778 | 26.667 | 113.89
0: 1.198; 0.1: 0.48 | !Capacity and Design Energy Input Fraction at | 0.5 | 7.778 | 26.667 | 115
0: 1.2184; 0.1: 0.48 | !Capacity and Design Energy Input Fraction at | 0.5 | 7.778 | 26.667 | 116.11
0: 0.9469; 0.1: 0.49 | !Capacity and Design Energy Input Fraction at | 0.5 | 7.778 | 29.444 | 108.89
0: 0.998; 0.1: 0.49 | !Capacity and Design Energy Input Fraction at | 0.5 | 7.778 | 29.444 | 111.67
0: 1.0449; 0.1: 0.49 | !Capacity and Design Energy Input Fraction at | 0.5 | 7.778 | 29.444 | 113.89
0: 1.0673; 0.1: 0.49 | !Capacity and Design Energy Input Fraction at | 0.5 | 7.778 | 29.444 | 115
0: 1.0898; 0.1: 0.49 | !Capacity and Design Energy Input Fraction at | 0.5 | 7.778 | 29.444 | 116.11
0: 0.8184; 0.1: 0.505 | !Capacity and Design Energy Input Fraction at | 0.5 | 7.778 | 32.222 | 108.89
0: 0.8694; 0.1: 0.505 | !Capacity and Design Energy Input Fraction at | 0.5 | 7.778 | 32.222 | 111.67
0: 0.9163; 0.1: 0.505 | !Capacity and Design Energy Input Fraction at | 0.5 | 7.778 | 32.222 | 113.89
0: 0.9388; 0.1: 0.505 | !Capacity and Design Energy Input Fraction at | 0.5 | 7.778 | 32.222 | 115
0: 0.9592; 0.1: 0.505 | !Capacity and Design Energy Input Fraction at | 0.5 | 7.778 | 32.222 | 116.11
0: 1.1204; 0.1: 0.475 | !Capacity and Design Energy Input Fraction at | 0.5 | 8.889 | 26.667 | 108.89
0: 1.1735; 0.1: 0.475 | !Capacity and Design Energy Input Fraction at | 0.5 | 8.889 | 26.667 | 111.67
0: 1.2204; 0.1: 0.475 | !Capacity and Design Energy Input Fraction at | 0.5 | 8.889 | 26.667 | 113.89
0: 1.2449; 0.1: 0.475 | !Capacity and Design Energy Input Fraction at | 0.5 | 8.889 | 26.667 | 115
0: 1.2673; 0.1: 0.475 | !Capacity and Design Energy Input Fraction at | 0.5 | 8.889 | 26.667 | 116.11
0: 0.9898; 0.1: 0.485 | !Capacity and Design Energy Input Fraction at | 0.5 | 8.889 | 29.444 | 108.89
0: 1.0408; 0.1: 0.485 | !Capacity and Design Energy Input Fraction at | 0.5 | 8.889 | 29.444 | 111.67
0: 1.0898; 0.1: 0.485 | !Capacity and Design Energy Input Fraction at | 0.5 | 8.889 | 29.444 | 113.89
0: 1.1122; 0.1: 0.485 | !Capacity and Design Energy Input Fraction at | 0.5 | 8.889 | 29.444 | 115
0: 1.1347; 0.1: 0.485 | !Capacity and Design Energy Input Fraction at | 0.5 | 8.889 | 29.444 | 116.11
0: 0.8592; 0.1: 0.5 | !Capacity and Design Energy Input Fraction at | 0.5 | 8.889 | 32.222 | 108.89
0: 0.9102; 0.1: 0.5 | !Capacity and Design Energy Input Fraction at | 0.5 | 8.889 | 32.222 | 111.67
0: 0.9592; 0.1: 0.5 | !Capacity and Design Energy Input Fraction at | 0.5 | 8.889 | 32.222 | 113.89
0: 0.9816; 0.1: 0.5 | !Capacity and Design Energy Input Fraction at | 0.5 | 8.889 | 32.222 | 115
0: 1.0041; 0.1: 0.5 | !Capacity and Design Energy Input Fraction at | 0.5 | 8.889 | 32.222 | 116.11
0: 1.1673; 0.1: 0.47 | !Capacity and Design Energy Input Fraction at | 0.5 | 10 | 26.667 | 108.89
0: 1.2204; 0.1: 0.47 | !Capacity and Design Energy Input Fraction at | 0.5 | 10 | 26.667 | 111.67
0: 1.2694; 0.1: 0.47 | !Capacity and Design Energy Input Fraction at | 0.5 | 10 | 26.667 | 113.89
0: 1.2898; 0.1: 0.47 | !Capacity and Design Energy Input Fraction at | 0.5 | 10 | 26.667 | 115
0: 1.2898; 0.1: 0.47 | !Capacity and Design Energy Input Fraction at | 0.5 | 10 | 26.667 | 116.11
0: 1.0347; 0.1: 0.48 | !Capacity and Design Energy Input Fraction at | 0.5 | 10 | 29.444 | 108.89
0: 1.0857; 0.1: 0.48 | !Capacity and Design Energy Input Fraction at | 0.5 | 10 | 29.444 | 111.67
0: 1.1347; 0.1: 0.48 | !Capacity and Design Energy Input Fraction at | 0.5 | 10 | 29.444 | 113.89
0: 1.1592; 0.1: 0.48 | !Capacity and Design Energy Input Fraction at | 0.5 | 10 | 29.444 | 115
0: 1.1796; 0.1: 0.48 | !Capacity and Design Energy Input Fraction at | 0.5 | 10 | 29.444 | 116.11
0: 0.902; 0.1: 0.49 | !Capacity and Design Energy Input Fraction at | 0.5 | 10 | 32.222 | 108.89
0: 0.9531; 0.1: 0.49 | !Capacity and Design Energy Input Fraction at | 0.5 | 10 | 32.222 | 111.67
0: 1.002; 0.1: 0.49 | !Capacity and Design Energy Input Fraction at | 0.5 | 10 | 32.222 | 113.89
0: 1.0245; 0.1: 0.49 | !Capacity and Design Energy Input Fraction at | 0.5 | 10 | 32.222 | 115
0: 1.0469; 0.1: 0.49 | !Capacity and Design Energy Input Fraction at | 0.5 | 10 | 32.222 | 116.11
0: 0.9878; 0.1: 0.594 | !Capacity and Design Energy Input Fraction at | 0.6 | 5.556 | 26.667 | 108.89
0: 1.0367; 0.1: 0.594 | !Capacity and Design Energy Input Fraction at | 0.6 | 5.556 | 26.667 | 111.67
0: 1.0837; 0.1: 0.594 | !Capacity and Design Energy Input Fraction at | 0.6 | 5.556 | 26.667 | 113.89
0: 1.1041; 0.1: 0.594 | !Capacity and Design Energy Input Fraction at | 0.6 | 5.556 | 26.667 | 115
0: 1.1265; 0.1: 0.594 | !Capacity and Design Energy Input Fraction at | 0.6 | 5.556 | 26.667 | 116.11
0: 0.8612; 0.1: 0.612 | !Capacity and Design Energy Input Fraction at | 0.6 | 5.556 | 29.444 | 108.89
0: 0.9102; 0.1: 0.612 | !Capacity and Design Energy Input Fraction at | 0.6 | 5.556 | 29.444 | 111.67
0: 0.9571; 0.1: 0.612 | !Capacity and Design Energy Input Fraction at | 0.6 | 5.556 | 29.444 | 113.89
0: 0.9796; 0.1: 0.612 | !Capacity and Design Energy Input Fraction at | 0.6 | 5.556 | 29.444 | 115
0: 1; 0.1: 0.612 | !Capacity and Design Energy Input Fraction at | 0.6 | 5.556 | 29.444 | 116.11
0: 0.7347; 0.1: 0.624 | !Capacity and Design Energy Input Fraction at | 0.6 | 5.556 | 32.222 | 108.89
0: 0.7857; 0.1: 0.624 | !Capacity and Design Energy Input Fraction at | 0.6 | 5.556 | 32.222 | 111.67
0: 0.8327; 0.1: 0.624 | !Capacity and Design Energy Input Fraction at | 0.6 | 5.556 | 32.222 | 113.89
0: 0.8531; 0.1: 0.624 | !Capacity and Design Energy Input Fraction at | 0.6 | 5.556 | 32.222 | 115
0: 0.8735; 0.1: 0.624 | !Capacity and Design Energy Input Fraction at | 0.6 | 5.556 | 32.222 | 116.11
0: 1.0102; 0.1: 0.588 | !Capacity and Design Energy Input Fraction at | 0.6 | 6.111 | 26.667 | 108.89
0: 1.0592; 0.1: 0.588 | !Capacity and Design Energy Input Fraction at | 0.6 | 6.111 | 26.667 | 111.67
0: 1.1061; 0.1: 0.588 | !Capacity and Design Energy Input Fraction at | 0.6 | 6.111 | 26.667 | 113.89
0: 1.1286; 0.1: 0.588 | !Capacity and Design Energy Input Fraction at | 0.6 | 6.111 | 26.667 | 115
0: 1.149; 0.1: 0.588 | !Capacity and Design Energy Input Fraction at | 0.6 | 6.111 | 26.667 | 116.11
0: 0.8837; 0.1: 0.606 | !Capacity and Design Energy Input Fraction at | 0.6 | 6.111 | 29.444 | 108.89
0: 0.9327; 0.1: 0.606 | !Capacity and Design Energy Input Fraction at | 0.6 | 6.111 | 29.444 | 111.67
0: 0.9776; 0.1: 0.606 | !Capacity and Design Energy Input Fraction at | 0.6 | 6.111 | 29.444 | 113.89
0: 1; 0.1: 0.606 | !Capacity and Design Energy Input Fraction at | 0.6 | 6.111 | 29.444 | 115
0: 1.0224; 0.1: 0.606 | !Capacity and Design Energy Input Fraction at | 0.6 | 6.111 | 29.444 | 116.11
0: 0.7571; 0.1: 0.624 | !Capacity and Design Energy Input Fraction at | 0.6 | 6.111 | 32.222 | 108.89
0: 0.8061; 0.1: 0.624 | !Capacity and Design Energy Input Fraction at | 0.6 | 6.111 | 32.222 | 111.67
0: 0.8531; 0.1: 0.624 | !Capacity and Design Energy Input Fraction at | 0.6 | 6.111 | 32.222 | 113.89
0: 0.8735; 0.1: 0.624 | !Capacity and Design Energy Input Fraction at | 0.6 | 6.111 | 32.222 | 115
0: 0.8959; 0.1: 0.624 | !Capacity and Design Energy Input Fraction at | 0.6 | 6.111 | 32.222 | 116.11
0: 1.0306; 0.1: 0.588 | !Capacity and Design Energy Input Fraction at | 0.6 | 6.667 | 26.667 | 108.89
0: 1.0816; 0.1: 0.588 | !Capacity and Design Energy Input Fraction at | 0.6 | 6.667 | 26.667 | 111.67
0: 1.1286; 0.1: 0.588 | !Capacity and Design Energy Input Fraction at | 0.6 | 6.667 | 26.667 | 113.89
0: 1.151; 0.1: 0.588 | !Capacity and Design Energy Input Fraction at | 0.6 | 6.667 | 26.667 | 115
0: 1.1714; 0.1: 0.588 | !Capacity and Design Energy Input Fraction at | 0.6 | 6.667 | 26.667 | 116.11
0: 0.9041; 0.1: 0.6 | !Capacity and Design Energy Input Fraction at | 0.6 | 6.667 | 29.444 | 108.89
0: 0.9531; 0.1: 0.6 | !Capacity and Design Energy Input Fraction at | 0.6 | 6.667 | 29.444 | 111.67
0: 1; 0.1: 0.6 | !Capacity and Design Energy Input Fraction at | 0.6 | 6.667 | 29.444 | 113.89
0: 1.0224; 0.1: 0.6 | !Capacity and Design Energy Input Fraction at | 0.6 | 6.667 | 29.444 | 115
0: 1.0449; 0.1: 0.6 | !Capacity and Design Energy Input Fraction at | 0.6 | 6.667 | 29.444 | 116.11
0: 0.7776; 0.1: 0.618 | !Capacity and Design Energy Input Fraction at | 0.6 | 6.667 | 32.222 | 108.89
0: 0.8265; 0.1: 0.618 | !Capacity and Design Energy Input Fraction at | 0.6 | 6.667 | 32.222 | 111.67
0: 0.8735; 0.1: 0.618 | !Capacity and Design Energy Input Fraction at | 0.6 | 6.667 | 32.222 | 113.89
0: 0.8959; 0.1: 0.618 | !Capacity and Design Energy Input Fraction at | 0.6 | 6.667 | 32.222 | 115
0: 0.9163; 0.1: 0.618 | !Capacity and Design Energy Input Fraction at | 0.6 | 6.667 | 32.222 | 116.11
0: 1.0531; 0.1: 0.582 | !Capacity and Design Energy Input Fraction at | 0.6 | 7.222 | 26.667 | 108.89
0: 1.1041; 0.1: 0.582 | !Capacity and Design Energy Input Fraction at | 0.6 | 7.222 | 26.667 | 111.67
0: 1.151; 0.1: 0.582 | !Capacity and Design Energy Input Fraction at | 0.6 | 7.222 | 26.667 | 113.89
0: 1.1735; 0.1: 0.582 | !Capacity and Design Energy Input Fraction at | 0.6 | 7.222 | 26.667 | 115
0: 1.1959; 0.1: 0.582 | !Capacity and Design Energy Input Fraction at | 0.6 | 7.222 | 26.667 | 116.11
0: 0.9245; 0.1: 0.594 | !Capacity and Design Energy Input Fraction at | 0.6 | 7.222 | 29.444 | 108.89
0: 0.9755; 0.1: 0.594 | !Capacity and Design Energy Input Fraction at | 0.6 | 7.222 | 29.444 | 111.67
0: 1.0224; 0.1: 0.594 | !Capacity and Design Energy Input Fraction at | 0.6 | 7.222 | 29.444 | 113.89
0: 1.0449; 0.1: 0.594 | !Capacity and Design Energy Input Fraction at | 0.6 | 7.222 | 29.444 | 115
0: 1.0673; 0.1: 0.594 | !Capacity and Design Energy Input Fraction at | 0.6 | 7.222 | 29.444 | 116.11
0: 0.798; 0.1: 0.612 | !Capacity and Design Energy Input Fraction at | 0.6 | 7.222 | 32.222 | 108.89
0: 0.8469; 0.1: 0.612 | !Capacity and Design Energy Input Fraction at | 0.6 | 7.222 | 32.222 | 111.67
0: 0.8939; 0.1: 0.612 | !Capacity and Design Energy Input Fraction at | 0.6 | 7.222 | 32.222 | 113.89
0: 0.9163; 0.1: 0.612 | !Capacity and Design Energy Input Fraction at | 0.6 | 7.222 | 32.222 | 115
0: 0.9388; 0.1: 0.612 | !Capacity and Design Energy Input Fraction at | 0.6 | 7.222 | 32.222 | 116.11
0: 1.0755; 0.1: 0.576 | !Capacity and Design Energy Input Fraction at | 0.6 | 7.778 | 26.667 | 108.89
0: 1.1265; 0.1: 0.576 | !Capacity and Design Energy Input Fraction at | 0.6 | 7.778 | 26.667 | 111.67
0: 1.1755; 0.1: 0.576 | !Capacity and Design Energy Input Fraction at | 0.6 | 7.778 | 26.667 | 113.89
0: 1.198; 0.1: 0.576 | !Capacity and Design Energy Input Fraction at | 0.6 | 7.778 | 26.667 | 115
0: 1.2184; 0.1: 0.576 | !Capacity and Design Energy Input Fraction at | 0.6 | 7.778 | 26.667 | 116.11
0: 0.9469; 0.1: 0.588 | !Capacity and Design Energy Input Fraction at | 0.6 | 7.778 | 29.444 | 108.89
0: 0.998; 0.1: 0.588 | !Capacity and Design Energy Input Fraction at | 0.6 | 7.778 | 29.444 | 111.67
0: 1.0449; 0.1: 0.588 | !Capacity and Design Energy Input Fraction at | 0.6 | 7.778 | 29.444 | 113.89
0: 1.0673; 0.1: 0.588 | !Capacity and Design Energy Input Fraction at | 0.6 | 7.778 | 29.444 | 115
0: 1.0898; 0.1: 0.588 | !Capacity and Design Energy Input Fraction at | 0.6 | 7.778 | 29.444 | 116.11
0: 0.8184; 0.1: 0.606 | !Capacity and Design Energy Input Fraction at | 0.6 | 7.778 | 32.222 | 108.89
0: 0.8694; 0.1: 0.606 | !Capacity and Design Energy Input Fraction at | 0.6 | 7.778 | 32.222 | 111.67
0: 0.9163; 0.1: 0.606 | !Capacity and Design Energy Input Fraction at | 0.6 | 7.778 | 32.222 | 113.89
0: 0.9388; 0.1: 0.606 | !Capacity and Design Energy Input Fraction at | 0.6 | 7.778 | 32.222 | 115
0: 0.9592; 0.1: 0.606 | !Capacity and Design Energy Input Fraction at | 0.6 | 7.778 | 32.222 | 116.11
0: 1.1204; 0.1: 0.57 | !Capacity and Design Energy Input Fraction at | 0.6 | 8.889 | 26.667 | 108.89
0: 1.1735; 0.1: 0.57 | !Capacity and Design Energy Input Fraction at | 0.6 | 8.889 | 26.667 | 111.67
0: 1.2204; 0.1: 0.57 | !Capacity and Design Energy Input Fraction at | 0.6 | 8.889 | 26.667 | 113.89
0: 1.2449; 0.1: 0.57 | !Capacity and Design Energy Input Fraction at | 0.6 | 8.889 | 26.667 | 115
0: 1.2673; 0.1: 0.57 | !Capacity and Design Energy Input Fraction at | 0.6 | 8.889 | 26.667 | 116.11
0: 0.9898; 0.1: 0.582 | !Capacity and Design Energy Input Fraction at | 0.6 | 8.889 | 29.444 | 108.89
0: 1.0408; 0.1: 0.582 | !Capacity and Design Energy Input Fraction at | 0.6 | 8.889 | 29.444 | 111.67
0: 1.0898; 0.1: 0.582 | !Capacity and Design Energy Input Fraction at | 0.6 | 8.889 | 29.444 | 113.89
0: 1.1122; 0.1: 0.582 | !Capacity and Design Energy Input Fraction at | 0.6 | 8.889 | 29.444 | 115
0: 1.1347; 0.1: 0.582 | !Capacity and Design Energy Input Fraction at | 0.6 | 8.889 | 29.444 | 116.11
0: 0.8592; 0.1: 0.6 | !Capacity and Design Energy Input Fraction at | 0.6 | 8.889 | 32.222 | 108.89
0: 0.9102; 0.1: 0.6 | !Capacity and Design Energy Input Fraction at | 0.6 | 8.889 | 32.222 | 111.67
0: 0.9592; 0.1: 0.6 | !Capacity and Design Energy Input Fraction at | 0.6 | 8.889 | 32.222 | 113.89
0: 0.9816; 0.1: 0.6 | !Capacity and Design Energy Input Fraction at | 0.6 | 8.889 | 32.222 | 115
0: 1.0041; 0.1: 0.6 | !Capacity and Design Energy Input Fraction at | 0.6 | 8.889 | 32.222 | 116.11
0: 1.1673; 0.1: 0.564 | !Capacity and Design Energy Input Fraction at | 0.6 | 10 | 26.667 | 108.89
0: 1.2204; 0.1: 0.564 | !Capacity and Design Energy Input Fraction at | 0.6 | 10 | 26.667 | 111.67
0: 1.2694; 0.1: 0.564 | !Capacity and Design Energy Input Fraction at | 0.6 | 10 | 26.667 | 113.89
0: 1.2898; 0.1: 0.564 | !Capacity and Design Energy Input Fraction at | 0.6 | 10 | 26.667 | 115
0: 1.2898; 0.1: 0.564 | !Capacity and Design Energy Input Fraction at | 0.6 | 10 | 26.667 | 116.11
0: 1.0347; 0.1: 0.576 | !Capacity and Design Energy Input Fraction at | 0.6 | 10 | 29.444 | 108.89
0: 1.0857; 0.1: 0.576 | !Capacity and Design Energy Input Fraction at | 0.6 | 10 | 29.444 | 111.67
0: 1.1347; 0.1: 0.576 | !Capacity and Design Energy Input Fraction at | 0.6 | 10 | 29.444 | 113.89
0: 1.1592; 0.1: 0.576 | !Capacity and Design Energy Input Fraction at | 0.6 | 10 | 29.444 | 115
0: 1.1796; 0.1: 0.576 | !Capacity and Design Energy Input Fraction at | 0.6 | 10 | 29.444 | 116.11
0: 0.902; 0.1: 0.588 | !Capacity and Design Energy Input Fraction at | 0.6 | 10 | 32.222 | 108.89
0: 0.9531; 0.1: 0.588 | !Capacity and Design Energy Input Fraction at | 0.6 | 10 | 32.222 | 111.67
0: 1.002; 0.1: 0.588 | !Capacity and Design Energy Input Fraction at | 0.6 | 10 | 32.222 | 113.89
0: 1.0245; 0.1: 0.588 | !Capacity and Design Energy Input Fraction at | 0.6 | 10 | 32.222 | 115
0: 1.0469; 0.1: 0.588 | !Capacity and Design Energy Input Fraction at | 0.6 | 10 | 32.222 | 116.11
0: 0.9878; 0.1: 0.693 | !Capacity and Design Energy Input Fraction at | 0.7 | 5.556 | 26.667 | 108.89
0: 1.0367; 0.1: 0.693 | !Capacity and Design Energy Input Fraction at | 0.7 | 5.556 | 26.667 | 111.67
0: 1.0837; 0.1: 0.693 | !Capacity and Design Energy Input Fraction at | 0.7 | 5.556 | 26.667 | 113.89
0: 1.1041; 0.1: 0.693 | !Capacity and Design Energy Input Fraction at | 0.7 | 5.556 | 26.667 | 115
0: 1.1265; 0.1: 0.693 | !Capacity and Design Energy Input Fraction at | 0.7 | 5.556 | 26.667 | 116.11
0: 0.8612; 0.1: 0.714 | !Capacity and Design Energy Input Fraction at | 0.7 | 5.556 | 29.444 | 108.89
0: 0.9102; 0.1: 0.714 | !Capacity and Design Energy Input Fraction at | 0.7 | 5.556 | 29.444 | 111.67
0: 0.9571; 0.1: 0.714 | !Capacity and Design Energy Input Fraction at | 0.7 | 5.556 | 29.444 | 113.89
0: 0.9796; 0.1: 0.714 | !Capacity and Design Energy Input Fraction at | 0.7 | 5.556 | 29.444 | 115
0: 1; 0.1: 0.714 | !Capacity and Design Energy Input Fraction at | 0.7 | 5.556 | 29.444 | 116.11
0: 0.7347; 0.1: 0.728 | !Capacity and Design Energy Input Fraction at | 0.7 | 5.556 | 32.222 | 108.89
0: 0.7857; 0.1: 0.728 | !Capacity and Design Energy Input Fraction at | 0.7 | 5.556 | 32.222 | 111.67
0: 0.8327; 0.1: 0.728 | !Capacity and Design Energy Input Fraction at | 0.7 | 5.556 | 32.222 | 113.89
0: 0.8531; 0.1: 0.728 | !Capacity and Design Energy Input Fraction at | 0.7 | 5.556 | 32.222 | 115
0: 0.8735; 0.1: 0.728 | !Capacity and Design Energy Input Fraction at | 0.7 | 5.556 | 32.222 | 116.11
0: 1.0102; 0.1: 0.686 | !Capacity and Design Energy Input Fraction at | 0.7 | 6.111 | 26.667 | 108.89
0: 1.0592; 0.1: 0.686 | !Capacity and Design Energy Input Fraction at | 0.7 | 6.111 | 26.667 | 111.67
0: 1.1061; 0.1: 0.686 | !Capacity and Design Energy Input Fraction at | 0.7 | 6.111 | 26.667 | 113.89
0: 1.1286; 0.1: 0.686 | !Capacity and Design Energy Input Fraction at | 0.7 | 6.111 | 26.667 | 115
0: 1.149; 0.1: 0.686 | !Capacity and Design Energy Input Fraction at | 0.7 | 6.111 | 26.667 | 116.11
0: 0.8837; 0.1: 0.707 | !Capacity and Design Energy Input Fraction at | 0.7 | 6.111 | 29.444 | 108.89
0: 0.9327; 0.1: 0.707 | !Capacity and Design Energy Input Fraction at | 0.7 | 6.111 | 29.444 | 111.67
0: 0.9776; 0.1: 0.707 | !Capacity and Design Energy Input Fraction at | 0.7 | 6.111 | 29.444 | 113.89
0: 1; 0.1: 0.707 | !Capacity and Design Energy Input Fraction at | 0.7 | 6.111 | 29.444 | 115
0: 1.0224; 0.1: 0.707 | !Capacity and Design Energy Input Fraction at | 0.7 | 6.111 | 29.444 | 116.11
0: 0.7571; 0.1: 0.728 | !Capacity and Design Energy Input Fraction at | 0.7 | 6.111 | 32.222 | 108.89
0: 0.8061; 0.1: 0.728 | !Capacity and Design Energy Input Fraction at | 0.7 | 6.111 | 32.222 | 111.67
0: 0.8531; 0.1: 0.728 | !Capacity and Design Energy Input Fraction at | 0.7 | 6.111 | 32.222 | 113.89
0: 0.8735; 0.1: 0.728 | !Capacity and Design Energy Input Fraction at | 0.7 | 6.111 | 32.222 | 115
0: 0.8959; 0.1: 0.728 | !Capacity and Design Energy Input Fraction at | 0.7 | 6.111 | 32.222 | 116.11
0: 1.0306; 0.1: 0.686 | !Capacity and Design Energy Input Fraction at | 0.7 | 6.667 | 26.667 | 108.89
0: 1.0816; 0.1: 0.686 | !Capacity and Design Energy Input Fraction at | 0.7 | 6.667 | 26.667 | 111.67
0: 1.1286; 0.1: 0.686 | !Capacity and Design Energy Input Fraction at | 0.7 | 6.667 | 26.667 | 113.89
0: 1.151; 0.1: 0.686 | !Capacity and Design Energy Input Fraction at | 0.7 | 6.667 | 26.667 | 115
0: 1.1714; 0.1: 0.686 | !Capacity and Design Energy Input Fraction at | 0.7 | 6.667 | 26.667 | 116.11
0: 0.9041; 0.1: 0.7 | !Capacity and Design Energy Input Fraction at | 0.7 | 6.667 | 29.444 | 108.89
0: 0.9531; 0.1: 0.7 | !Capacity and Design Energy Input Fraction at | 0.7 | 6.667 | 29.444 | 111.67
0: 1; 0.1: 0.7 | !Capacity and Design Energy Input Fraction at | 0.7 | 6.667 | 29.444 | 113.89
0: 1.0224; 0.1: 0.7 | !Capacity and Design Energy Input Fraction at | 0.7 | 6.667 | 29.444 | 115
0: 1.0449; 0.1: 0.7 | !Capacity and Design Energy Input Fraction at | 0.7 | 6.667 | 29.444 | 116.11
0: 0.7776; 0.1: 0.721 | !Capacity and Design Energy Input Fraction at | 0.7 | 6.667 | 32.222 | 108.89
0: 0.8265; 0.1: 0.721 | !Capacity and Design Energy Input Fraction at | 0.7 | 6.667 | 32.222 | 111.67
0: 0.8735; 0.1: 0.721 | !Capacity and Design Energy Input Fraction at | 0.7 | 6.667 | 32.222 | 113.89
0: 0.8959; 0.1: 0.721 | !Capacity and Design Energy Input Fraction at | 0.7 | 6.667 | 32.222 | 115
0: 0.9163; 0.1: 0.721 | !Capacity and Design Energy Input Fraction at | 0.7 | 6.667 | 32.222 | 116.11
0: 1.0531; 0.1: 0.679 | !Capacity and Design Energy Input Fraction at | 0.7 | 7.222 | 26.667 | 108.89
0: 1.1041; 0.1: 0.679 | !Capacity and Design Energy Input Fraction at | 0.7 | 7.222 | 26.667 | 111.67
0: 1.151; 0.1: 0.679 | !Capacity and Design Energy Input Fraction at | 0.7 | 7.222 | 26.667 | 113.89
0: 1.1735; 0.1: 0.679 | !Capacity and Design Energy Input Fraction at | 0.7 | 7.222 | 26.667 | 115
0: 1.1959; 0.1: 0.679 | !Capacity and Design Energy Input Fraction at | 0.7 | 7.222 | 26.667 | 116.11
0: 0.9245; 0.1: 0.693 | !Capacity and Design Energy Input Fraction at | 0.7 | 7.222 | 29.444 | 108.89
0: 0.9755; 0.1: 0.693 | !Capacity and Design Energy Input Fraction at | 0.7 | 7.222 | 29.444 | 111.67
0: 1.0224; 0.1: 0.693 | !Capacity and Design Energy Input Fraction at | 0.7 | 7.222 | 29.444 | 113.89
0: 1.0449; 0.1: 0.693 | !Capacity and Design Energy Input Fraction at | 0.7 | 7.222 | 29.444 | 115
0: 1.0673; 0.1: 0.693 | !Capacity and Design Energy Input Fraction at | 0.7 | 7.222 | 29.444 | 116.11
0: 0.798; 0.1: 0.714 | !Capacity and Design Energy Input Fraction at | 0.7 | 7.222 | 32.222 | 108.89
0: 0.8469; 0.1: 0.714 | !Capacity and Design Energy Input Fraction at | 0.7 | 7.222 | 32.222 | 111.67
0: 0.8939; 0.1: 0.714 | !Capacity and Design Energy Input Fraction at | 0.7 | 7.222 | 32.222 | 113.89
0: 0.9163; 0.1: 0.714 | !Capacity and Design Energy Input Fraction at | 0.7 | 7.222 | 32.222 | 115
0: 0.9388; 0.1: 0.714 | !Capacity and Design Energy Input Fraction at | 0.7 | 7.222 | 32.222 | 116.11
0: 1.0755; 0.1: 0.672 | !Capacity and Design Energy Input Fraction at | 0.7 | 7.778 | 26.667 | 108.89
0: 1.1265; 0.1: 0.672 | !Capacity and Design Energy Input Fraction at | 0.7 | 7.778 | 26.667 | 111.67
0: 1.1755; 0.1: 0.672 | !Capacity and Design Energy Input Fraction at | 0.7 | 7.778 | 26.667 | 113.89
0: 1.198; 0.1: 0.672 | !Capacity and Design Energy Input Fraction at | 0.7 | 7.778 | 26.667 | 115
0: 1.2184; 0.1: 0.672 | !Capacity and Design Energy Input Fraction at | 0.7 | 7.778 | 26.667 | 116.11
0: 0.9469; 0.1: 0.686 | !Capacity and Design Energy Input Fraction at | 0.7 | 7.778 | 29.444 | 108.89
0: 0.998; 0.1: 0.686 | !Capacity and Design Energy Input Fraction at | 0.7 | 7.778 | 29.444 | 111.67
0: 1.0449; 0.1: 0.686 | !Capacity and Design Energy Input Fraction at | 0.7 | 7.778 | 29.444 | 113.89
0: 1.0673; 0.1: 0.686 | !Capacity and Design Energy Input Fraction at | 0.7 | 7.778 | 29.444 | 115
0: 1.0898; 0.1: 0.686 | !Capacity and Design Energy Input Fraction at | 0.7 | 7.778 | 29.444 | 116.11
0: 0.8184; 0.1: 0.707 | !Capacity and Design Energy Input Fraction at | 0.7 | 7.778 | 32.222 | 108.89
0: 0.8694; 0.1: 0.707 | !Capacity and Design Energy Input Fraction at | 0.7 | 7.778 | 32.222 | 111.67
0: 0.9163; 0.1: 0.707 | !Capacity and Design Energy Input Fraction at | 0.7 | 7.778 | 32.222 | 113.89
0: 0.9388; 0.1: 0.707 | !Capacity and Design Energy Input Fraction at | 0.7 | 7.778 | 32.222 | 115
0: 0.9592; 0.1: 0.707 | !Capacity and Design Energy Input Fraction at | 0.7 | 7.778 | 32.222 | 116.11
0: 1.1204; 0.1: 0.665 | !Capacity and Design Energy Input Fraction at | 0.7 | 8.889 | 26.667 | 108.89
0: 1.1735; 0.1: 0.665 | !Capacity and Design Energy Input Fraction at | 0.7 | 8.889 | 26.667 | 111.67
0: 1.2204; 0.1: 0.665 | !Capacity and Design Energy Input Fraction at | 0.7 | 8.889 | 26.667 | 113.89
0: 1.2449; 0.1: 0.665 | !Capacity and Design Energy Input Fraction at | 0.7 | 8.889 | 26.667 | 115
0: 1.2673; 0.1: 0.665 | !Capacity and Design Energy Input Fraction at | 0.7 | 8.889 | 26.667 | 116.11
0: 0.9898; 0.1: 0.679 | !Capacity and Design Energy Input Fraction at | 0.7 | 8.889 | 29.444 | 108.89
0: 1.0408; 0.1: 0.679 | !Capacity and Design Energy Input Fraction at | 0.7 | 8.889 | 29.444 | 111.67
0: 1.0898; 0.1: 0.679 | !Capacity and Design Energy Input Fraction at | 0.7 | 8.889 | 29.444 | 113.89
0: 1.1122; 0.1: 0.679 | !Capacity and Design Energy Input Fraction at | 0.7 | 8.889 | 29.444 | 115
0: 1.1347; 0.1: 0.679 | !Capacity and Design Energy Input Fraction at | 0.7 | 8.889 | 29.444 | 116.11
0: 0.8592; 0.1: 0.7 | !Capacity and Design Energy Input Fraction at | 0.7 | 8.889 | 32.222 | 108.89
0: 0.9102; 0.1: 0.7 | !Capacity and Design Energy Input Fraction at | 0.7 | 8.889 | 32.222 | 111.67
0: 0.9592; 0.1: 0.7 | !Capacity and Design Energy Input Fraction at | 0.7 | 8.889 | 32.222 | 113.89
0: 0.9816; 0.1: 0.7 | !Capacity and Design Energy Input Fraction at | 0.7 | 8.889 | 32.222 | 115
0: 1.0041; 0.1: 0.7 | !Capacity and Design Energy Input Fraction at | 0.7 | 8.889 | 32.222 | 116.11
0: 1.1673; 0.1: 0.658 | !Capacity and Design Energy Input Fraction at | 0.7 | 10 | 26.667 | 108.89
0: 1.2204; 0.1: 0.658 | !Capacity and Design Energy Input Fraction at | 0.7 | 10 | 26.667 | 111.67
0: 1.2694; 0.1: 0.658 | !Capacity and Design Energy Input Fraction at | 0.7 | 10 | 26.667 | 113.89
0: 1.2898; 0.1: 0.658 | !Capacity and Design Energy Input Fraction at | 0.7 | 10 | 26.667 | 115
0: 1.2898; 0.1: 0.658 | !Capacity and Design Energy Input Fraction at | 0.7 | 10 | 26.667 | 116.11
0: 1.0347; 0.1: 0.672 | !Capacity and Design Energy Input Fraction at | 0.7 | 10 | 29.444 | 108.89
0: 1.0857; 0.1: 0.672 | !Capacity and Design Energy Input Fraction at | 0.7 | 10 | 29.444 | 111.67
0: 1.1347; 0.1: 0.672 | !Capacity and Design Energy Input Fraction at | 0.7 | 10 | 29.444 | 113.89
0: 1.1592; 0.1: 0.672 | !Capacity and Design Energy Input Fraction at | 0.7 | 10 | 29.444 | 115
0: 1.1796; 0.1: 0.672 | !Capacity and Design Energy Input Fraction at | 0.7 | 10 | 29.444 | 116.11
0: 0.902; 0.1: 0.686 | !Capacity and Design Energy Input Fraction at | 0.7 | 10 | 32.222 | 108.89
0: 0.9531; 0.1: 0.686 | !Capacity and Design Energy Input Fraction at | 0.7 | 10 | 32.222 | 111.67
0: 1.002; 0.1: 0.686 | !Capacity and Design Energy Input Fraction at | 0.7 | 10 | 32.222 | 113.89
0: 1.0245; 0.1: 0.686 | !Capacity and Design Energy Input Fraction at | 0.7 | 10 | 32.222 | 115
0: 1.0469; 0.1: 0.686 | !Capacity and Design Energy Input Fraction at | 0.7 | 10 | 32.222 | 116.11
0: 0.9878; 0.1: 0.792 | !Capacity and Design Energy Input Fraction at | 0.8 | 5.556 | 26.667 | 108.89
0: 1.0367; 0.1: 0.792 | !Capacity and Design Energy Input Fraction at | 0.8 | 5.556 | 26.667 | 111.67
0: 1.0837; 0.1: 0.792 | !Capacity and Design Energy Input Fraction at | 0.8 | 5.556 | 26.667 | 113.89
0: 1.1041; 0.1: 0.792 | !Capacity and Design Energy Input Fraction at | 0.8 | 5.556 | 26.667 | 115
0: 1.1265; 0.1: 0.792 | !Capacity and Design Energy Input Fraction at | 0.8 | 5.556 | 26.667 | 116.11
0: 0.8612; 0.1: 0.816 | !Capacity and Design Energy Input Fraction at | 0.8 | 5.556 | 29.444 | 108.89
0: 0.9102; 0.1: 0.816 | !Capacity and Design Energy Input Fraction at | 0.8 | 5.556 | 29.444 | 111.67
0: 0.9571; 0.1: 0.816 | !Capacity and Design Energy Input Fraction at | 0.8 | 5.556 | 29.444 | 113.89
0: 0.9796; 0.1: 0.816 | !Capacity and Design Energy Input Fraction at | 0.8 | 5.556 | 29.444 | 115
0: 1; 0.1: 0.816 | !Capacity and Design Energy Input Fraction at | 0.8 | 5.556 | 29.444 | 116.11
0: 0.7347; 0.1: 0.832 | !Capacity and Design Energy Input Fraction at | 0.8 | 5.556 | 32.222 | 108.89
0: 0.7857; 0.1: 0.832 | !Capacity and Design Energy Input Fraction at | 0.8 | 5.556 | 32.222 | 111.67
0: 0.8327; 0.1: 0.832 | !Capacity and Design Energy Input Fraction at | 0.8 | 5.556 | 32.222 | 113.89
0: 0.8531; 0.1: 0.832 | !Capacity and Design Energy Input Fraction at | 0.8 | 5.556 | 32.222 | 115
0: 0.8735; 0.1: 0.832 | !Capacity and Design Energy Input Fraction at | 0.8 | 5.556 | 32.222 | 116.11
0: 1.0102; 0.1: 0.784 | !Capacity and Design Energy Input Fraction at | 0.8 | 6.111 | 26.667 | 108.89
0: 1.0592; 0.1: 0.784 | !Capacity and Design Energy Input Fraction at | 0.8 | 6.111 | 26.667 | 111.67
0: 1.1061; 0.1: 0.784 | !Capacity and Design Energy Input Fraction at | 0.8 | 6.111 | 26.667 | 113.89
0: 1.1286; 0.1: 0.784 | !Capacity and Design Energy Input Fraction at | 0.8 | 6.111 | 26.667 | 115
0: 1.149; 0.1: 0.784 | !Capacity and Design Energy Input Fraction at | 0.8 | 6.111 | 26.667 | 116.11
0: 0.8837; 0.1: 0.808 | !Capacity and Design Energy Input Fraction at | 0.8 | 6.111 | 29.444 | 108.89
0: 0.9327; 0.1: 0.808 | !Capacity and Design Energy Input Fraction at | 0.8 | 6.111 | 29.444 | 111.67
0: 0.9776; 0.1: 0.808 | !Capacity and Design Energy Input Fraction at | 0.8 | 6.111 | 29.444 | 113.89
0: 1; 0.1: 0.808 | !Capacity and Design Energy Input Fraction at | 0.8 | 6.111 | 29.444 | 115
0: 1.0224; 0.1: 0.808 | !Capacity and Design Energy Input Fraction at | 0.8 | 6.111 | 29.444 | 116.11
0: 0.7571; 0.1: 0.832 | !Capacity and Design Energy Input Fraction at | 0.8 | 6.111 | 32.222 | 108.89
0: 0.8061; 0.1: 0.832 | !Capacity and Design Energy Input Fraction at | 0.8 | 6.111 | 32.222 | 111.67
0: 0.8531; 0.1: 0.832 | !Capacity and Design Energy Input Fraction at | 0.8 | 6.111 | 32.222 | 113.89
0: 0.8735; 0.1: 0.832 | !Capacity and Design Energy Input Fraction at | 0.8 | 6.111 | 32.222 | 115
0: 0.8959; 0.1: 0.832 | !Capacity and Design Energy Input Fraction at | 0.8 | 6.111 | 32.222 | 116.11
0: 1.0306; 0.1: 0.784 | !Capacity and Design Energy Input Fraction at | 0.8 | 6.667 | 26.667 | 108.89
0: 1.0816; 0.1: 0.784 | !Capacity and Design Energy Input Fraction at | 0.8 | 6.667 | 26.667 | 111.67
0: 1.1286; 0.1: 0.784 | !Capacity and Design Energy Input Fraction at | 0.8 | 6.667 | 26.667 | 113.89
0: 1.151; 0.1: 0.784 | !Capacity and Design Energy Input Fraction at | 0.8 | 6.667 | 26.667 | 115
0: 1.1714; 0.1: 0.784 | !Capacity and Design Energy Input Fraction at | 0.8 | 6.667 | 26.667 | 116.11
0: 0.9041; 0.1: 0.8 | !Capacity and Design Energy Input Fraction at | 0.8 | 6.667 | 29.444 | 108.89
0: 0.9531; 0.1: 0.8 | !Capacity and Design Energy Input Fraction at | 0.8 | 6.667 | 29.444 | 111.67
0: 1; 0.1: 0.8 | !Capacity and Design Energy Input Fraction at | 0.8 | 6.667 | 29.444 | 113.89
0: 1.0224; 0.1: 0.8 | !Capacity and Design Energy Input Fraction at | 0.8 | 6.667 | 29.444 | 115
0: 1.0449; 0.1: 0.8 | !Capacity and Design Energy Input Fraction at | 0.8 | 6.667 | 29.444 | 116.11
0: 0.7776; 0.1: 0.824 | !Capacity and Design Energy Input Fraction at | 0.8 | 6.667 | 32.222 | 108.89
0: 0.8265; 0.1: 0.824 | !Capacity and Design Energy Input Fraction at | 0.8 | 6.667 | 32.222 | 111.67
0: 0.8735; 0.1: 0.824 | !Capacity and Design Energy Input Fraction at | 0.8 | 6.667 | 32.222 | 113.89
0: 0.8959; 0.1: 0.824 | !Capacity and Design Energy Input Fraction at | 0.8 | 6.667 | 32.222 | 115
0: 0.9163; 0.1: 0.824 | !Capacity and Design Energy Input Fraction at | 0.8 | 6.667 | 32.222 | 116.11
0: 1.0531; 0.1: 0.776 | !Capacity and Design Energy Input Fraction at | 0.8 | 7.222 | 26.667 | 108.89
0: 1.1041; 0.1: 0.776 | !Capacity and Design Energy Input Fraction at | 0.8 | 7.222 | 26.667 | 111.67
0: 1.151; 0.1: 0.776 | !Capacity and Design Energy Input Fraction at | 0.8 | 7.222 | 26.667 | 113.89
0: 1.1735; 0.1: 0.776 | !Capacity and Design Energy Input Fraction at | 0.8 | 7.222 | 26.667 | 115
0: 1.1959; 0.1: 0.776 | !Capacity and Design Energy Input Fraction at | 0.8 | 7.222 | 26.667 | 116.11
0: 0.9245; 0.1: 0.792 | !Capacity and Design Energy Input Fraction at | 0.8 | 7.222 | 29.444 | 108.89
0: 0.9755; 0.1: 0.792 | !Capacity and Design Energy Input Fraction at | 0.8 | 7.222 | 29.444 | 111.67
0: 1.0224; 0.1: 0.792 | !Capacity and Design Energy Input Fraction at | 0.8 | 7.222 | 29.444 | 113.89
0: 1.0449; 0.1: 0.792 | !Capacity and Design Energy Input Fraction at | 0.8 | 7.222 | 29.444 | 115
0: 1.0673; 0.1: 0.792 | !Capacity and Design Energy Input Fraction at | 0.8 | 7.222 | 29.444 | 116.11
0: 0.798; 0.1: 0.816 | !Capacity and Design Energy Input Fraction at | 0.8 | 7.222 | 32.222 | 108.89
0: 0.8469; 0.1: 0.816 | !Capacity and Design Energy Input Fraction at | 0.8 | 7.222 | 32.222 | 111.67
0: 0.8939; 0.1: 0.816 | !Capacity and Design Energy Input Fraction at | 0.8 | 7.222 | 32.222 | 113.89
0: 0.9163; 0.1: 0.816 | !Capacity and Design Energy Input Fraction at | 0.8 | 7.222 | 32.222 | 115
0: 0.9388; 0.1: 0.816 | !Capacity and Design Energy Input Fraction at | 0.8 | 7.222 | 32.222 | 116.11
0: 1.0755; 0.1: 0.768 | !Capacity and Design Energy Input Fraction at | 0.8 | 7.778 | 26.667 | 108.89
0: 1.1265; 0.1: 0.768 | !Capacity and Design Energy Input Fraction at | 0.8 | 7.778 | 26.667 | 111.67
0: 1.1755; 0.1: 0.768 | !Capacity and Design Energy Input Fraction at | 0.8 | 7.778 | 26.667 | 113.89
0: 1.198; 0.1: 0.768 | !Capacity and Design Energy Input Fraction at | 0.8 | 7.778 | 26.667 | 115
0: 1.2184; 0.1: 0.768 | !Capacity and Design Energy Input Fraction at | 0.8 | 7.778 | 26.667 | 116.11
0: 0.9469; 0.1: 0.784 | !Capacity and Design Energy Input Fraction at | 0.8 | 7.778 | 29.444 | 108.89
0: 0.998; 0.1: 0.784 | !Capacity and Design Energy Input Fraction at | 0.8 | 7.778 | 29.444 | 111.67
0: 1.0449; 0.1: 0.784 | !Capacity and Design Energy Input Fraction at | 0.8 | 7.778 | 29.444 | 113.89
0: 1.0673; 0.1: 0.784 | !Capacity and Design Energy Input Fraction at | 0.8 | 7.778 | 29.444 | 115
0: 1.0898; 0.1: 0.784 | !Capacity and Design Energy Input Fraction at | 0.8 | 7.778 | 29.444 | 116.11
0: 0.8184; 0.1: 0.808 | !Capacity and Design Energy Input Fraction at | 0.8 | 7.778 | 32.222 | 108.89
0: 0.8694; 0.1: 0.808 | !Capacity and Design Energy Input Fraction at | 0.8 | 7.778 | 32.222 | 111.67
0: 0.9163; 0.1: 0.808 | !Capacity and Design Energy Input Fraction at | 0.8 | 7.778 | 32.222 | 113.89
0: 0.9388; 0.1: 0.808 | !Capacity and Design Energy Input Fraction at | 0.8 | 7.778 | 32.222 | 115
0: 0.9592; 0.1: 0.808 | !Capacity and Design Energy Input Fraction at | 0.8 | 7.778 | 32.222 | 116.11
0: 1.1204; 0.1: 0.76 | !Capacity and Design Energy Input Fraction at | 0.8 | 8.889 | 26.667 | 108.89
0: 1.1735; 0.1: 0.76 | !Capacity and Design Energy Input Fraction at | 0.8 | 8.889 | 26.667 | 111.67
0: 1.2204; 0.1: 0.76 | !Capacity and Design Energy Input Fraction at | 0.8 | 8.889 | 26.667 | 113.89
0: 1.2449; 0.1: 0.76 | !Capacity and Design Energy Input Fraction at | 0.8 | 8.889 | 26.667 | 115
0: 1.2673; 0.1: 0.76 | !Capacity and Design Energy Input Fraction at | 0.8 | 8.889 | 26.667 | 116.11
0: 0.9898; 0.1: 0.776 | !Capacity and Design Energy Input Fraction at | 0.8 | 8.889 | 29.444 | 108.89
0: 1.0408; 0.1: 0.776 | !Capacity and Design Energy Input Fraction at | 0.8 | 8.889 | 29.444 | 111.67
0: 1.0898; 0.1: 0.776 | !Capacity and Design Energy Input Fraction at | 0.8 | 8.889 | 29.444 | 113.89
0: 1.1122; 0.1: 0.776 | !Capacity and Design Energy Input Fraction at | 0.8 | 8.889 | 29.444 | 115
0: 1.1347; 0.1: 0.776 | !Capacity and Design Energy Input Fraction at | 0.8 | 8.889 | 29.444 | 116.11
0: 0.8592; 0.1: 0.8 | !Capacity and Design Energy Input Fraction at | 0.8 | 8.889 | 32.222 | 108.89
0: 0.9102; 0.1: 0.8 | !Capacity and Design Energy Input Fraction at | 0.8 | 8.889 | 32.222 | 111.67
0: 0.9592; 0.1: 0.8 | !Capacity and Design Energy Input Fraction at | 0.8 | 8.889 | 32.222 | 113.89
0: 0.9816; 0.1: 0.8 | !Capacity and Design Energy Input Fraction at | 0.8 | 8.889 | 32.222 | 115
0: 1.0041; 0.1: 0.8 | !Capacity and Design Energy Input Fraction at | 0.8 | 8.889 | 32.222 | 116.11
0: 1.1673; 0.1: 0.752 | !Capacity and Design Energy Input Fraction at | 0.8 | 10 | 26.667 | 108.89
0: 1.2204; 0.1: 0.752 | !Capacity and Design Energy Input Fraction at | 0.8 | 10 | 26.667 | 111.67
0: 1.2694; 0.1: 0.752 | !Capacity and Design Energy Input Fraction at | 0.8 | 10 | 26.667 | 113.89
0: 1.2898; 0.1: 0.752 | !Capacity and Design Energy Input Fraction at | 0.8 | 10 | 26.667 | 115
0: 1.2898; 0.1: 0.752 | !Capacity and Design Energy Input Fraction at | 0.8 | 10 | 26.667 | 116.11
0: 1.0347; 0.1: 0.768 | !Capacity and Design Energy Input Fraction at | 0.8 | 10 | 29.444 | 108.89
0: 1.0857; 0.1: 0.768 | !Capacity and Design Energy Input Fraction at | 0.8 | 10 | 29.444 | 111.67
0: 1.1347; 0.1: 0.768 | !Capacity and Design Energy Input Fraction at | 0.8 | 10 | 29.444 | 113.89
0: 1.1592; 0.1: 0.768 | !Capacity and Design Energy Input Fraction at | 0.8 | 10 | 29.444 | 115
0: 1.1796; 0.1: 0.768 | !Capacity and Design Energy Input Fraction at | 0.8 | 10 | 29.444 | 116.11
0: 0.902; 0.1: 0.784 | !Capacity and Design Energy Input Fraction at | 0.8 | 10 | 32.222 | 108.89
0: 0.9531; 0.1: 0.784 | !Capacity and Design Energy Input Fraction at | 0.8 | 10 | 32.222 | 111.67
0: 1.002; 0.1: 0.784 | !Capacity and Design Energy Input Fraction at | 0.8 | 10 | 32.222 | 113.89
0: 1.0245; 0.1: 0.784 | !Capacity and Design Energy Input Fraction at | 0.8 | 10 | 32.222 | 115
0: 1.0469; 0.1: 0.784 | !Capacity and Design Energy Input Fraction at | 0.8 | 10 | 32.222 | 116.11
0: 0.9878; 0.1: 0.891 | !Capacity and Design Energy Input Fraction at | 0.9 | 5.556 | 26.667 | 108.89
0: 1.0367; 0.1: 0.891 | !Capacity and Design Energy Input Fraction at | 0.9 | 5.556 | 26.667 | 111.67
0: 1.0837; 0.1: 0.891 | !Capacity and Design Energy Input Fraction at | 0.9 | 5.556 | 26.667 | 113.89
0: 1.1041; 0.1: 0.891 | !Capacity and Design Energy Input Fraction at | 0.9 | 5.556 | 26.667 | 115
0: 1.1265; 0.1: 0.891 | !Capacity and Design Energy Input Fraction at | 0.9 | 5.556 | 26.667 | 116.11
0: 0.8612; 0.1: 0.918 | !Capacity and Design Energy Input Fraction at | 0.9 | 5.556 | 29.444 | 108.89
0: 0.9102; 0.1: 0.918 | !Capacity and Design Energy Input Fraction at | 0.9 | 5.556 | 29.444 | 111.67
0: 0.9571; 0.1: 0.918 | !Capacity and Design Energy Input Fraction at | 0.9 | 5.556 | 29.444 | 113.89
0: 0.9796; 0.1: 0.918 | !Capacity and Design Energy Input Fraction at | 0.9 | 5.556 | 29.444 | 115
0: 1; 0.1: 0.918 | !Capacity and Design Energy Input Fraction at | 0.9 | 5.556 | 29.444 | 116.11
0: 0.7347; 0.1: 0.936 | !Capacity and Design Energy Input Fraction at | 0.9 | 5.556 | 32.222 | 108.89
0: 0.7857; 0.1: 0.936 | !Capacity and Design Energy Input Fraction at | 0.9 | 5.556 | 32.222 | 111.67
0: 0.8327; 0.1: 0.936 | !Capacity and Design Energy Input Fraction at | 0.9 | 5.556 | 32.222 | 113.89
0: 0.8531; 0.1: 0.936 | !Capacity and Design Energy Input Fraction at | 0.9 | 5.556 | 32.222 | 115
0: 0.8735; 0.1: 0.936 | !Capacity and Design Energy Input Fraction at | 0.9 | 5.556 | 32.222 | 116.11
0: 1.0102; 0.1: 0.882 | !Capacity and Design Energy Input Fraction at | 0.9 | 6.111 | 26.667 | 108.89
0: 1.0592; 0.1: 0.882 | !Capacity and Design Energy Input Fraction at | 0.9 | 6.111 | 26.667 | 111.67
0: 1.1061; 0.1: 0.882 | !Capacity and Design Energy Input Fraction at | 0.9 | 6.111 | 26.667 | 113.89
0: 1.1286; 0.1: 0.882 | !Capacity and Design Energy Input Fraction at | 0.9 | 6.111 | 26.667 | 115
0: 1.149; 0.1: 0.882 | !Capacity and Design Energy Input Fraction at | 0.9 | 6.111 | 26.667 | 116.11
0: 0.8837; 0.1: 0.909 | !Capacity and Design Energy Input Fraction at | 0.9 | 6.111 | 29.444 | 108.89
0: 0.9327; 0.1: 0.909 | !Capacity and Design Energy Input Fraction at | 0.9 | 6.111 | 29.444 | 111.67
0: 0.9776; 0.1: 0.909 | !Capacity and Design Energy Input Fraction at | 0.9 | 6.111 | 29.444 | 113.89
0: 1; 0.1: 0.909 | !Capacity and Design Energy Input Fraction at | 0.9 | 6.111 | 29.444 | 115
0: 1.0224; 0.1: 0.909 | !Capacity and Design Energy Input Fraction at | 0.9 | 6.111 | 29.444 | 116.11
0: 0.7571; 0.1: 0.936 | !Capacity and Design Energy Input Fraction at | 0.9 | 6.111 | 32.222 | 108.89
0: 0.8061; 0.1: 0.936 | !Capacity and Design Energy Input Fraction at | 0.9 | 6.111 | 32.222 | 111.67
0: 0.8531; 0.1: 0.936 | !Capacity and Design Energy Input Fraction at | 0.9 | 6.111 | 32.222 | 113.89
0: 0.8735; 0.1: 0.936 | !Capacity and Design Energy Input Fraction at | 0.9 | 6.111 | 32.222 | 115
0: 0.8959; 0.1: 0.936 | !Capacity and Design Energy Input Fraction at | 0.9 | 6.111 | 32.222 | 116.11
0: 1.0306; 0.1: 0.882 | !Capacity and Design Energy Input Fraction at | 0.9 | 6.667 | 26.667 | 108.89
0: 1.0816; 0.1: 0.882 | !Capacity and Design Energy Input Fraction at | 0.9 | 6.667 | 26.667 | 111.67
0: 1.1286; 0.1: 0.882 | !Capacity and Design Energy Input Fraction at | 0.9 | 6.667 | 26.667 | 113.89
0: 1.151; 0.1: 0.882 | !Capacity and Design Energy Input Fraction at | 0.9 | 6.667 | 26.667 | 115
0: 1.1714; 0.1: 0.882 | !Capacity and Design Energy Input Fraction at | 0.9 | 6.667 | 26.667 | 116.11
0: 0.9041; 0.1: 0.9 | !Capacity and Design Energy Input Fraction at | 0.9 | 6.667 | 29.444 | 108.89
0: 0.9531; 0.1: 0.9 | !Capacity and Design Energy Input Fraction at | 0.9 | 6.667 | 29.444 | 111.67
0: 1; 0.1: 0.9 | !Capacity and Design Energy Input Fraction at | 0.9 | 6.667 | 29.444 | 113.89
0: 1.0224; 0.1: 0.9 | !Capacity and Design Energy Input Fraction at | 0.9 | 6.667 | 29.444 | 115
0: 1.0449; 0.1: 0.9 | !Capacity and Design Energy Input Fraction at | 0.9 | 6.667 | 29.444 | 116.11
0: 0.7776; 0.1: 0.927 | !Capacity and Design Energy Input Fraction at | 0.9 | 6.667 | 32.222 | 108.89
0: 0.8265; 0.1: 0.927 | !Capacity and Design Energy Input Fraction at | 0.9 | 6.667 | 32.222 | 111.67
0: 0.8735; 0.1: 0.927 | !Capacity and Design Energy Input Fraction at | 0.9 | 6.667 | 32.222 | 113.89
0: 0.8959; 0.1: 0.927 | !Capacity and Design Energy Input Fraction at | 0.9 | 6.667 | 32.222 | 115
0: 0.9163; 0.1: 0.927 | !Capacity and Design Energy Input Fraction at | 0.9 | 6.667 | 32.222 | 116.11
0: 1.0531; 0.1: 0.873 | !Capacity and Design Energy Input Fraction at | 0.9 | 7.222 | 26.667 | 108.89
0: 1.1041; 0.1: 0.873 | !Capacity and Design Energy Input Fraction at | 0.9 | 7.222 | 26.667 | 111.67
0: 1.151; 0.1: 0.873 | !Capacity and Design Energy Input Fraction at | 0.9 | 7.222 | 26.667 | 113.89
0: 1.1735; 0.1: 0.873 | !Capacity and Design Energy Input Fraction at | 0.9 | 7.222 | 26.667 | 115
0: 1.1959; 0.1: 0.873 | !Capacity and Design Energy Input Fraction at | 0.9 | 7.222 | 26.667 | 116.11
0: 0.9245; 0.1: 0.891 | !Capacity and Design Energy Input Fraction at | 0.9 | 7.222 | 29.444 | 108.89
0: 0.9755; 0.1: 0.891 | !Capacity and Design Energy Input Fraction at | 0.9 | 7.222 | 29.444 | 111.67
0: 1.0224; 0.1: 0.891 | !Capacity and Design Energy Input Fraction at | 0.9 | 7.222 | 29.444 | 113.89
0: 1.0449; 0.1: 0.891 | !Capacity and Design Energy Input Fraction at | 0.9 | 7.222 | 29.444 | 115
0: 1.0673; 0.1: 0.891 | !Capacity and Design Energy Input Fraction at | 0.9 | 7.222 | 29.444 | 116.11
0: 0.798; 0.1: 0.918 | !Capacity and Design Energy Input Fraction at | 0.9 | 7.222 | 32.222 | 108.89
0: 0.8469; 0.1: 0.918 | !Capacity and Design Energy Input Fraction at | 0.9 | 7.222 | 32.222 | 111.67
0: 0.8939; 0.1: 0.918 | !Capacity and Design Energy Input Fraction at | 0.9 | 7.222 | 32.222 | 113.89
0: 0.9163; 0.1: 0.918 | !Capacity and Design Energy Input Fraction at | 0.9 | 7.222 | 32.222 | 115
0: 0.9388; 0.1: 0.918 | !Capacity and Design Energy Input Fraction at | 0.9 | 7.222 | 32.222 | 116.11
0: 1.0755; 0.1: 0.864 | !Capacity and Design Energy Input Fraction at | 0.9 | 7.778 | 26.667 | 108.89
0: 1.1265; 0.1: 0.864 | !Capacity and Design Energy Input Fraction at | 0.9 | 7.778 | 26.667 | 111.67
0: 1.1755; 0.1: 0.864 | !Capacity and Design Energy Input Fraction at | 0.9 | 7.778 | 26.667 | 113.89
0: 1.198; 0.1: 0.864 | !Capacity and Design Energy Input Fraction at | 0.9 | 7.778 | 26.667 | 115
0: 1.2184; 0.1: 0.864 | !Capacity and Design Energy Input Fraction at | 0.9 | 7.778 | 26.667 | 116.11
0: 0.9469; 0.1: 0.882 | !Capacity and Design Energy Input Fraction at | 0.9 | 7.778 | 29.444 | 108.89
0: 0.998; 0.1: 0.882 | !Capacity and Design Energy Input Fraction at | 0.9 | 7.778 | 29.444 | 111.67
0: 1.0449; 0.1: 0.882 | !Capacity and Design Energy Input Fraction at | 0.9 | 7.778 | 29.444 | 113.89
0: 1.0673; 0.1: 0.882 | !Capacity and Design Energy Input Fraction at | 0.9 | 7.778 | 29.444 | 115
0: 1.0898; 0.1: 0.882 | !Capacity and Design Energy Input Fraction at | 0.9 | 7.778 | 29.444 | 116.11
0: 0.8184; 0.1: 0.909 | !Capacity and Design Energy Input Fraction at | 0.9 | 7.778 | 32.222 | 108.89
0: 0.8694; 0.1: 0.909 | !Capacity and Design Energy Input Fraction at | 0.9 | 7.778 | 32.222 | 111.67
0: 0.9163; 0.1: 0.909 | !Capacity and Design Energy Input Fraction at | 0.9 | 7.778 | 32.222 | 113.89
0: 0.9388; 0.1: 0.909 | !Capacity and Design Energy Input Fraction at | 0.9 | 7.778 | 32.222 | 115
0: 0.9592; 0.1: 0.909 | !Capacity and Design Energy Input Fraction at | 0.9 | 7.778 | 32.222 | 116.11
0: 1.1204; 0.1: 0.855 | !Capacity and Design Energy Input Fraction at | 0.9 | 8.889 | 26.667 | 108.89
0: 1.1735; 0.1: 0.855 | !Capacity and Design Energy Input Fraction at | 0.9 | 8.889 | 26.667 | 111.67
0: 1.2204; 0.1: 0.855 | !Capacity and Design Energy Input Fraction at | 0.9 | 8.889 | 26.667 | 113.89
0: 1.2449; 0.1: 0.855 | !Capacity and Design Energy Input Fraction at | 0.9 | 8.889 | 26.667 | 115
0: 1.2673; 0.1: 0.855 | !Capacity and Design Energy Input Fraction at | 0.9 | 8.889 | 26.667 | 116.11
0: 0.9898; 0.1: 0.873 | !Capacity and Design Energy Input Fraction at | 0.9 | 8.889 | 29.444 | 108.89
0: 1.0408; 0.1: 0.873 | !Capacity and Design Energy Input Fraction at | 0.9 | 8.889 | 29.444 | 111.67
0: 1.0898; 0.1: 0.873 | !Capacity and Design Energy Input Fraction at | 0.9 | 8.889 | 29.444 | 113.89
0: 1.1122; 0.1: 0.873 | !Capacity and Design Energy Input Fraction at | 0.9 | 8.889 | 29.444 | 115
0: 1.1347; 0.1: 0.873 | !Capacity and Design Energy Input Fraction at | 0.9 | 8.889 | 29.444 | 116.11
0: 0.8592; 0.1: 0.9 | !Capacity and Design Energy Input Fraction at | 0.9 | 8.889 | 32.222 | 108.89
0: 0.9102; 0.1: 0.9 | !Capacity and Design Energy Input Fraction at | 0.9 | 8.889 | 32.222 | 111.67
0: 0.9592; 0.1: 0.9 | !Capacity and Design Energy Input Fraction at | 0.9 | 8.889 | 32.222 | 113.89
0: 0.9816; 0.1: 0.9 | !Capacity and Design Energy Input Fraction at | 0.9 | 8.889 | 32.222 | 115
0: 1.0041; 0.1: 0.9 | !Capacity and Design Energy Input Fraction at | 0.9 | 8.889 | 32.222 | 116.11
0: 1.1673; 0.1: 0.846 | !Capacity and Design Energy Input Fraction at | 0.9 | 10 | 26.667 | 108.89
0: 1.2204; 0.1: 0.846 | !Capacity and Design Energy Input Fraction at | 0.9 | 10 | 26.667 | 111.67
0: 1.2694; 0.1: 0.846 | !Capacity and Design Energy Input Fraction at | 0.9 | 10 | 26.667 | 113.89
0: 1.2898; 0.1: 0.846 | !Capacity and Design Energy Input Fraction at | 0.9 | 10 | 26.667 | 115
0: 1.2898; 0.1: 0.846 | !Capacity and Design Energy Input Fraction at | 0.9 | 10 | 26.667 | 116.11
0: 1.0347; 0.1: 0.864 | !Capacity and Design Energy Input Fraction at | 0.9 | 10 | 29.444 | 108.89
0: 1.0857; 0.1: 0.864 | !Capacity and Design Energy Input Fraction at | 0.9 | 10 | 29.444 | 111.67
0: 1.1347; 0.1: 0.864 | !Capacity and Design Energy Input Fraction at | 0.9 | 10 | 29.444 | 113.89
0: 1.1592; 0.1: 0.864 | !Capacity and Design Energy Input Fraction at | 0.9 | 10 | 29.444 | 115
0: 1.1796; 0.1: 0.864 | !Capacity and Design Energy Input Fraction at | 0.9 | 10 | 29.444 | 116.11
0: 0.902; 0.1: 0.882 | !Capacity and Design Energy Input Fraction at | 0.9 | 10 | 32.222 | 108.89
0: 0.9531; 0.1: 0.882 | !Capacity and Design Energy Input Fraction at | 0.9 | 10 | 32.222 | 111.67
0: 1.002; 0.1: 0.882 | !Capacity and Design Energy Input Fraction at | 0.9 | 10 | 32.222 | 113.89
0: 1.0245; 0.1: 0.882 | !Capacity and Design Energy Input Fraction at | 0.9 | 10 | 32.222 | 115
0: 1.0469; 0.1: 0.882 | !Capacity and Design Energy Input Fraction at | 0.9 | 10 | 32.222 | 116.11
0: 0.9878; 0.1: 0.99 | !Capacity and Design Energy Input Fraction at | 1 | 5.556 | 26.667 | 108.89
0: 1.0367; 0.1: 0.99 | !Capacity and Design Energy Input Fraction at | 1 | 5.556 | 26.667 | 111.67
0: 1.0837; 0.1: 0.99 | !Capacity and Design Energy Input Fraction at | 1 | 5.556 | 26.667 | 113.89
0: 1.1041; 0.1: 0.99 | !Capacity and Design Energy Input Fraction at | 1 | 5.556 | 26.667 | 115
0: 1.1265; 0.1: 0.99 | !Capacity and Design Energy Input Fraction at | 1 | 5.556 | 26.667 | 116.11
0: 0.8612; 0.1: 1.02 | !Capacity and Design Energy Input Fraction at | 1 | 5.556 | 29.444 | 108.89
0: 0.9102; 0.1: 1.02 | !Capacity and Design Energy Input Fraction at | 1 | 5.556 | 29.444 | 111.67
0: 0.9571; 0.1: 1.02 | !Capacity and Design Energy Input Fraction at | 1 | 5.556 | 29.444 | 113.89
0: 0.9796; 0.1: 1.02 | !Capacity and Design Energy Input Fraction at | 1 | 5.556 | 29.444 | 115
0: 1; 0.1: 1.02 | !Capacity and Design Energy Input Fraction at | 1 | 5.556 | 29.444 | 116.11
0: 0.7347; 0.1: 1.04 | !Capacity and Design Energy Input Fraction at | 1 | 5.556 | 32.222 | 108.89
0: 0.7857; 0.1: 1.04 | !Capacity and Design Energy Input Fraction at | 1 | 5.556 | 32.222 | 111.67
0: 0.8327; 0.1: 1.04 | !Capacity and Design Energy Input Fraction at | 1 | 5.556 | 32.222 | 113.89
0: 0.8531; 0.1: 1.04 | !Capacity and Design Energy Input Fraction at | 1 | 5.556 | 32.222 | 115
0: 0.8735; 0.1: 1.04 | !Capacity and Design Energy Input Fraction at | 1 | 5.556 | 32.222 | 116.11
0: 1.0102; 0.1: 0.98 | !Capacity and Design Energy Input Fraction at | 1 | 6.111 | 26.667 | 108.89
0: 1.0592; 0.1: 0.98 | !Capacity and Design Energy Input Fraction at | 1 | 6.111 | 26.667 | 111.67
0: 1.1061; 0.1: 0.98 | !Capacity and Design Energy Input Fraction at | 1 | 6.111 | 26.667 | 113.89
0: 1.1286; 0.1: 0.98 | !Capacity and Design Energy Input Fraction at | 1 | 6.111 | 26.667 | 115
0: 1.149; 0.1: 0.98 | !Capacity and Design Energy Input Fraction at | 1 | 6.111 | 26.667 | 116.11
0: 0.8837; 0.1: 1.01 | !Capacity and Design Energy Input Fraction at | 1 | 6.111 | 29.444 | 108.89
0: 0.9327; 0.1: 1.01 | !Capacity and Design Energy Input Fraction at | 1 | 6.111 | 29.444 | 111.67
0: 0.9776; 0.1: 1.01 | !Capacity and Design Energy Input Fraction at | 1 | 6.111 | 29.444 | 113.89
0: 1; 0.1: 1.01 | !Capacity and Design Energy Input Fraction at | 1 | 6.111 | 29.444 | 115
0: 1.0224; 0.1: 1.01 | !Capacity and Design Energy Input Fraction at | 1 | 6.111 | 29.444 | 116.11
0: 0.7571; 0.1: 1.04 | !Capacity and Design Energy Input Fraction at | 1 | 6.111 | 32.222 | 108.89
0: 0.8061; 0.1: 1.04 | !Capacity and Design Energy Input Fraction at | 1 | 6.111 | 32.222 | 111.67
0: 0.8531; 0.1: 1.04 | !Capacity and Design Energy Input Fraction at | 1 | 6.111 | 32.222 | 113.89
0: 0.8735; 0.1: 1.04 | !Capacity and Design Energy Input Fraction at | 1 | 6.111 | 32.222 | 115
0: 0.8959; 0.1: 1.04 | !Capacity and Design Energy Input Fraction at | 1 | 6.111 | 32.222 | 116.11
0: 1.0306; 0.1: 0.98 | !Capacity and Design Energy Input Fraction at | 1 | 6.667 | 26.667 | 108.89
0: 1.0816; 0.1: 0.98 | !Capacity and Design Energy Input Fraction at | 1 | 6.667 | 26.667 | 111.67
0: 1.1286; 0.1: 0.98 | !Capacity and Design Energy Input Fraction at | 1 | 6.667 | 26.667 | 113.89
0: 1.151; 0.1: 0.98 | !Capacity and Design Energy Input Fraction at | 1 | 6.667 | 26.667 | 115
0: 1.1714; 0.1: 0.98 | !Capacity and Design Energy Input Fraction at | 1 | 6.667 | 26.667 | 116.11
0: 0.9041; 0.1: 1 | !Capacity and Design Energy Input Fraction at | 1 | 6.667 | 29.444 | 108.89
0: 0.9531; 0.1: 1 | !Capacity and Design Energy Input Fraction at | 1 | 6.667 | 29.444 | 111.67
[11 empty] | !Capacity and Design Energy Input Fraction at | 1 | 6.667 | 29.444 | 113.89 | bar: 0 to 0.1
0: 1.0224; 0.1: 1 | !Capacity and Design Energy Input Fraction at | 1 | 6.667 | 29.444 | 115
0: 1.0449; 0.1: 1 | !Capacity and Design Energy Input Fraction at | 1 | 6.667 | 29.444 | 116.11
0: 0.7776; 0.1: 1.03 | !Capacity and Design Energy Input Fraction at | 1 | 6.667 | 32.222 | 108.89
0: 0.8265; 0.1: 1.03 | !Capacity and Design Energy Input Fraction at | 1 | 6.667 | 32.222 | 111.67
0: 0.8735; 0.1: 1.03 | !Capacity and Design Energy Input Fraction at | 1 | 6.667 | 32.222 | 113.89
0: 0.8959; 0.1: 1.03 | !Capacity and Design Energy Input Fraction at | 1 | 6.667 | 32.222 | 115
0: 0.9163; 0.1: 1.03 | !Capacity and Design Energy Input Fraction at | 1 | 6.667 | 32.222 | 116.11
0: 1.0531; 0.1: 0.97 | !Capacity and Design Energy Input Fraction at | 1 | 7.222 | 26.667 | 108.89
0: 1.1041; 0.1: 0.97 | !Capacity and Design Energy Input Fraction at | 1 | 7.222 | 26.667 | 111.67
0: 1.151; 0.1: 0.97 | !Capacity and Design Energy Input Fraction at | 1 | 7.222 | 26.667 | 113.89
0: 1.1735; 0.1: 0.97 | !Capacity and Design Energy Input Fraction at | 1 | 7.222 | 26.667 | 115
0: 1.1959; 0.1: 0.97 | !Capacity and Design Energy Input Fraction at | 1 | 7.222 | 26.667 | 116.11
0: 0.9245; 0.1: 0.99 | !Capacity and Design Energy Input Fraction at | 1 | 7.222 | 29.444 | 108.89
0: 0.9755; 0.1: 0.99 | !Capacity and Design Energy Input Fraction at | 1 | 7.222 | 29.444 | 111.67
0: 1.0224; 0.1: 0.99 | !Capacity and Design Energy Input Fraction at | 1 | 7.222 | 29.444 | 113.89
0: 1.0449; 0.1: 0.99 | !Capacity and Design Energy Input Fraction at | 1 | 7.222 | 29.444 | 115
0: 1.0673; 0.1: 0.99 | !Capacity and Design Energy Input Fraction at | 1 | 7.222 | 29.444 | 116.11
0: 0.798; 0.1: 1.02 | !Capacity and Design Energy Input Fraction at | 1 | 7.222 | 32.222 | 108.89
0: 0.8469; 0.1: 1.02 | !Capacity and Design Energy Input Fraction at | 1 | 7.222 | 32.222 | 111.67
0: 0.8939; 0.1: 1.02 | !Capacity and Design Energy Input Fraction at | 1 | 7.222 | 32.222 | 113.89
0: 0.9163; 0.1: 1.02 | !Capacity and Design Energy Input Fraction at | 1 | 7.222 | 32.222 | 115
0: 0.9388; 0.1: 1.02 | !Capacity and Design Energy Input Fraction at | 1 | 7.222 | 32.222 | 116.11
0: 1.0755; 0.1: 0.96 | !Capacity and Design Energy Input Fraction at | 1 | 7.778 | 26.667 | 108.89
0: 1.1265; 0.1: 0.96 | !Capacity and Design Energy Input Fraction at | 1 | 7.778 | 26.667 | 111.67
0: 1.1755; 0.1: 0.96 | !Capacity and Design Energy Input Fraction at | 1 | 7.778 | 26.667 | 113.89
0: 1.198; 0.1: 0.96 | !Capacity and Design Energy Input Fraction at | 1 | 7.778 | 26.667 | 115
0: 1.2184; 0.1: 0.96 | !Capacity and Design Energy Input Fraction at | 1 | 7.778 | 26.667 | 116.11
0: 0.9469; 0.1: 0.98 | !Capacity and Design Energy Input Fraction at | 1 | 7.778 | 29.444 | 108.89
0: 0.998; 0.1: 0.98 | !Capacity and Design Energy Input Fraction at | 1 | 7.778 | 29.444 | 111.67
0: 1.0449; 0.1: 0.98 | !Capacity and Design Energy Input Fraction at | 1 | 7.778 | 29.444 | 113.89
0: 1.0673; 0.1: 0.98 | !Capacity and Design Energy Input Fraction at | 1 | 7.778 | 29.444 | 115
0: 1.0898; 0.1: 0.98 | !Capacity and Design Energy Input Fraction at | 1 | 7.778 | 29.444 | 116.11
0: 0.8184; 0.1: 1.01 | !Capacity and Design Energy Input Fraction at | 1 | 7.778 | 32.222 | 108.89
0: 0.8694; 0.1: 1.01 | !Capacity and Design Energy Input Fraction at | 1 | 7.778 | 32.222 | 111.67
0: 0.9163; 0.1: 1.01 | !Capacity and Design Energy Input Fraction at | 1 | 7.778 | 32.222 | 113.89
0: 0.9388; 0.1: 1.01 | !Capacity and Design Energy Input Fraction at | 1 | 7.778 | 32.222 | 115
0: 0.9592; 0.1: 1.01 | !Capacity and Design Energy Input Fraction at | 1 | 7.778 | 32.222 | 116.11
0: 1.1204; 0.1: 0.95 | !Capacity and Design Energy Input Fraction at | 1 | 8.889 | 26.667 | 108.89
0: 1.1735; 0.1: 0.95 | !Capacity and Design Energy Input Fraction at | 1 | 8.889 | 26.667 | 111.67
0: 1.2204; 0.1: 0.95 | !Capacity and Design Energy Input Fraction at | 1 | 8.889 | 26.667 | 113.89
0: 1.2449; 0.1: 0.95 | !Capacity and Design Energy Input Fraction at | 1 | 8.889 | 26.667 | 115
0: 1.2673; 0.1: 0.95 | !Capacity and Design Energy Input Fraction at | 1 | 8.889 | 26.667 | 116.11
0: 0.9898; 0.1: 0.97 | !Capacity and Design Energy Input Fraction at | 1 | 8.889 | 29.444 | 108.89
0: 1.0408; 0.1: 0.97 | !Capacity and Design Energy Input Fraction at | 1 | 8.889 | 29.444 | 111.67
0: 1.0898; 0.1: 0.97 | !Capacity and Design Energy Input Fraction at | 1 | 8.889 | 29.444 | 113.89
0: 1.1122; 0.1: 0.97 | !Capacity and Design Energy Input Fraction at | 1 | 8.889 | 29.444 | 115
0: 1.1347; 0.1: 0.97 | !Capacity and Design Energy Input Fraction at | 1 | 8.889 | 29.444 | 116.11
0: 0.8592; 0.1: 1 | !Capacity and Design Energy Input Fraction at | 1 | 8.889 | 32.222 | 108.89
0: 0.9102; 0.1: 1 | !Capacity and Design Energy Input Fraction at | 1 | 8.889 | 32.222 | 111.67
0: 0.9592; 0.1: 1 | !Capacity and Design Energy Input Fraction at | 1 | 8.889 | 32.222 | 113.89
0: 0.9816; 0.1: 1 | !Capacity and Design Energy Input Fraction at | 1 | 8.889 | 32.222 | 115
0: 1.0041; 0.1: 1 | !Capacity and Design Energy Input Fraction at | 1 | 8.889 | 32.222 | 116.11
0: 1.1673; 0.1: 0.94 | !Capacity and Design Energy Input Fraction at | 1 | 10 | 26.667 | 108.89
0: 1.2204; 0.1: 0.94 | !Capacity and Design Energy Input Fraction at | 1 | 10 | 26.667 | 111.67
0: 1.2694; 0.1: 0.94 | !Capacity and Design Energy Input Fraction at | 1 | 10 | 26.667 | 113.89
0: 1.2898; 0.1: 0.94 | !Capacity and Design Energy Input Fraction at | 1 | 10 | 26.667 | 115
0: 1.2898; 0.1: 0.94 | !Capacity and Design Energy Input Fraction at | 1 | 10 | 26.667 | 116.11
0: 1.0347; 0.1: 0.96 | !Capacity and Design Energy Input Fraction at | 1 | 10 | 29.444 | 108.89
0: 1.0857; 0.1: 0.96 | !Capacity and Design Energy Input Fraction at | 1 | 10 | 29.444 | 111.67
0: 1.1347; 0.1: 0.96 | !Capacity and Design Energy Input Fraction at | 1 | 10 | 29.444 | 113.89
0: 1.1592; 0.1: 0.96 | !Capacity and Design Energy Input Fraction at | 1 | 10 | 29.444 | 115
0: 1.1796; 0.1: 0.96 | !Capacity and Design Energy Input Fraction at | 1 | 10 | 29.444 | 116.11
0: 0.902; 0.1: 0.98 | !Capacity and Design Energy Input Fraction at | 1 | 10 | 32.222 | 108.89
0: 0.9531; 0.1: 0.98 | !Capacity and Design Energy Input Fraction at | 1 | 10 | 32.222 | 111.67
0: 1.002; 0.1: 0.98 | !Capacity and Design Energy Input Fraction at | 1 | 10 | 32.222 | 113.89
0: 1.0245; 0.1: 0.98 | !Capacity and Design Energy Input Fraction at | 1 | 10 | 32.222 | 115
0: 1.0469; 0.1: 0.98 | !Capacity and Design Energy Input Fraction at | 1 | 10 | 32.222 | 116.11