## Chiller Performance3_3 (hidden)
| Anlagenname |  | Temp. Kühlwasser VL
| Anlagentyp |  | 30 | 30 | 32 | 32 | 34 | 34
| Temp. KW VL | Temp. KW RL | Kältekap. [KW] | Leistungsaufn. [kW] | Kältekap. [KW] | Leistungsaufn. [kW] | Kältekap. [KW] | Leistungsaufn. [kW]
| 5 | 0 | 783.72 | 157.2 | 766.84 | 163.4 | 749.16 | 170
| 7 | 0 | 840.32 | 159.6 | 822.74 | 165.7 | 805.16 | 172.1
| 9 | 0 | 899.39 | 162.3 | 881.11 | 168.3 | 862.83 | 174.6
| Nenndaten: | Temp. Kühlwasser VL: |  | 30 |  | Kältekap. [KW] | 840.32 | Kältekap. [kJ/hr] | 3025152 |  | COP: | 5.26
|  | Temp. KW VL: |  | 7 |  | Leistungsaufn. [kW] | 159.6 | Leistungsaufn. [kJ/hr] | 574560
| in kJ/hr |  | Capacity | Pel | Capacity | Pel | Capacity | Pel
| Temp. KW VL | Temp. KW RL | Kältekap. [kJ/hr] | Leistungsaufn. [kJ/hr] | Kältekap. [kJ/hr] | Leistungsaufn. [kJ/hr] | Kältekap. [kJ/hr] | Leistungsaufn. [kJ/hr]
| 5 | 0 | 2821392 | 565920 | 2760624 | 588240 | 2696976 | 612000
| 7 | 0 | 3025152 | 574560 | 2961864 | 596520 | 2898576 | 619560
| 9 | 0 | 3237804 | 584280 | 3171996 | 605880 | 3106188 | 628560
EER
| 5 | 0 | 4.9855 |  | 4.693 |  | 4.4068
| 7 | 0 | 5.2652 |  | 4.9652 |  | 4.6784
| 9 | 0 | 5.5415 |  | 5.2354 |  | 4.9418
|  |  | capacity ratio | COP ratio | capacity ratio | COP ratio | capacity ratio | COP ratio
| 5 | 0 | 0.93264 | 0.94781 | 0.91256 | 0.89221 | 0.89152 | 0.8378
| 7 | 0 | 1 | 1.001 | 0.97908 | 0.94396 | 0.95816 | 0.88944
| 9 | 0 | 1.0703 | 1.0535 | 1.0485 | 0.99531 | 1.0268 | 0.9395
Datei für Type 666
| 5 | 7 | 9 |  |  |  |  | !Chilled water leaving temperature (C)
| 30 | 32 | 34 |  |  |  |  | !Cooling water inlet temperature (C)
| 0.9326 | 0.9478 | [5 empty] | !Capacity ratio and COP ratio at | 5 | C oulet CHWT and | 30 | C inlet CWT
| 0.9125 | 0.8922 | [5 empty] | !Capacity ratio and COP ratio at | 5 | C oulet CHWT and | 32 | C inlet CWT
| 0.8915 | 0.8377 | [5 empty] | !Capacity ratio and COP ratio at | 5 | C oulet CHWT and | 34 | C inlet CWT
| 1 | 1.0009 | [5 empty] | !Capacity ratio and COP ratio at | 7 | C oulet CHWT and | 30 | C inlet CWT
| 0.979 | 0.9439 | [5 empty] | !Capacity ratio and COP ratio at | 7 | C oulet CHWT and | 32 | C inlet CWT
| 0.9581 | 0.8894 | [5 empty] | !Capacity ratio and COP ratio at | 7 | C oulet CHWT and | 34 | C inlet CWT
| 1.0702 | 1.0535 | [5 empty] | !Capacity ratio and COP ratio at | 9 | C oulet CHWT and | 30 | C inlet CWT
| 1.0485 | 0.9953 | [5 empty] | !Capacity ratio and COP ratio at | 9 | C oulet CHWT and | 32 | C inlet CWT
| 1.0267 | 0.9394 | [5 empty] | !Capacity ratio and COP ratio at | 9 | C oulet CHWT and | 34 | C inlet CWT
Format: mit Punkt
| 5 | 7 | 9 |  |  |  |  | !Chilled water leaving temperature (C)
| 30 | 32 | 34 |  |  |  |  | !Cooling water inlet temperature (C)
| 0.9326 | 0.9478 | [5 empty] | !Capacity ratio and COP ratio at | 5 | C oulet CHWT and | 30 | C inlet CWT
| 0.9125 | 0.8922 | [5 empty] | !Capacity ratio and COP ratio at | 5 | C oulet CHWT and | 32 | C inlet CWT
| 0.8915 | 0.8377 | [5 empty] | !Capacity ratio and COP ratio at | 5 | C oulet CHWT and | 34 | C inlet CWT
| 1 | 1.0009 | [5 empty] | !Capacity ratio and COP ratio at | 7 | C oulet CHWT and | 30 | C inlet CWT
| 0.979 | 0.9439 | [5 empty] | !Capacity ratio and COP ratio at | 7 | C oulet CHWT and | 32 | C inlet CWT
| 0.9581 | 0.8894 | [5 empty] | !Capacity ratio and COP ratio at | 7 | C oulet CHWT and | 34 | C inlet CWT
| 1.0702 | 1.0535 | [5 empty] | !Capacity ratio and COP ratio at | 9 | C oulet CHWT and | 30 | C inlet CWT
| 1.0485 | 0.9953 | [5 empty] | !Capacity ratio and COP ratio at | 9 | C oulet CHWT and | 32 | C inlet CWT
| 1.0267 | 0.9394 | [5 empty] | !Capacity ratio and COP ratio at | 9 | C oulet CHWT and | 34 | C inlet CWT

## Chiller Performance3_4 (hidden)
| Anlagenname |  | Temp. Kühlwasser VL
| Anlagentyp |  | 30 | 30 | 32 | 32 | 34 | 34 | 36 | 36
| Temp. KW VL | Temp. KW RL | Kältekap. [KW] | Leistungsaufn. [kW] | Kältekap. [KW] | Leistungsaufn. [kW] | Kältekap. [KW] | Leistungsaufn. [kW] | Kältekap. [KW] | Leistungsaufn. [kW]
| 5 | 0 | 783.72 | 157.2 | 766.84 | 163.4 | 749.16 | 170 | 1 | 1
| 7 | 0 | 840.32 | 159.6 | 822.74 | 165.7 | 805.16 | 172.1 | 1 | 1
| 9 | 0 | 899.39 | 162.3 | 881.11 | 168.3 | 862.83 | 174.6 | 1 | 1
| Nenndaten: | Temp. Kühlwasser VL: |  | 30 |  | Kältekap. [KW] | 840.32 | Kältekap. [kJ/hr] | 3025152 |  | COP: | 5.26
|  | Temp. KW VL: |  | 7 |  | Leistungsaufn. [kW] | 159.6 | Leistungsaufn. [kJ/hr] | 574560
| in kJ/hr |  | Capacity | Pel | Capacity | Pel | Capacity | Pel | Capacity | Pel
| Temp. KW VL | Temp. KW RL | Kältekap. [kJ/hr] | Leistungsaufn. [kJ/hr] | Kältekap. [kJ/hr] | Leistungsaufn. [kJ/hr] | Kältekap. [kJ/hr] | Leistungsaufn. [kJ/hr] | Kältekap. [kJ/hr] | Leistungsaufn. [kJ/hr]
| 5 | 0 | 2821392 | 565920 | 2760624 | 588240 | 2696976 | 612000 | 3600 | 3600
| 7 | 0 | 3025152 | 574560 | 2961864 | 596520 | 2898576 | 619560 | 3600 | 3600
| 9 | 0 | 3237804 | 584280 | 3171996 | 605880 | 3106188 | 628560 | 3600 | 3600
EER
| 5 | 0 | 4.9855 |  | 4.693 |  | 4.4068 |  | 1
| 7 | 0 | 5.2652 |  | 4.9652 |  | 4.6784 |  | 1
| 9 | 0 | 5.5415 |  | 5.2354 |  | 4.9418 |  | 1
|  |  | capacity ratio | COP ratio | capacity ratio | COP ratio | capacity ratio | COP ratio | capacity ratio | COP ratio
| 5 | 0 | 0.93264 | 0.94781 | 0.91256 | 0.89221 | 0.89152 | 0.8378 | 0.00119 | 0.19011
| 7 | 0 | 1 | 1.001 | 0.97908 | 0.94396 | 0.95816 | 0.88944 | 0.00119 | 0.19011
| 9 | 0 | 1.0703 | 1.0535 | 1.0485 | 0.99531 | 1.0268 | 0.9395 | 0.00119 | 0.19011
Datei für Type 666
| 5 | 7 | 9 |  |  |  |  | !Chilled water leaving temperature (C)
| 30 | 32 | 34 | 36 |  |  |  | !Cooling water inlet temperature (C)
| 0.9326 | 0.9478 | [5 empty] | !Capacity ratio and COP ratio at | 5 | C oulet CHWT and | 30 | C inlet CWT
| 0.9125 | 0.8922 | [5 empty] | !Capacity ratio and COP ratio at | 5 | C oulet CHWT and | 32 | C inlet CWT
| 0.8915 | 0.8377 | [5 empty] | !Capacity ratio and COP ratio at | 5 | C oulet CHWT and | 34 | C inlet CWT
| 0.0011 | 0.1901 | [5 empty] | !Capacity ratio and COP ratio at | 5 | C oulet CHWT and | 36 | C inlet CWT
| 1 | 1.0009 | [5 empty] | !Capacity ratio and COP ratio at | 7 | C oulet CHWT and | 30 | C inlet CWT
| 0.979 | 0.9439 | [5 empty] | !Capacity ratio and COP ratio at | 7 | C oulet CHWT and | 32 | C inlet CWT
| 0.9581 | 0.8894 | [5 empty] | !Capacity ratio and COP ratio at | 7 | C oulet CHWT and | 34 | C inlet CWT
| 0.0011 | 0.1901 | [5 empty] | !Capacity ratio and COP ratio at | 7 | C oulet CHWT and | 36 | C inlet CWT
| 1.0702 | 1.0535 | [5 empty] | !Capacity ratio and COP ratio at | 9 | C oulet CHWT and | 30 | C inlet CWT
| 1.0485 | 0.9953 | [5 empty] | !Capacity ratio and COP ratio at | 9 | C oulet CHWT and | 32 | C inlet CWT
| 1.0267 | 0.9394 | [5 empty] | !Capacity ratio and COP ratio at | 9 | C oulet CHWT and | 34 | C inlet CWT
| 0.0011 | 0.1901 | [5 empty] | !Capacity ratio and COP ratio at | 9 | C oulet CHWT and | 36 | C inlet CWT
Format: mit Punkt
| 5 | 7 | 9 |  |  |  |  | !Chilled water leaving temperature (C)
| 30 | 32 | 34 | 36 |  |  |  | !Cooling water inlet temperature (C)
| 0.9326 | 0.9478 | [5 empty] | !Capacity ratio and COP ratio at | 5 | C oulet CHWT and | 30 | C inlet CWT
| 0.9125 | 0.8922 | [5 empty] | !Capacity ratio and COP ratio at | 5 | C oulet CHWT and | 32 | C inlet CWT
| 0.8915 | 0.8377 | [5 empty] | !Capacity ratio and COP ratio at | 5 | C oulet CHWT and | 34 | C inlet CWT
| 0.0011 | 0.1901 | [5 empty] | !Capacity ratio and COP ratio at | 5 | C oulet CHWT and | 36 | C inlet CWT
| 1 | 1.0009 | [5 empty] | !Capacity ratio and COP ratio at | 7 | C oulet CHWT and | 30 | C inlet CWT
| 0.979 | 0.9439 | [5 empty] | !Capacity ratio and COP ratio at | 7 | C oulet CHWT and | 32 | C inlet CWT
| 0.9581 | 0.8894 | [5 empty] | !Capacity ratio and COP ratio at | 7 | C oulet CHWT and | 34 | C inlet CWT
| 0.0011 | 0.1901 | [5 empty] | !Capacity ratio and COP ratio at | 7 | C oulet CHWT and | 36 | C inlet CWT
| 1.0702 | 1.0535 | [5 empty] | !Capacity ratio and COP ratio at | 9 | C oulet CHWT and | 30 | C inlet CWT
| 1.0485 | 0.9953 | [5 empty] | !Capacity ratio and COP ratio at | 9 | C oulet CHWT and | 32 | C inlet CWT
| 1.0267 | 0.9394 | [5 empty] | !Capacity ratio and COP ratio at | 9 | C oulet CHWT and | 34 | C inlet CWT
| 0.0011 | 0.1901 | [5 empty] | !Capacity ratio and COP ratio at | 9 | C oulet CHWT and | 36 | C inlet CWT

## Chiller Performance3_5
| Anlagenname |  | Temp. Kühlwasser VL
| Anlagentyp |  | 30 | 30 | 32 | 32 | 34 | 34 | 36 | 36 | 38 | 38
| Temp. KW VL | Temp. KW RL | Kältekap. [KW] | Leistungsaufn. [kW] | Kältekap. [KW] | Leistungsaufn. [kW] | Kältekap. [KW] | Leistungsaufn. [kW] | Kältekap. [KW] | Leistungsaufn. [kW] | Kältekap. [KW] | Leistungsaufn. [kW]
| 5 | 0 | 783.72 | 157.2 | 766.84 | 163.4 | 749.16 | 170 | 1 | 1 | 1 | 1
| 7 | 0 | 840.32 | 159.6 | 822.74 | 165.7 | 805.16 | 172.1 | 1 | 1 | 1 | 1
| 9 | 0 | 899.39 | 162.3 | 881.11 | 168.3 | 862.83 | 174.6 | 1 | 1 | 3 | 3
| Nenndaten: | Temp. Kühlwasser VL: |  | 30 |  | Kältekap. [KW] | 840.32 | Kältekap. [kJ/hr] | 3025152 |  | COP: | 5.26
|  | Temp. KW VL: |  | 6 |  | Leistungsaufn. [kW] | 159.6 | Leistungsaufn. [kJ/hr] | 574560
| in kJ/hr |  | Capacity | Pel | Capacity | Pel | Capacity | Pel | Capacity | Pel | Capacity | Pel
| Temp. KW VL | Temp. KW RL | Kältekap. [kJ/hr] | Leistungsaufn. [kJ/hr] | Kältekap. [kJ/hr] | Leistungsaufn. [kJ/hr] | Kältekap. [kJ/hr] | Leistungsaufn. [kJ/hr] | Kältekap. [kJ/hr] | Leistungsaufn. [kJ/hr] | Kältekap. [kJ/hr] | Leistungsaufn. [kJ/hr]
| 5 | 0 | 2821392 | 565920 | 2760624 | 588240 | 2696976 | 612000 | 3600 | 3600 | 3600 | 3600
| 7 | 0 | 3025152 | 574560 | 2961864 | 596520 | 2898576 | 619560 | 3600 | 3600 | 3600 | 3600
| 9 | 0 | 3237804 | 584280 | 3171996 | 605880 | 3106188 | 628560 | 3600 | 3600 | 10800 | 10800
EER
| 5 | 0 | 4.9855 |  | 4.693 |  | 4.4068 |  | 1 |  | 1
| 7 | 0 | 5.2652 |  | 4.9652 |  | 4.6784 |  | 1 |  | 1
| 9 | 0 | 5.5415 |  | 5.2354 |  | 4.9418 |  | 1 |  | 1
|  |  | capacity ratio | COP ratio | capacity ratio | COP ratio | capacity ratio | COP ratio | capacity ratio | COP ratio | capacity ratio | COP ratio
| 5 | 0 | 0.93264 | 0.94781 | 0.91256 | 0.89221 | 0.89152 | 0.8378 | 0.00119 | 0.19011 | 0.00119 | 0.19011
| 7 | 0 | 1 | 1.001 | 0.97908 | 0.94396 | 0.95816 | 0.88944 | 0.00119 | 0.19011 | 0.00119 | 0.19011
| 9 | 0 | 1.0703 | 1.0535 | 1.0485 | 0.99531 | 1.0268 | 0.9395 | 0.00119 | 0.19011 | 0.0035701 | 0.19011
Datei für Type 666
| 5 | 7 | 9 |  |  |  |  | !Chilled water leaving temperature (C)
| 30 | 32 | 34 | 36 | 38 |  |  | !Cooling water inlet temperature (C)
| 0.9326 | 0.9478 | [5 empty] | !Capacity ratio and COP ratio at | 5 | C oulet CHWT and | 30 | C inlet CWT
| 0.9125 | 0.8922 | [5 empty] | !Capacity ratio and COP ratio at | 5 | C oulet CHWT and | 32 | C inlet CWT
| 0.8915 | 0.8377 | [5 empty] | !Capacity ratio and COP ratio at | 5 | C oulet CHWT and | 34 | C inlet CWT
| 0.0011 | 0.1901 | [5 empty] | !Capacity ratio and COP ratio at | 5 | C oulet CHWT and | 36 | C inlet CWT
| 0.0011 | 0.1901 | [5 empty] | !Capacity ratio and COP ratio at | 5 | C oulet CHWT and | 38 | C inlet CWT
| 1 | 1.0009 | [5 empty] | !Capacity ratio and COP ratio at | 7 | C oulet CHWT and | 30 | C inlet CWT
| 0.979 | 0.9439 | [5 empty] | !Capacity ratio and COP ratio at | 7 | C oulet CHWT and | 32 | C inlet CWT
| 0.9581 | 0.8894 | [5 empty] | !Capacity ratio and COP ratio at | 7 | C oulet CHWT and | 34 | C inlet CWT
| 0.0011 | 0.1901 | [5 empty] | !Capacity ratio and COP ratio at | 7 | C oulet CHWT and | 36 | C inlet CWT
| 0.0011 | 0.1901 | [5 empty] | !Capacity ratio and COP ratio at | 7 | C oulet CHWT and | 38 | C inlet CWT
| 1.0702 | 1.0535 | [5 empty] | !Capacity ratio and COP ratio at | 9 | C oulet CHWT and | 30 | C inlet CWT
| 1.0485 | 0.9953 | [5 empty] | !Capacity ratio and COP ratio at | 9 | C oulet CHWT and | 32 | C inlet CWT
| 1.0267 | 0.9394 | [5 empty] | !Capacity ratio and COP ratio at | 9 | C oulet CHWT and | 34 | C inlet CWT
| 0.0011 | 0.1901 | [5 empty] | !Capacity ratio and COP ratio at | 9 | C oulet CHWT and | 36 | C inlet CWT
| 0.0035 | 0.1901 | [5 empty] | !Capacity ratio and COP ratio at | 9 | C oulet CHWT and | 38 | C inlet CWT
Format: mit Punkt
| 5 | 7 | 9 |  |  |  |  | !Chilled water leaving temperature (C)
| 30 | 32 | 34 | 36 | 38 |  |  | !Cooling water inlet temperature (C)
| 0.9326 | 0.9478 | [5 empty] | !Capacity ratio and COP ratio at | 5 | C oulet CHWT and | 30 | C inlet CWT
| 0.9125 | 0.8922 | [5 empty] | !Capacity ratio and COP ratio at | 5 | C oulet CHWT and | 32 | C inlet CWT
| 0.8915 | 0.8377 | [5 empty] | !Capacity ratio and COP ratio at | 5 | C oulet CHWT and | 34 | C inlet CWT
| 0.0011 | 0.1901 | [5 empty] | !Capacity ratio and COP ratio at | 5 | C oulet CHWT and | 36 | C inlet CWT
| 0.0011 | 0.1901 | [5 empty] | !Capacity ratio and COP ratio at | 5 | C oulet CHWT and | 38 | C inlet CWT
| 1 | 1.0009 | [5 empty] | !Capacity ratio and COP ratio at | 7 | C oulet CHWT and | 30 | C inlet CWT
| 0.979 | 0.9439 | [5 empty] | !Capacity ratio and COP ratio at | 7 | C oulet CHWT and | 32 | C inlet CWT
| 0.9581 | 0.8894 | [5 empty] | !Capacity ratio and COP ratio at | 7 | C oulet CHWT and | 34 | C inlet CWT
| 0.0011 | 0.1901 | [5 empty] | !Capacity ratio and COP ratio at | 7 | C oulet CHWT and | 36 | C inlet CWT
| 0.0011 | 0.1901 | [5 empty] | !Capacity ratio and COP ratio at | 7 | C oulet CHWT and | 38 | C inlet CWT
| 1.0702 | 1.0535 | [5 empty] | !Capacity ratio and COP ratio at | 9 | C oulet CHWT and | 30 | C inlet CWT
| 1.0485 | 0.9953 | [5 empty] | !Capacity ratio and COP ratio at | 9 | C oulet CHWT and | 32 | C inlet CWT
| 1.0267 | 0.9394 | [5 empty] | !Capacity ratio and COP ratio at | 9 | C oulet CHWT and | 34 | C inlet CWT
| 0.0011 | 0.1901 | [5 empty] | !Capacity ratio and COP ratio at | 9 | C oulet CHWT and | 36 | C inlet CWT
| 0.0035 | 0.1901 | [5 empty] | !Capacity ratio and COP ratio at | 9 | C oulet CHWT and | 38 | C inlet CWT

## Chiller Performance3_6 (hidden)
| Anlagenname |  | Temp. Kühlwasser VL
| Anlagentyp |  | 20 | 20 | 25 | 25 | 30 | 30 | 35 | 35 | 40 | 40 | 45 | 45
| Temp. KW VL | Temp. KW RL | Kältekap. [KW] | Leistungsaufn. [kW] | Kältekap. [KW] | Leistungsaufn. [kW] | Kältekap. [KW] | Leistungsaufn. [kW] | Kältekap. [KW] | Leistungsaufn. [kW] | Kältekap. [KW] | Leistungsaufn. [kW] | Kältekap. [KW] | Leistungsaufn. [kW]
| 5 | 0 | 66.9 | 14.1 | 64.2 | 15.7 | 61.4 | 17.5 | 58.3 | 19.7 | 55 | 22.2 | 51.5 | 25
| 7 | 0 | 71 | 14.3 | 68.3 | 15.8 | 65.2 | 17.7 | 62 | 19.9 | 58.5 | 22.4 | 54.8 | 25.2
| 9 | 0 | 75.2 | 14.4 | 72.3 | 15.9 | 69.2 | 17.8 | 65.7 | 20 | 62.1 | 22.6 | 58.2 | 25.4
| Nenndaten: | Temp. Kühlwasser VL: |  | 30 |  | Kältekap. [KW] | 840.32 | Kältekap. [kJ/hr] | 3025152 |  | COP: | 5.26
|  | Temp. KW VL: |  | 7 |  | Leistungsaufn. [kW] | 159.6 | Leistungsaufn. [kJ/hr] | 574560
| in kJ/hr |  | Capacity | Pel | Capacity | Pel | Capacity | Pel | Capacity | Pel | Capacity | Pel | Capacity | Pel
| Temp. KW VL | Temp. KW RL | Kältekap. [kJ/hr] | Leistungsaufn. [kJ/hr] | Kältekap. [kJ/hr] | Leistungsaufn. [kJ/hr] | Kältekap. [kJ/hr] | Leistungsaufn. [kJ/hr] | Kältekap. [kJ/hr] | Leistungsaufn. [kJ/hr] | Kältekap. [kJ/hr] | Leistungsaufn. [kJ/hr] | Kältekap. [kJ/hr] | Leistungsaufn. [kJ/hr]
| 5 | 0 | 240840 | 50760 | 231120 | 56520 | 221040 | 63000 | 209880 | 70920 | 198000 | 79920 | 185400 | 90000
| 7 | 0 | 255600 | 51480 | 245880 | 56880 | 234720 | 63720 | 223200 | 71640 | 210600 | 80640 | 197280 | 90720
| 9 | 0 | 270720 | 51840 | 260280 | 57240 | 249120 | 64080 | 236520 | 72000 | 223560 | 81360 | 209520 | 91440
EER
| 5 | 0 | 4.7447 |  | 4.0892 |  | 3.5086 |  | 2.9594 |  | 2.4775 |  | 2.06
| 7 | 0 | 4.965 |  | 4.3228 |  | 3.6836 |  | 3.1156 |  | 2.6116 |  | 2.1746
| 9 | 0 | 5.2222 |  | 4.5472 |  | 3.8876 |  | 3.285 |  | 2.7478 |  | 2.2913
|  |  | capacity ratio | COP ratio | capacity ratio | COP ratio | capacity ratio | COP ratio | capacity ratio | COP ratio | capacity ratio | COP ratio | capacity ratio | COP ratio
| 5 | 0 | 0.079613 | 0.90203 | 0.076399 | 0.77741 | 0.073067 | 0.66703 | 0.069378 | 0.56262 | 0.065451 | 0.471 | 0.061286 | 0.39163
| 7 | 0 | 0.084492 | 0.94392 | 0.081279 | 0.82182 | 0.077589 | 0.70031 | 0.073781 | 0.59232 | 0.069616 | 0.4965 | 0.065213 | 0.41342
| 9 | 0 | 0.08949 | 0.99282 | 0.086039 | 0.86448 | 0.08235 | 0.7391 | 0.078185 | 0.62452 | 0.0739 | 0.52239 | 0.069259 | 0.43562
Datei für Type 666
| 5 | 7 | 9 |  |  |  |  | !Chilled water leaving temperature (C)
| 20 | 25 | 30 | 35 | 40 | 45 |  | !Cooling water inlet temperature (C)
| 0.0796 | 0.902 | [5 empty] | !Capacity ratio and COP ratio at | 5 | C oulet CHWT and | 20 | C inlet CWT
| 0.0763 | 0.7774 | [5 empty] | !Capacity ratio and COP ratio at | 5 | C oulet CHWT and | 25 | C inlet CWT
| 0.073 | 0.667 | [5 empty] | !Capacity ratio and COP ratio at | 5 | C oulet CHWT and | 30 | C inlet CWT
| 0.0693 | 0.5626 | [5 empty] | !Capacity ratio and COP ratio at | 5 | C oulet CHWT and | 35 | C inlet CWT
| 0.0654 | 0.471 | [5 empty] | !Capacity ratio and COP ratio at | 5 | C oulet CHWT and | 40 | C inlet CWT
| 0.0612 | 0.3916 | [5 empty] | !Capacity ratio and COP ratio at | 5 | C oulet CHWT and | 45 | C inlet CWT
| 0.0844 | 0.9439 | [5 empty] | !Capacity ratio and COP ratio at | 7 | C oulet CHWT and | 20 | C inlet CWT
| 0.0812 | 0.8218 | [5 empty] | !Capacity ratio and COP ratio at | 7 | C oulet CHWT and | 25 | C inlet CWT
| 0.0775 | 0.7003 | [5 empty] | !Capacity ratio and COP ratio at | 7 | C oulet CHWT and | 30 | C inlet CWT
| 0.0737 | 0.5923 | [5 empty] | !Capacity ratio and COP ratio at | 7 | C oulet CHWT and | 35 | C inlet CWT
| 0.0696 | 0.4965 | [5 empty] | !Capacity ratio and COP ratio at | 7 | C oulet CHWT and | 40 | C inlet CWT
| 0.0652 | 0.4134 | [5 empty] | !Capacity ratio and COP ratio at | 7 | C oulet CHWT and | 45 | C inlet CWT
| 0.0894 | 0.9928 | [5 empty] | !Capacity ratio and COP ratio at | 9 | C oulet CHWT and | 20 | C inlet CWT
| 0.086 | 0.8644 | [5 empty] | !Capacity ratio and COP ratio at | 9 | C oulet CHWT and | 25 | C inlet CWT
| 0.0823 | 0.739 | [5 empty] | !Capacity ratio and COP ratio at | 9 | C oulet CHWT and | 30 | C inlet CWT
| 0.0781 | 0.6245 | [5 empty] | !Capacity ratio and COP ratio at | 9 | C oulet CHWT and | 35 | C inlet CWT
| 0.0739 | 0.5223 | [5 empty] | !Capacity ratio and COP ratio at | 9 | C oulet CHWT and | 40 | C inlet CWT
| 0.0692 | 0.4356 | [5 empty] | !Capacity ratio and COP ratio at | 9 | C oulet CHWT and | 45 | C inlet CWT
Format: mit Punkt
| 5 | 7 | 9 |  |  |  |  | !Chilled water leaving temperature (C)
| 20 | 25 | 30 | 35 | 40 | 45 |  | !Cooling water inlet temperature (C)
| 0.0796 | 0.902 | [5 empty] | !Capacity ratio and COP ratio at | 5 | C oulet CHWT and | 20 | C inlet CWT
| 0.0763 | 0.7774 | [5 empty] | !Capacity ratio and COP ratio at | 5 | C oulet CHWT and | 25 | C inlet CWT
| 0.073 | 0.667 | [5 empty] | !Capacity ratio and COP ratio at | 5 | C oulet CHWT and | 30 | C inlet CWT
| 0.0693 | 0.5626 | [5 empty] | !Capacity ratio and COP ratio at | 5 | C oulet CHWT and | 35 | C inlet CWT
| 0.0654 | 0.471 | [5 empty] | !Capacity ratio and COP ratio at | 5 | C oulet CHWT and | 40 | C inlet CWT
| 0.0612 | 0.3916 | [5 empty] | !Capacity ratio and COP ratio at | 5 | C oulet CHWT and | 45 | C inlet CWT
| 0.0844 | 0.9439 | [5 empty] | !Capacity ratio and COP ratio at | 7 | C oulet CHWT and | 20 | C inlet CWT
| 0.0812 | 0.8218 | [5 empty] | !Capacity ratio and COP ratio at | 7 | C oulet CHWT and | 25 | C inlet CWT
| 0.0775 | 0.7003 | [5 empty] | !Capacity ratio and COP ratio at | 7 | C oulet CHWT and | 30 | C inlet CWT
| 0.0737 | 0.5923 | [5 empty] | !Capacity ratio and COP ratio at | 7 | C oulet CHWT and | 35 | C inlet CWT
| 0.0696 | 0.4965 | [5 empty] | !Capacity ratio and COP ratio at | 7 | C oulet CHWT and | 40 | C inlet CWT
| 0.0652 | 0.4134 | [5 empty] | !Capacity ratio and COP ratio at | 7 | C oulet CHWT and | 45 | C inlet CWT
| 0.0894 | 0.9928 | [5 empty] | !Capacity ratio and COP ratio at | 9 | C oulet CHWT and | 20 | C inlet CWT
| 0.086 | 0.8644 | [5 empty] | !Capacity ratio and COP ratio at | 9 | C oulet CHWT and | 25 | C inlet CWT
| 0.0823 | 0.739 | [5 empty] | !Capacity ratio and COP ratio at | 9 | C oulet CHWT and | 30 | C inlet CWT
| 0.0781 | 0.6245 | [5 empty] | !Capacity ratio and COP ratio at | 9 | C oulet CHWT and | 35 | C inlet CWT
| 0.0739 | 0.5223 | [5 empty] | !Capacity ratio and COP ratio at | 9 | C oulet CHWT and | 40 | C inlet CWT
| 0.0692 | 0.4356 | [5 empty] | !Capacity ratio and COP ratio at | 9 | C oulet CHWT and | 45 | C inlet CWT

## Chiller Performance4_3 (hidden)
| Anlagenname |  | Temp. Kühlwasser VL
| Anlagentyp |  | 30 | 30 | 32 | 32 | 34 | 34
| Temp. KW VL | Temp. KW RL | Kältekap. [KW] | Leistungsaufn. [kW] | Kältekap. [KW] | Leistungsaufn. [kW] | Kältekap. [KW] | Leistungsaufn. [kW]
| 5 | 0 | 783.72 | 157.2 | 766.84 | 163.4 | 749.16 | 170
| 7 | 0 | 840.32 | 159.6 | 822.74 | 165.7 | 805.16 | 172.1
| 8 | 0 | 1 | 1 | 1 | 1 | 1 | 1
| 9 | 0 | 899.39 | 162.3 | 881.11 | 168.3 | 862.83 | 174.6
| Nenndaten: | Temp. Kühlwasser VL: |  | 30 |  | Kältekap. [KW] | 840.32 | Kältekap. [kJ/hr] | 3025152 |  | COP: | 5.26
|  | Temp. KW VL: |  | 7 |  | Leistungsaufn. [kW] | 159.6 | Leistungsaufn. [kJ/hr] | 574560
| in kJ/hr |  | Capacity | Pel | Capacity | Pel | Capacity | Pel
| Temp. KW VL | Temp. KW RL | Kältekap. [kJ/hr] | Leistungsaufn. [kJ/hr] | Kältekap. [kJ/hr] | Leistungsaufn. [kJ/hr] | Kältekap. [kJ/hr] | Leistungsaufn. [kJ/hr]
| 5 | 0 | 2821392 | 565920 | 2760624 | 588240 | 2696976 | 612000
| 7 | 0 | 3025152 | 574560 | 2961864 | 596520 | 2898576 | 619560
| 8 | 0 | 3600 | 3600 | 3600 | 3600 | 3600 | 3600
| 9 | 0 | 3237804 | 584280 | 3171996 | 605880 | 3106188 | 628560
EER
| 5 | 0 | 4.9855 |  | 4.693 |  | 4.4068
| 7 | 0 | 5.2652 |  | 4.9652 |  | 4.6784
| 8 | 0 | 1 |  | 1 |  | 1
| 9 | 0 | 5.5415 |  | 5.2354 |  | 4.9418
|  |  | capacity ratio | COP ratio | capacity ratio | COP ratio | capacity ratio | COP ratio
| 5 | 0 | 0.93264 | 0.94781 | 0.91256 | 0.89221 | 0.89152 | 0.8378
| 7 | 0 | 1 | 1.001 | 0.97908 | 0.94396 | 0.95816 | 0.88944
| 8 | 0 | 0.00119 | 0.19011 | 0.00119 | 0.19011 | 0.00119 | 0.19011
| 9 | 0 | 1.0703 | 1.0535 | 1.0485 | 0.99531 | 1.0268 | 0.9395
Datei für Type 666
| 5 | 7 | 8 | 9 |  |  |  | !Chilled water leaving temperature (C)
| 30 | 32 | 34 |  |  |  |  | !Cooling water inlet temperature (C)
| 0.9326 | 0.9478 | [5 empty] | !Capacity ratio and COP ratio at | 5 | C oulet CHWT and | 30 | C inlet CWT
| 0.9125 | 0.8922 | [5 empty] | !Capacity ratio and COP ratio at | 5 | C oulet CHWT and | 32 | C inlet CWT
| 0.8915 | 0.8377 | [5 empty] | !Capacity ratio and COP ratio at | 5 | C oulet CHWT and | 34 | C inlet CWT
| 1 | 1.0009 | [5 empty] | !Capacity ratio and COP ratio at | 7 | C oulet CHWT and | 30 | C inlet CWT
| 0.979 | 0.9439 | [5 empty] | !Capacity ratio and COP ratio at | 7 | C oulet CHWT and | 32 | C inlet CWT
| 0.9581 | 0.8894 | [5 empty] | !Capacity ratio and COP ratio at | 7 | C oulet CHWT and | 34 | C inlet CWT
| 0.0011 | 0.1901 | [5 empty] | !Capacity ratio and COP ratio at | 8 | C oulet CHWT and | 30 | C inlet CWT
| 0.0011 | 0.1901 | [5 empty] | !Capacity ratio and COP ratio at | 8 | C oulet CHWT and | 32 | C inlet CWT
| 0.0011 | 0.1901 | [5 empty] | !Capacity ratio and COP ratio at | 8 | C oulet CHWT and | 34 | C inlet CWT
| 1.0702 | 1.0535 | [5 empty] | !Capacity ratio and COP ratio at | 9 | C oulet CHWT and | 30 | C inlet CWT
| 1.0485 | 0.9953 | [5 empty] | !Capacity ratio and COP ratio at | 9 | C oulet CHWT and | 32 | C inlet CWT
| 1.0267 | 0.9394 | [5 empty] | !Capacity ratio and COP ratio at | 9 | C oulet CHWT and | 34 | C inlet CWT
Format: mit Punkt
| 5 | 7 | 8 | 9 |  |  |  | !Chilled water leaving temperature (C)
| 30 | 32 | 34 |  |  |  |  | !Cooling water inlet temperature (C)
| 0.9326 | 0.9478 | [5 empty] | !Capacity ratio and COP ratio at | 5 | C oulet CHWT and | 30 | C inlet CWT
| 0.9125 | 0.8922 | [5 empty] | !Capacity ratio and COP ratio at | 5 | C oulet CHWT and | 32 | C inlet CWT
| 0.8915 | 0.8377 | [5 empty] | !Capacity ratio and COP ratio at | 5 | C oulet CHWT and | 34 | C inlet CWT
| 1 | 1.0009 | [5 empty] | !Capacity ratio and COP ratio at | 7 | C oulet CHWT and | 30 | C inlet CWT
| 0.979 | 0.9439 | [5 empty] | !Capacity ratio and COP ratio at | 7 | C oulet CHWT and | 32 | C inlet CWT
| 0.9581 | 0.8894 | [5 empty] | !Capacity ratio and COP ratio at | 7 | C oulet CHWT and | 34 | C inlet CWT
| 0.0011 | 0.1901 | [5 empty] | !Capacity ratio and COP ratio at | 8 | C oulet CHWT and | 30 | C inlet CWT
| 0.0011 | 0.1901 | [5 empty] | !Capacity ratio and COP ratio at | 8 | C oulet CHWT and | 32 | C inlet CWT
| 0.0011 | 0.1901 | [5 empty] | !Capacity ratio and COP ratio at | 8 | C oulet CHWT and | 34 | C inlet CWT
| 1.0702 | 1.0535 | [5 empty] | !Capacity ratio and COP ratio at | 9 | C oulet CHWT and | 30 | C inlet CWT
| 1.0485 | 0.9953 | [5 empty] | !Capacity ratio and COP ratio at | 9 | C oulet CHWT and | 32 | C inlet CWT
| 1.0267 | 0.9394 | [5 empty] | !Capacity ratio and COP ratio at | 9 | C oulet CHWT and | 34 | C inlet CWT

## Chiller Performance4_4 (hidden)
| Anlagenname |  | Temp. Kühlwasser VL
| Anlagentyp |  | 30 | 30 | 32 | 32 | 34 | 34 | 36 | 36
| Temp. KW VL | Temp. KW RL | Kältekap. [KW] | Leistungsaufn. [kW] | Kältekap. [KW] | Leistungsaufn. [kW] | Kältekap. [KW] | Leistungsaufn. [kW] | Kältekap. [KW] | Leistungsaufn. [kW]
| 5 | 0 | 783.72 | 157.2 | 766.84 | 163.4 | 749.16 | 170 | 1 | 2
| 7 | 0 | 840.32 | 159.6 | 822.74 | 165.7 | 805.16 | 172.1 | 1 | 1
| 8 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| 9 | 0 | 899.39 | 162.3 | 881.11 | 168.3 | 862.83 | 174.6 | 51 | 5
| Nenndaten: | Temp. Kühlwasser VL: |  | 30 |  | Kältekap. [KW] | 840.32 | Kältekap. [kJ/hr] | 3025152 |  | COP: | 5.26
|  | Temp. KW VL: |  | 7 |  | Leistungsaufn. [kW] | 159.6 | Leistungsaufn. [kJ/hr] | 574560
| in kJ/hr |  | Capacity | Pel | Capacity | Pel | Capacity | Pel | Capacity | Pel
| Temp. KW VL | Temp. KW RL | Kältekap. [kJ/hr] | Leistungsaufn. [kJ/hr] | Kältekap. [kJ/hr] | Leistungsaufn. [kJ/hr] | Kältekap. [kJ/hr] | Leistungsaufn. [kJ/hr] | Kältekap. [kJ/hr] | Leistungsaufn. [kJ/hr]
| 5 | 0 | 2821392 | 565920 | 2760624 | 588240 | 2696976 | 612000 | 3600 | 7200
| 7 | 0 | 3025152 | 574560 | 2961864 | 596520 | 2898576 | 619560 | 3600 | 3600
| 8 | 0 | 3600 | 3600 | 3600 | 3600 | 3600 | 3600 | 3600 | 3600
| 9 | 0 | 3237804 | 584280 | 3171996 | 605880 | 3106188 | 628560 | 183600 | 18000
EER
| 5 | 0 | 4.9855 |  | 4.693 |  | 4.4068 |  | 0.5
| 7 | 0 | 5.2652 |  | 4.9652 |  | 4.6784 |  | 1
| 8 | 0 | 1 |  | 1 |  | 1 |  | 1
| 9 | 0 | 5.5415 |  | 5.2354 |  | 4.9418 |  | 10.2
|  |  | capacity ratio | COP ratio | capacity ratio | COP ratio | capacity ratio | COP ratio | capacity ratio | COP ratio
| 5 | 0 | 0.93264 | 0.94781 | 0.91256 | 0.89221 | 0.89152 | 0.8378 | 0.00119 | 0.095057
| 7 | 0 | 1 | 1.001 | 0.97908 | 0.94396 | 0.95816 | 0.88944 | 0.00119 | 0.19011
| 8 | 0 | 0.00119 | 0.19011 | 0.00119 | 0.19011 | 0.00119 | 0.19011 | 0.00119 | 0.19011
| 9 | 0 | 1.0703 | 1.0535 | 1.0485 | 0.99531 | 1.0268 | 0.9395 | 0.060691 | 1.9392
Datei für Type 666
| 5 | 7 | 8 | 9 |  |  |  | !Chilled water leaving temperature (C)
| 30 | 32 | 34 | 36 |  |  |  | !Cooling water inlet temperature (C)
| 0.9326 | 0.9478 | [5 empty] | !Capacity ratio and COP ratio at | 5 | C oulet CHWT and | 30 | C inlet CWT
| 0.9125 | 0.8922 | [5 empty] | !Capacity ratio and COP ratio at | 5 | C oulet CHWT and | 32 | C inlet CWT
| 0.8915 | 0.8377 | [5 empty] | !Capacity ratio and COP ratio at | 5 | C oulet CHWT and | 34 | C inlet CWT
| 0.0011 | 0.095 | [5 empty] | !Capacity ratio and COP ratio at | 5 | C oulet CHWT and | 36 | C inlet CWT
| 1 | 1.0009 | [5 empty] | !Capacity ratio and COP ratio at | 7 | C oulet CHWT and | 30 | C inlet CWT
| 0.979 | 0.9439 | [5 empty] | !Capacity ratio and COP ratio at | 7 | C oulet CHWT and | 32 | C inlet CWT
| 0.9581 | 0.8894 | [5 empty] | !Capacity ratio and COP ratio at | 7 | C oulet CHWT and | 34 | C inlet CWT
| 0.0011 | 0.1901 | [5 empty] | !Capacity ratio and COP ratio at | 7 | C oulet CHWT and | 36 | C inlet CWT
| 0.0011 | 0.1901 | [5 empty] | !Capacity ratio and COP ratio at | 8 | C oulet CHWT and | 30 | C inlet CWT
| 0.0011 | 0.1901 | [5 empty] | !Capacity ratio and COP ratio at | 8 | C oulet CHWT and | 32 | C inlet CWT
| 0.0011 | 0.1901 | [5 empty] | !Capacity ratio and COP ratio at | 8 | C oulet CHWT and | 34 | C inlet CWT
| 0.0011 | 0.1901 | [5 empty] | !Capacity ratio and COP ratio at | 8 | C oulet CHWT and | 36 | C inlet CWT
| 1.0702 | 1.0535 | [5 empty] | !Capacity ratio and COP ratio at | 9 | C oulet CHWT and | 30 | C inlet CWT
| 1.0485 | 0.9953 | [5 empty] | !Capacity ratio and COP ratio at | 9 | C oulet CHWT and | 32 | C inlet CWT
| 1.0267 | 0.9394 | [5 empty] | !Capacity ratio and COP ratio at | 9 | C oulet CHWT and | 34 | C inlet CWT
| 0.0606 | 1.9391 | [5 empty] | !Capacity ratio and COP ratio at | 9 | C oulet CHWT and | 36 | C inlet CWT
Format: mit Punkt
| 5 | 7 | 8 | 9 |  |  |  | !Chilled water leaving temperature (C)
| 30 | 32 | 34 | 36 |  |  |  | !Cooling water inlet temperature (C)
| 0.9326 | 0.9478 | [5 empty] | !Capacity ratio and COP ratio at | 5 | C oulet CHWT and | 30 | C inlet CWT
| 0.9125 | 0.8922 | [5 empty] | !Capacity ratio and COP ratio at | 5 | C oulet CHWT and | 32 | C inlet CWT
| 0.8915 | 0.8377 | [5 empty] | !Capacity ratio and COP ratio at | 5 | C oulet CHWT and | 34 | C inlet CWT
| 0.0011 | 0.095 | [5 empty] | !Capacity ratio and COP ratio at | 5 | C oulet CHWT and | 36 | C inlet CWT
| 1 | 1.0009 | [5 empty] | !Capacity ratio and COP ratio at | 7 | C oulet CHWT and | 30 | C inlet CWT
| 0.979 | 0.9439 | [5 empty] | !Capacity ratio and COP ratio at | 7 | C oulet CHWT and | 32 | C inlet CWT
| 0.9581 | 0.8894 | [5 empty] | !Capacity ratio and COP ratio at | 7 | C oulet CHWT and | 34 | C inlet CWT
| 0.0011 | 0.1901 | [5 empty] | !Capacity ratio and COP ratio at | 7 | C oulet CHWT and | 36 | C inlet CWT
| 0.0011 | 0.1901 | [5 empty] | !Capacity ratio and COP ratio at | 8 | C oulet CHWT and | 30 | C inlet CWT
| 0.0011 | 0.1901 | [5 empty] | !Capacity ratio and COP ratio at | 8 | C oulet CHWT and | 32 | C inlet CWT
| 0.0011 | 0.1901 | [5 empty] | !Capacity ratio and COP ratio at | 8 | C oulet CHWT and | 34 | C inlet CWT
| 0.0011 | 0.1901 | [5 empty] | !Capacity ratio and COP ratio at | 8 | C oulet CHWT and | 36 | C inlet CWT
| 1.0702 | 1.0535 | [5 empty] | !Capacity ratio and COP ratio at | 9 | C oulet CHWT and | 30 | C inlet CWT
| 1.0485 | 0.9953 | [5 empty] | !Capacity ratio and COP ratio at | 9 | C oulet CHWT and | 32 | C inlet CWT
| 1.0267 | 0.9394 | [5 empty] | !Capacity ratio and COP ratio at | 9 | C oulet CHWT and | 34 | C inlet CWT
| 0.0606 | 1.9391 | [5 empty] | !Capacity ratio and COP ratio at | 9 | C oulet CHWT and | 36 | C inlet CWT

## Chiller Performance4_5 (hidden)
| Anlagenname |  | Temp. Kühlwasser VL
| Anlagentyp |  | 30 | 30 | 32 | 32 | 34 | 34 | 36 | 36 | 38 | 38
| Temp. KW VL | Temp. KW RL | Kältekap. [KW] | Leistungsaufn. [kW] | Kältekap. [KW] | Leistungsaufn. [kW] | Kältekap. [KW] | Leistungsaufn. [kW] | Kältekap. [KW] | Leistungsaufn. [kW] | Kältekap. [KW] | Leistungsaufn. [kW]
| 5 | 0 | 783.72 | 157.2 | 766.84 | 163.4 | 749.16 | 170 | 1 | 2 | 5 | 51
| 7 | 0 | 840.32 | 159.6 | 822.74 | 165.7 | 805.16 | 172.1 | 1 | 1 | 51 | 95
| 8 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| 9 | 0 | 899.39 | 162.3 | 881.11 | 168.3 | 862.83 | 174.6 | 51 | 5 | 6 | 5
| Nenndaten: | Temp. Kühlwasser VL: |  | 30 |  | Kältekap. [KW] | 840.32 | Kältekap. [kJ/hr] | 3025152 |  | COP: | 5.26
|  | Temp. KW VL: |  | 7 |  | Leistungsaufn. [kW] | 159.6 | Leistungsaufn. [kJ/hr] | 574560
| in kJ/hr |  | Capacity | Pel | Capacity | Pel | Capacity | Pel | Capacity | Pel | Capacity | Pel
| Temp. KW VL | Temp. KW RL | Kältekap. [kJ/hr] | Leistungsaufn. [kJ/hr] | Kältekap. [kJ/hr] | Leistungsaufn. [kJ/hr] | Kältekap. [kJ/hr] | Leistungsaufn. [kJ/hr] | Kältekap. [kJ/hr] | Leistungsaufn. [kJ/hr] | Kältekap. [kJ/hr] | Leistungsaufn. [kJ/hr]
| 5 | 0 | 2821392 | 565920 | 2760624 | 588240 | 2696976 | 612000 | 3600 | 7200 | 18000 | 183600
| 7 | 0 | 3025152 | 574560 | 2961864 | 596520 | 2898576 | 619560 | 3600 | 3600 | 183600 | 342000
| 8 | 0 | 3600 | 3600 | 3600 | 3600 | 3600 | 3600 | 3600 | 3600 | 3600 | 3600
| 9 | 0 | 3237804 | 584280 | 3171996 | 605880 | 3106188 | 628560 | 183600 | 18000 | 21600 | 18000
EER
| 5 | 0 | 4.9855 |  | 4.693 |  | 4.4068 |  | 0.5 |  | 0.098039
| 7 | 0 | 5.2652 |  | 4.9652 |  | 4.6784 |  | 1 |  | 0.53684
| 8 | 0 | 1 |  | 1 |  | 1 |  | 1 |  | 1
| 9 | 0 | 5.5415 |  | 5.2354 |  | 4.9418 |  | 10.2 |  | 1.2
|  |  | capacity ratio | COP ratio | capacity ratio | COP ratio | capacity ratio | COP ratio | capacity ratio | COP ratio | capacity ratio | COP ratio
| 5 | 0 | 0.93264 | 0.94781 | 0.91256 | 0.89221 | 0.89152 | 0.8378 | 0.00119 | 0.095057 | 0.0059501 | 0.018639
| 7 | 0 | 1 | 1.001 | 0.97908 | 0.94396 | 0.95816 | 0.88944 | 0.00119 | 0.19011 | 0.060691 | 0.10206
| 8 | 0 | 0.00119 | 0.19011 | 0.00119 | 0.19011 | 0.00119 | 0.19011 | 0.00119 | 0.19011 | 0.00119 | 0.19011
| 9 | 0 | 1.0703 | 1.0535 | 1.0485 | 0.99531 | 1.0268 | 0.9395 | 0.060691 | 1.9392 | 0.0071401 | 0.22814
Datei für Type 666
| 5 | 7 | 8 | 9 |  |  |  | !Chilled water leaving temperature (C)
| 30 | 32 | 34 | 36 | 38 |  |  | !Cooling water inlet temperature (C)
| 0.9326 | 0.9478 | [5 empty] | !Capacity ratio and COP ratio at | 5 | C oulet CHWT and | 30 | C inlet CWT
| 0.9125 | 0.8922 | [5 empty] | !Capacity ratio and COP ratio at | 5 | C oulet CHWT and | 32 | C inlet CWT
| 0.8915 | 0.8377 | [5 empty] | !Capacity ratio and COP ratio at | 5 | C oulet CHWT and | 34 | C inlet CWT
| 0.0011 | 0.095 | [5 empty] | !Capacity ratio and COP ratio at | 5 | C oulet CHWT and | 36 | C inlet CWT
| 0.0059 | 0.0186 | [5 empty] | !Capacity ratio and COP ratio at | 5 | C oulet CHWT and | 38 | C inlet CWT
| 1 | 1.0009 | [5 empty] | !Capacity ratio and COP ratio at | 7 | C oulet CHWT and | 30 | C inlet CWT
| 0.979 | 0.9439 | [5 empty] | !Capacity ratio and COP ratio at | 7 | C oulet CHWT and | 32 | C inlet CWT
| 0.9581 | 0.8894 | [5 empty] | !Capacity ratio and COP ratio at | 7 | C oulet CHWT and | 34 | C inlet CWT
| 0.0011 | 0.1901 | [5 empty] | !Capacity ratio and COP ratio at | 7 | C oulet CHWT and | 36 | C inlet CWT
| 0.0606 | 0.102 | [5 empty] | !Capacity ratio and COP ratio at | 7 | C oulet CHWT and | 38 | C inlet CWT
| 0.0011 | 0.1901 | [5 empty] | !Capacity ratio and COP ratio at | 8 | C oulet CHWT and | 30 | C inlet CWT
| 0.0011 | 0.1901 | [5 empty] | !Capacity ratio and COP ratio at | 8 | C oulet CHWT and | 32 | C inlet CWT
| 0.0011 | 0.1901 | [5 empty] | !Capacity ratio and COP ratio at | 8 | C oulet CHWT and | 34 | C inlet CWT
| 0.0011 | 0.1901 | [5 empty] | !Capacity ratio and COP ratio at | 8 | C oulet CHWT and | 36 | C inlet CWT
| 0.0011 | 0.1901 | [5 empty] | !Capacity ratio and COP ratio at | 8 | C oulet CHWT and | 38 | C inlet CWT
| 1.0702 | 1.0535 | [5 empty] | !Capacity ratio and COP ratio at | 9 | C oulet CHWT and | 30 | C inlet CWT
| 1.0485 | 0.9953 | [5 empty] | !Capacity ratio and COP ratio at | 9 | C oulet CHWT and | 32 | C inlet CWT
| 1.0267 | 0.9394 | [5 empty] | !Capacity ratio and COP ratio at | 9 | C oulet CHWT and | 34 | C inlet CWT
| 0.0606 | 1.9391 | [5 empty] | !Capacity ratio and COP ratio at | 9 | C oulet CHWT and | 36 | C inlet CWT
| 0.0071 | 0.2281 | [5 empty] | !Capacity ratio and COP ratio at | 9 | C oulet CHWT and | 38 | C inlet CWT
Format: mit Punkt
| 5 | 7 | 8 | 9 |  |  |  | !Chilled water leaving temperature (C)
| 30 | 32 | 34 | 36 | 38 |  |  | !Cooling water inlet temperature (C)
| 0.9326 | 0.9478 | [5 empty] | !Capacity ratio and COP ratio at | 5 | C oulet CHWT and | 30 | C inlet CWT
| 0.9125 | 0.8922 | [5 empty] | !Capacity ratio and COP ratio at | 5 | C oulet CHWT and | 32 | C inlet CWT
| 0.8915 | 0.8377 | [5 empty] | !Capacity ratio and COP ratio at | 5 | C oulet CHWT and | 34 | C inlet CWT
| 0.0011 | 0.095 | [5 empty] | !Capacity ratio and COP ratio at | 5 | C oulet CHWT and | 36 | C inlet CWT
| 0.0059 | 0.0186 | [5 empty] | !Capacity ratio and COP ratio at | 5 | C oulet CHWT and | 38 | C inlet CWT
| 1 | 1.0009 | [5 empty] | !Capacity ratio and COP ratio at | 7 | C oulet CHWT and | 30 | C inlet CWT
| 0.979 | 0.9439 | [5 empty] | !Capacity ratio and COP ratio at | 7 | C oulet CHWT and | 32 | C inlet CWT
| 0.9581 | 0.8894 | [5 empty] | !Capacity ratio and COP ratio at | 7 | C oulet CHWT and | 34 | C inlet CWT
| 0.0011 | 0.1901 | [5 empty] | !Capacity ratio and COP ratio at | 7 | C oulet CHWT and | 36 | C inlet CWT
| 0.0606 | 0.102 | [5 empty] | !Capacity ratio and COP ratio at | 7 | C oulet CHWT and | 38 | C inlet CWT
| 0.0011 | 0.1901 | [5 empty] | !Capacity ratio and COP ratio at | 8 | C oulet CHWT and | 30 | C inlet CWT
| 0.0011 | 0.1901 | [5 empty] | !Capacity ratio and COP ratio at | 8 | C oulet CHWT and | 32 | C inlet CWT
| 0.0011 | 0.1901 | [5 empty] | !Capacity ratio and COP ratio at | 8 | C oulet CHWT and | 34 | C inlet CWT
| 0.0011 | 0.1901 | [5 empty] | !Capacity ratio and COP ratio at | 8 | C oulet CHWT and | 36 | C inlet CWT
| 0.0011 | 0.1901 | [5 empty] | !Capacity ratio and COP ratio at | 8 | C oulet CHWT and | 38 | C inlet CWT
| 1.0702 | 1.0535 | [5 empty] | !Capacity ratio and COP ratio at | 9 | C oulet CHWT and | 30 | C inlet CWT
| 1.0485 | 0.9953 | [5 empty] | !Capacity ratio and COP ratio at | 9 | C oulet CHWT and | 32 | C inlet CWT
| 1.0267 | 0.9394 | [5 empty] | !Capacity ratio and COP ratio at | 9 | C oulet CHWT and | 34 | C inlet CWT
| 0.0606 | 1.9391 | [5 empty] | !Capacity ratio and COP ratio at | 9 | C oulet CHWT and | 36 | C inlet CWT
| 0.0071 | 0.2281 | [5 empty] | !Capacity ratio and COP ratio at | 9 | C oulet CHWT and | 38 | C inlet CWT

## Chiller Performance4_6 (hidden)
| Anlagenname |  | Temp. Kühlwasser VL
| Anlagentyp |  | 30 | 30 | 32 | 32 | 34 | 34 | 36 | 36 | 38 | 38 | 40 | 40
| Temp. KW VL | Temp. KW RL | Kältekap. [KW] | Leistungsaufn. [kW] | Kältekap. [KW] | Leistungsaufn. [kW] | Kältekap. [KW] | Leistungsaufn. [kW] | Kältekap. [KW] | Leistungsaufn. [kW] | Kältekap. [KW] | Leistungsaufn. [kW] | Kältekap. [KW] | Leistungsaufn. [kW]
| 5 | 0 | 783.72 | 157.2 | 766.84 | 163.4 | 749.16 | 170 | 1 | 2 | 5 | 51 | 2 | 2
| 7 | 0 | 840.32 | 159.6 | 822.74 | 165.7 | 805.16 | 172.1 | 1 | 1 | 51 | 95 | 2365 | 26
| 8 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| 9 | 0 | 899.39 | 162.3 | 881.11 | 168.3 | 862.83 | 174.6 | 51 | 5 | 6 | 5 | 62 | 6
| Nenndaten: | Temp. Kühlwasser VL: |  | 30 |  | Kältekap. [KW] | 840.32 | Kältekap. [kJ/hr] | 3025152 |  | COP: | 5.26
|  | Temp. KW VL: |  | 7 |  | Leistungsaufn. [kW] | 159.6 | Leistungsaufn. [kJ/hr] | 574560
| in kJ/hr |  | Capacity | Pel | Capacity | Pel | Capacity | Pel | Capacity | Pel | Capacity | Pel | Capacity | Pel
| Temp. KW VL | Temp. KW RL | Kältekap. [kJ/hr] | Leistungsaufn. [kJ/hr] | Kältekap. [kJ/hr] | Leistungsaufn. [kJ/hr] | Kältekap. [kJ/hr] | Leistungsaufn. [kJ/hr] | Kältekap. [kJ/hr] | Leistungsaufn. [kJ/hr] | Kältekap. [kJ/hr] | Leistungsaufn. [kJ/hr] | Kältekap. [kJ/hr] | Leistungsaufn. [kJ/hr]
| 5 | 0 | 2821392 | 565920 | 2760624 | 588240 | 2696976 | 612000 | 3600 | 7200 | 18000 | 183600 | 7200 | 7200
| 7 | 0 | 3025152 | 574560 | 2961864 | 596520 | 2898576 | 619560 | 3600 | 3600 | 183600 | 342000 | 8514000 | 93600
| 8 | 0 | 3600 | 3600 | 3600 | 3600 | 3600 | 3600 | 3600 | 3600 | 3600 | 3600 | 3600 | 3600
| 9 | 0 | 3237804 | 584280 | 3171996 | 605880 | 3106188 | 628560 | 183600 | 18000 | 21600 | 18000 | 223200 | 21600
EER
| 5 | 0 | 4.9855 |  | 4.693 |  | 4.4068 |  | 0.5 |  | 0.098039 |  | 1
| 7 | 0 | 5.2652 |  | 4.9652 |  | 4.6784 |  | 1 |  | 0.53684 |  | 90.9615
| 8 | 0 | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1
| 9 | 0 | 5.5415 |  | 5.2354 |  | 4.9418 |  | 10.2 |  | 1.2 |  | 10.3333
|  |  | capacity ratio | COP ratio | capacity ratio | COP ratio | capacity ratio | COP ratio | capacity ratio | COP ratio | capacity ratio | COP ratio | capacity ratio | COP ratio
| 5 | 0 | 0.93264 | 0.94781 | 0.91256 | 0.89221 | 0.89152 | 0.8378 | 0.00119 | 0.095057 | 0.0059501 | 0.018639 | 0.00238 | 0.19011
| 7 | 0 | 1 | 1.001 | 0.97908 | 0.94396 | 0.95816 | 0.88944 | 0.00119 | 0.19011 | 0.060691 | 0.10206 | 2.8144 | 17.2931
| 8 | 0 | 0.00119 | 0.19011 | 0.00119 | 0.19011 | 0.00119 | 0.19011 | 0.00119 | 0.19011 | 0.00119 | 0.19011 | 0.00119 | 0.19011
| 9 | 0 | 1.0703 | 1.0535 | 1.0485 | 0.99531 | 1.0268 | 0.9395 | 0.060691 | 1.9392 | 0.0071401 | 0.22814 | 0.073781 | 1.9645
Datei für Type 666
| 5 | 7 | 8 | 9 |  |  |  | !Chilled water leaving temperature (C)
| 30 | 32 | 34 | 36 | 38 | 40 |  | !Cooling water inlet temperature (C)
| 0.9326 | 0.9478 | [5 empty] | !Capacity ratio and COP ratio at | 5 | C oulet CHWT and | 30 | C inlet CWT
| 0.9125 | 0.8922 | [5 empty] | !Capacity ratio and COP ratio at | 5 | C oulet CHWT and | 32 | C inlet CWT
| 0.8915 | 0.8377 | [5 empty] | !Capacity ratio and COP ratio at | 5 | C oulet CHWT and | 34 | C inlet CWT
| 0.0011 | 0.095 | [5 empty] | !Capacity ratio and COP ratio at | 5 | C oulet CHWT and | 36 | C inlet CWT
| 0.0059 | 0.0186 | [5 empty] | !Capacity ratio and COP ratio at | 5 | C oulet CHWT and | 38 | C inlet CWT
| 0.0023 | 0.1901 | [5 empty] | !Capacity ratio and COP ratio at | 5 | C oulet CHWT and | 40 | C inlet CWT
| 1 | 1.0009 | [5 empty] | !Capacity ratio and COP ratio at | 7 | C oulet CHWT and | 30 | C inlet CWT
| 0.979 | 0.9439 | [5 empty] | !Capacity ratio and COP ratio at | 7 | C oulet CHWT and | 32 | C inlet CWT
| 0.9581 | 0.8894 | [5 empty] | !Capacity ratio and COP ratio at | 7 | C oulet CHWT and | 34 | C inlet CWT
| 0.0011 | 0.1901 | [5 empty] | !Capacity ratio and COP ratio at | 7 | C oulet CHWT and | 36 | C inlet CWT
| 0.0606 | 0.102 | [5 empty] | !Capacity ratio and COP ratio at | 7 | C oulet CHWT and | 38 | C inlet CWT
| 2.8144 | 17.293 | [5 empty] | !Capacity ratio and COP ratio at | 7 | C oulet CHWT and | 40 | C inlet CWT
| 0.0011 | 0.1901 | [5 empty] | !Capacity ratio and COP ratio at | 8 | C oulet CHWT and | 30 | C inlet CWT
| 0.0011 | 0.1901 | [5 empty] | !Capacity ratio and COP ratio at | 8 | C oulet CHWT and | 32 | C inlet CWT
| 0.0011 | 0.1901 | [5 empty] | !Capacity ratio and COP ratio at | 8 | C oulet CHWT and | 34 | C inlet CWT
| 0.0011 | 0.1901 | [5 empty] | !Capacity ratio and COP ratio at | 8 | C oulet CHWT and | 36 | C inlet CWT
| 0.0011 | 0.1901 | [5 empty] | !Capacity ratio and COP ratio at | 8 | C oulet CHWT and | 38 | C inlet CWT
| 0.0011 | 0.1901 | [5 empty] | !Capacity ratio and COP ratio at | 8 | C oulet CHWT and | 40 | C inlet CWT
| 1.0702 | 1.0535 | [5 empty] | !Capacity ratio and COP ratio at | 9 | C oulet CHWT and | 30 | C inlet CWT
| 1.0485 | 0.9953 | [5 empty] | !Capacity ratio and COP ratio at | 9 | C oulet CHWT and | 32 | C inlet CWT
| 1.0267 | 0.9394 | [5 empty] | !Capacity ratio and COP ratio at | 9 | C oulet CHWT and | 34 | C inlet CWT
| 0.0606 | 1.9391 | [5 empty] | !Capacity ratio and COP ratio at | 9 | C oulet CHWT and | 36 | C inlet CWT
| 0.0071 | 0.2281 | [5 empty] | !Capacity ratio and COP ratio at | 9 | C oulet CHWT and | 38 | C inlet CWT
| 0.0737 | 1.9645 | [5 empty] | !Capacity ratio and COP ratio at | 9 | C oulet CHWT and | 40 | C inlet CWT
Format: mit Punkt
| 5 | 7 | 8 | 9 |  |  |  | !Chilled water leaving temperature (C)
| 30 | 32 | 34 | 36 | 38 | 40 |  | !Cooling water inlet temperature (C)
| 0.9326 | 0.9478 | [5 empty] | !Capacity ratio and COP ratio at | 5 | C oulet CHWT and | 30 | C inlet CWT
| 0.9125 | 0.8922 | [5 empty] | !Capacity ratio and COP ratio at | 5 | C oulet CHWT and | 32 | C inlet CWT
| 0.8915 | 0.8377 | [5 empty] | !Capacity ratio and COP ratio at | 5 | C oulet CHWT and | 34 | C inlet CWT
| 0.0011 | 0.095 | [5 empty] | !Capacity ratio and COP ratio at | 5 | C oulet CHWT and | 36 | C inlet CWT
| 0.0059 | 0.0186 | [5 empty] | !Capacity ratio and COP ratio at | 5 | C oulet CHWT and | 38 | C inlet CWT
| 0.0023 | 0.1901 | [5 empty] | !Capacity ratio and COP ratio at | 5 | C oulet CHWT and | 40 | C inlet CWT
| 1 | 1.0009 | [5 empty] | !Capacity ratio and COP ratio at | 7 | C oulet CHWT and | 30 | C inlet CWT
| 0.979 | 0.9439 | [5 empty] | !Capacity ratio and COP ratio at | 7 | C oulet CHWT and | 32 | C inlet CWT
| 0.9581 | 0.8894 | [5 empty] | !Capacity ratio and COP ratio at | 7 | C oulet CHWT and | 34 | C inlet CWT
| 0.0011 | 0.1901 | [5 empty] | !Capacity ratio and COP ratio at | 7 | C oulet CHWT and | 36 | C inlet CWT
| 0.0606 | 0.102 | [5 empty] | !Capacity ratio and COP ratio at | 7 | C oulet CHWT and | 38 | C inlet CWT
| 2.8144 | 17.293 | [5 empty] | !Capacity ratio and COP ratio at | 7 | C oulet CHWT and | 40 | C inlet CWT
| 0.0011 | 0.1901 | [5 empty] | !Capacity ratio and COP ratio at | 8 | C oulet CHWT and | 30 | C inlet CWT
| 0.0011 | 0.1901 | [5 empty] | !Capacity ratio and COP ratio at | 8 | C oulet CHWT and | 32 | C inlet CWT
| 0.0011 | 0.1901 | [5 empty] | !Capacity ratio and COP ratio at | 8 | C oulet CHWT and | 34 | C inlet CWT
| 0.0011 | 0.1901 | [5 empty] | !Capacity ratio and COP ratio at | 8 | C oulet CHWT and | 36 | C inlet CWT
| 0.0011 | 0.1901 | [5 empty] | !Capacity ratio and COP ratio at | 8 | C oulet CHWT and | 38 | C inlet CWT
| 0.0011 | 0.1901 | [5 empty] | !Capacity ratio and COP ratio at | 8 | C oulet CHWT and | 40 | C inlet CWT
| 1.0702 | 1.0535 | [5 empty] | !Capacity ratio and COP ratio at | 9 | C oulet CHWT and | 30 | C inlet CWT
| 1.0485 | 0.9953 | [5 empty] | !Capacity ratio and COP ratio at | 9 | C oulet CHWT and | 32 | C inlet CWT
| 1.0267 | 0.9394 | [5 empty] | !Capacity ratio and COP ratio at | 9 | C oulet CHWT and | 34 | C inlet CWT
| 0.0606 | 1.9391 | [5 empty] | !Capacity ratio and COP ratio at | 9 | C oulet CHWT and | 36 | C inlet CWT
| 0.0071 | 0.2281 | [5 empty] | !Capacity ratio and COP ratio at | 9 | C oulet CHWT and | 38 | C inlet CWT
| 0.0737 | 1.9645 | [5 empty] | !Capacity ratio and COP ratio at | 9 | C oulet CHWT and | 40 | C inlet CWT

## Chiller Performance5_3 (hidden)
| Anlagenname |  | Temp. Kühlwasser VL
| Anlagentyp |  | 30 | 30 | 32 | 32 | 34 | 34
| Temp. KW VL | Temp. KW RL | Kältekap. [KW] | Leistungsaufn. [kW] | Kältekap. [KW] | Leistungsaufn. [kW] | Kältekap. [KW] | Leistungsaufn. [kW]
| 5 | 0 | 783.72 | 157.2 | 766.84 | 163.4 | 749.16 | 170
| 6 | 0 | 2 | 2 | 2 | 2 | 2 | 2
| 7 | 0 | 840.32 | 159.6 | 822.74 | 165.7 | 805.16 | 172.1
| 8 | 0 | 1 | 1 | 1 | 1 | 1 | 1
| 9 | 0 | 899.39 | 162.3 | 881.11 | 168.3 | 862.83 | 174.6
| Nenndaten: | Temp. Kühlwasser VL: |  | 30 |  | Kältekap. [KW] | 840.32 | Kältekap. [kJ/hr] | 3025152 |  | COP: | 5.26
|  | Temp. KW VL: |  | 7 |  | Leistungsaufn. [kW] | 159.6 | Leistungsaufn. [kJ/hr] | 574560
| in kJ/hr |  | Capacity | Pel | Capacity | Pel | Capacity | Pel
| Temp. KW VL | Temp. KW RL | Kältekap. [kJ/hr] | Leistungsaufn. [kJ/hr] | Kältekap. [kJ/hr] | Leistungsaufn. [kJ/hr] | Kältekap. [kJ/hr] | Leistungsaufn. [kJ/hr]
| 5 | 0 | 2821392 | 565920 | 2760624 | 588240 | 2696976 | 612000
| 6 | 0 | 7200 | 7200 | 7200 | 7200 | 7200 | 7200
| 7 | 0 | 3025152 | 574560 | 2961864 | 596520 | 2898576 | 619560
| 8 | 0 | 3600 | 3600 | 3600 | 3600 | 3600 | 3600
| 9 | 0 | 3237804 | 584280 | 3171996 | 605880 | 3106188 | 628560
EER
| 5 | 0 | 4.9855 |  | 4.693 |  | 4.4068
| 6 | 0 | 1 |  | 1 |  | 1
| 7 | 0 | 5.2652 |  | 4.9652 |  | 4.6784
| 8 | 0 | 1 |  | 1 |  | 1
| 9 | 0 | 5.5415 |  | 5.2354 |  | 4.9418
|  |  | capacity ratio | COP ratio | capacity ratio | COP ratio | capacity ratio | COP ratio
| 5 | 0 | 0.93264 | 0.94781 | 0.91256 | 0.89221 | 0.89152 | 0.8378
| 6 | 0 | 0.00238 | 0.19011 | 0.00238 | 0.19011 | 0.00238 | 0.19011
| 7 | 0 | 1 | 1.001 | 0.97908 | 0.94396 | 0.95816 | 0.88944
| 8 | 0 | 0.00119 | 0.19011 | 0.00119 | 0.19011 | 0.00119 | 0.19011
| 9 | 0 | 1.0703 | 1.0535 | 1.0485 | 0.99531 | 1.0268 | 0.9395
Datei für Type 666
| 5 | 6 | 7 | 8 | 9 |  |  | !Chilled water leaving temperature (C)
| 30 | 32 | 34 |  |  |  |  | !Cooling water inlet temperature (C)
| 0.9326 | 0.9478 | [5 empty] | !Capacity ratio and COP ratio at | 5 | C oulet CHWT and | 30 | C inlet CWT
| 0.9125 | 0.8922 | [5 empty] | !Capacity ratio and COP ratio at | 5 | C oulet CHWT and | 32 | C inlet CWT
| 0.8915 | 0.8377 | [5 empty] | !Capacity ratio and COP ratio at | 5 | C oulet CHWT and | 34 | C inlet CWT
| 0.0023 | 0.1901 | [5 empty] | !Capacity ratio and COP ratio at | 6 | C oulet CHWT and | 30 | C inlet CWT
| 0.0023 | 0.1901 | [5 empty] | !Capacity ratio and COP ratio at | 6 | C oulet CHWT and | 32 | C inlet CWT
| 0.0023 | 0.1901 | [5 empty] | !Capacity ratio and COP ratio at | 6 | C oulet CHWT and | 34 | C inlet CWT
| 1 | 1.0009 | [5 empty] | !Capacity ratio and COP ratio at | 7 | C oulet CHWT and | 30 | C inlet CWT
| 0.979 | 0.9439 | [5 empty] | !Capacity ratio and COP ratio at | 7 | C oulet CHWT and | 32 | C inlet CWT
| 0.9581 | 0.8894 | [5 empty] | !Capacity ratio and COP ratio at | 7 | C oulet CHWT and | 34 | C inlet CWT
| 0.0011 | 0.1901 | [5 empty] | !Capacity ratio and COP ratio at | 8 | C oulet CHWT and | 30 | C inlet CWT
| 0.0011 | 0.1901 | [5 empty] | !Capacity ratio and COP ratio at | 8 | C oulet CHWT and | 32 | C inlet CWT
| 0.0011 | 0.1901 | [5 empty] | !Capacity ratio and COP ratio at | 8 | C oulet CHWT and | 34 | C inlet CWT
| 1.0702 | 1.0535 | [5 empty] | !Capacity ratio and COP ratio at | 9 | C oulet CHWT and | 30 | C inlet CWT
| 1.0485 | 0.9953 | [5 empty] | !Capacity ratio and COP ratio at | 9 | C oulet CHWT and | 32 | C inlet CWT
| 1.0267 | 0.9394 | [5 empty] | !Capacity ratio and COP ratio at | 9 | C oulet CHWT and | 34 | C inlet CWT
Format: mit Punkt
| 5 | 6 | 7 | 8 | 9 |  |  | !Chilled water leaving temperature (C)
| 30 | 32 | 34 |  |  |  |  | !Cooling water inlet temperature (C)
| 0.9326 | 0.9478 | [5 empty] | !Capacity ratio and COP ratio at | 5 | C oulet CHWT and | 30 | C inlet CWT
| 0.9125 | 0.8922 | [5 empty] | !Capacity ratio and COP ratio at | 5 | C oulet CHWT and | 32 | C inlet CWT
| 0.8915 | 0.8377 | [5 empty] | !Capacity ratio and COP ratio at | 5 | C oulet CHWT and | 34 | C inlet CWT
| 0.0023 | 0.1901 | [5 empty] | !Capacity ratio and COP ratio at | 6 | C oulet CHWT and | 30 | C inlet CWT
| 0.0023 | 0.1901 | [5 empty] | !Capacity ratio and COP ratio at | 6 | C oulet CHWT and | 32 | C inlet CWT
| 0.0023 | 0.1901 | [5 empty] | !Capacity ratio and COP ratio at | 6 | C oulet CHWT and | 34 | C inlet CWT
| 1 | 1.0009 | [5 empty] | !Capacity ratio and COP ratio at | 7 | C oulet CHWT and | 30 | C inlet CWT
| 0.979 | 0.9439 | [5 empty] | !Capacity ratio and COP ratio at | 7 | C oulet CHWT and | 32 | C inlet CWT
| 0.9581 | 0.8894 | [5 empty] | !Capacity ratio and COP ratio at | 7 | C oulet CHWT and | 34 | C inlet CWT
| 0.0011 | 0.1901 | [5 empty] | !Capacity ratio and COP ratio at | 8 | C oulet CHWT and | 30 | C inlet CWT
| 0.0011 | 0.1901 | [5 empty] | !Capacity ratio and COP ratio at | 8 | C oulet CHWT and | 32 | C inlet CWT
| 0.0011 | 0.1901 | [5 empty] | !Capacity ratio and COP ratio at | 8 | C oulet CHWT and | 34 | C inlet CWT
| 1.0702 | 1.0535 | [5 empty] | !Capacity ratio and COP ratio at | 9 | C oulet CHWT and | 30 | C inlet CWT
| 1.0485 | 0.9953 | [5 empty] | !Capacity ratio and COP ratio at | 9 | C oulet CHWT and | 32 | C inlet CWT
| 1.0267 | 0.9394 | [5 empty] | !Capacity ratio and COP ratio at | 9 | C oulet CHWT and | 34 | C inlet CWT

## Chiller Performance5_4 (hidden)
| Anlagenname |  | Temp. Kühlwasser VL
| Anlagentyp |  | 30 | 30 | 32 | 32 | 34 | 34 | 36 | 36
| Temp. KW VL | Temp. KW RL | Kältekap. [KW] | Leistungsaufn. [kW] | Kältekap. [KW] | Leistungsaufn. [kW] | Kältekap. [KW] | Leistungsaufn. [kW] | Kältekap. [KW] | Leistungsaufn. [kW]
| 5 | 0 | 783.72 | 157.2 | 766.84 | 163.4 | 749.16 | 170 | 1 | 2
| 6 | 0 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2
| 7 | 0 | 840.32 | 159.6 | 822.74 | 165.7 | 805.16 | 172.1 | 1 | 1
| 8 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| 9 | 0 | 899.39 | 162.3 | 881.11 | 168.3 | 862.83 | 174.6 | 51 | 5
| Nenndaten: | Temp. Kühlwasser VL: |  | 30 |  | Kältekap. [KW] | 840.32 | Kältekap. [kJ/hr] | 3025152 |  | COP: | 5.26
|  | Temp. KW VL: |  | 7 |  | Leistungsaufn. [kW] | 159.6 | Leistungsaufn. [kJ/hr] | 574560
| in kJ/hr |  | Capacity | Pel | Capacity | Pel | Capacity | Pel | Capacity | Pel
| Temp. KW VL | Temp. KW RL | Kältekap. [kJ/hr] | Leistungsaufn. [kJ/hr] | Kältekap. [kJ/hr] | Leistungsaufn. [kJ/hr] | Kältekap. [kJ/hr] | Leistungsaufn. [kJ/hr] | Kältekap. [kJ/hr] | Leistungsaufn. [kJ/hr]
| 5 | 0 | 2821392 | 565920 | 2760624 | 588240 | 2696976 | 612000 | 3600 | 7200
| 6 | 0 | 7200 | 7200 | 7200 | 7200 | 7200 | 7200 | 7200 | 7200
| 7 | 0 | 3025152 | 574560 | 2961864 | 596520 | 2898576 | 619560 | 3600 | 3600
| 8 | 0 | 3600 | 3600 | 3600 | 3600 | 3600 | 3600 | 3600 | 3600
| 9 | 0 | 3237804 | 584280 | 3171996 | 605880 | 3106188 | 628560 | 183600 | 18000
EER
| 5 | 0 | 4.9855 |  | 4.693 |  | 4.4068 |  | 0.5
| 6 | 0 | 1 |  | 1 |  | 1 |  | 1
| 7 | 0 | 5.2652 |  | 4.9652 |  | 4.6784 |  | 1
| 8 | 0 | 1 |  | 1 |  | 1 |  | 1
| 9 | 0 | 5.5415 |  | 5.2354 |  | 4.9418 |  | 10.2
|  |  | capacity ratio | COP ratio | capacity ratio | COP ratio | capacity ratio | COP ratio | capacity ratio | COP ratio
| 5 | 0 | 0.93264 | 0.94781 | 0.91256 | 0.89221 | 0.89152 | 0.8378 | 0.00119 | 0.095057
| 6 | 0 | 0.00238 | 0.19011 | 0.00238 | 0.19011 | 0.00238 | 0.19011 | 0.00238 | 0.19011
| 7 | 0 | 1 | 1.001 | 0.97908 | 0.94396 | 0.95816 | 0.88944 | 0.00119 | 0.19011
| 8 | 0 | 0.00119 | 0.19011 | 0.00119 | 0.19011 | 0.00119 | 0.19011 | 0.00119 | 0.19011
| 9 | 0 | 1.0703 | 1.0535 | 1.0485 | 0.99531 | 1.0268 | 0.9395 | 0.060691 | 1.9392
Datei für Type 666
| 5 | 6 | 7 | 8 | 9 |  |  | !Chilled water leaving temperature (C)
| 30 | 32 | 34 | 36 |  |  |  | !Cooling water inlet temperature (C)
| 0.9326 | 0.9478 | [5 empty] | !Capacity ratio and COP ratio at | 5 | C oulet CHWT and | 30 | C inlet CWT
| 0.9125 | 0.8922 | [5 empty] | !Capacity ratio and COP ratio at | 5 | C oulet CHWT and | 32 | C inlet CWT
| 0.8915 | 0.8377 | [5 empty] | !Capacity ratio and COP ratio at | 5 | C oulet CHWT and | 34 | C inlet CWT
| 0.0011 | 0.095 | [5 empty] | !Capacity ratio and COP ratio at | 5 | C oulet CHWT and | 36 | C inlet CWT
| 0.0023 | 0.1901 | [5 empty] | !Capacity ratio and COP ratio at | 6 | C oulet CHWT and | 30 | C inlet CWT
| 0.0023 | 0.1901 | [5 empty] | !Capacity ratio and COP ratio at | 6 | C oulet CHWT and | 32 | C inlet CWT
| 0.0023 | 0.1901 | [5 empty] | !Capacity ratio and COP ratio at | 6 | C oulet CHWT and | 34 | C inlet CWT
| 0.0023 | 0.1901 | [5 empty] | !Capacity ratio and COP ratio at | 6 | C oulet CHWT and | 36 | C inlet CWT
| 1 | 1.0009 | [5 empty] | !Capacity ratio and COP ratio at | 7 | C oulet CHWT and | 30 | C inlet CWT
| 0.979 | 0.9439 | [5 empty] | !Capacity ratio and COP ratio at | 7 | C oulet CHWT and | 32 | C inlet CWT
| 0.9581 | 0.8894 | [5 empty] | !Capacity ratio and COP ratio at | 7 | C oulet CHWT and | 34 | C inlet CWT
| 0.0011 | 0.1901 | [5 empty] | !Capacity ratio and COP ratio at | 7 | C oulet CHWT and | 36 | C inlet CWT
| 0.0011 | 0.1901 | [5 empty] | !Capacity ratio and COP ratio at | 8 | C oulet CHWT and | 30 | C inlet CWT
| 0.0011 | 0.1901 | [5 empty] | !Capacity ratio and COP ratio at | 8 | C oulet CHWT and | 32 | C inlet CWT
| 0.0011 | 0.1901 | [5 empty] | !Capacity ratio and COP ratio at | 8 | C oulet CHWT and | 34 | C inlet CWT
| 0.0011 | 0.1901 | [5 empty] | !Capacity ratio and COP ratio at | 8 | C oulet CHWT and | 36 | C inlet CWT
| 1.0702 | 1.0535 | [5 empty] | !Capacity ratio and COP ratio at | 9 | C oulet CHWT and | 30 | C inlet CWT
| 1.0485 | 0.9953 | [5 empty] | !Capacity ratio and COP ratio at | 9 | C oulet CHWT and | 32 | C inlet CWT
| 1.0267 | 0.9394 | [5 empty] | !Capacity ratio and COP ratio at | 9 | C oulet CHWT and | 34 | C inlet CWT
| 0.0606 | 1.9391 | [5 empty] | !Capacity ratio and COP ratio at | 9 | C oulet CHWT and | 36 | C inlet CWT
Format: mit Punkt
| 5 | 6 | 7 | 8 | 9 |  |  | !Chilled water leaving temperature (C)
| 30 | 32 | 34 | 36 |  |  |  | !Cooling water inlet temperature (C)
| 0.9326 | 0.9478 | [5 empty] | !Capacity ratio and COP ratio at | 5 | C oulet CHWT and | 30 | C inlet CWT
| 0.9125 | 0.8922 | [5 empty] | !Capacity ratio and COP ratio at | 5 | C oulet CHWT and | 32 | C inlet CWT
| 0.8915 | 0.8377 | [5 empty] | !Capacity ratio and COP ratio at | 5 | C oulet CHWT and | 34 | C inlet CWT
| 0.0011 | 0.095 | [5 empty] | !Capacity ratio and COP ratio at | 5 | C oulet CHWT and | 36 | C inlet CWT
| 0.0023 | 0.1901 | [5 empty] | !Capacity ratio and COP ratio at | 6 | C oulet CHWT and | 30 | C inlet CWT
| 0.0023 | 0.1901 | [5 empty] | !Capacity ratio and COP ratio at | 6 | C oulet CHWT and | 32 | C inlet CWT
| 0.0023 | 0.1901 | [5 empty] | !Capacity ratio and COP ratio at | 6 | C oulet CHWT and | 34 | C inlet CWT
| 0.0023 | 0.1901 | [5 empty] | !Capacity ratio and COP ratio at | 6 | C oulet CHWT and | 36 | C inlet CWT
| 1 | 1.0009 | [5 empty] | !Capacity ratio and COP ratio at | 7 | C oulet CHWT and | 30 | C inlet CWT
| 0.979 | 0.9439 | [5 empty] | !Capacity ratio and COP ratio at | 7 | C oulet CHWT and | 32 | C inlet CWT
| 0.9581 | 0.8894 | [5 empty] | !Capacity ratio and COP ratio at | 7 | C oulet CHWT and | 34 | C inlet CWT
| 0.0011 | 0.1901 | [5 empty] | !Capacity ratio and COP ratio at | 7 | C oulet CHWT and | 36 | C inlet CWT
| 0.0011 | 0.1901 | [5 empty] | !Capacity ratio and COP ratio at | 8 | C oulet CHWT and | 30 | C inlet CWT
| 0.0011 | 0.1901 | [5 empty] | !Capacity ratio and COP ratio at | 8 | C oulet CHWT and | 32 | C inlet CWT
| 0.0011 | 0.1901 | [5 empty] | !Capacity ratio and COP ratio at | 8 | C oulet CHWT and | 34 | C inlet CWT
| 0.0011 | 0.1901 | [5 empty] | !Capacity ratio and COP ratio at | 8 | C oulet CHWT and | 36 | C inlet CWT
| 1.0702 | 1.0535 | [5 empty] | !Capacity ratio and COP ratio at | 9 | C oulet CHWT and | 30 | C inlet CWT
| 1.0485 | 0.9953 | [5 empty] | !Capacity ratio and COP ratio at | 9 | C oulet CHWT and | 32 | C inlet CWT
| 1.0267 | 0.9394 | [5 empty] | !Capacity ratio and COP ratio at | 9 | C oulet CHWT and | 34 | C inlet CWT
| 0.0606 | 1.9391 | [5 empty] | !Capacity ratio and COP ratio at | 9 | C oulet CHWT and | 36 | C inlet CWT

## Chiller Performance5_5 (hidden)
| Anlagenname |  | Temp. Kühlwasser VL
| Anlagentyp |  | 30 | 30 | 32 | 32 | 34 | 34 | 36 | 36 | 38 | 38
| Temp. KW VL | Temp. KW RL | Kältekap. [KW] | Leistungsaufn. [kW] | Kältekap. [KW] | Leistungsaufn. [kW] | Kältekap. [KW] | Leistungsaufn. [kW] | Kältekap. [KW] | Leistungsaufn. [kW] | Kältekap. [KW] | Leistungsaufn. [kW]
| 5 | 0 | 783.72 | 157.2 | 766.84 | 163.4 | 749.16 | 170 | 1 | 2 | 5 | 51
| 6 | 0 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2
| 7 | 0 | 840.32 | 159.6 | 822.74 | 165.7 | 805.16 | 172.1 | 1 | 1 | 51 | 95
| 8 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| 9 | 0 | 899.39 | 162.3 | 881.11 | 168.3 | 862.83 | 174.6 | 51 | 5 | 6 | 5
| Nenndaten: | Temp. Kühlwasser VL: |  | 30 |  | Kältekap. [KW] | 840.32 | Kältekap. [kJ/hr] | 3025152 |  | COP: | 5.26
|  | Temp. KW VL: |  | 7 |  | Leistungsaufn. [kW] | 159.6 | Leistungsaufn. [kJ/hr] | 574560
| in kJ/hr |  | Capacity | Pel | Capacity | Pel | Capacity | Pel | Capacity | Pel | Capacity | Pel
| Temp. KW VL | Temp. KW RL | Kältekap. [kJ/hr] | Leistungsaufn. [kJ/hr] | Kältekap. [kJ/hr] | Leistungsaufn. [kJ/hr] | Kältekap. [kJ/hr] | Leistungsaufn. [kJ/hr] | Kältekap. [kJ/hr] | Leistungsaufn. [kJ/hr] | Kältekap. [kJ/hr] | Leistungsaufn. [kJ/hr]
| 5 | 0 | 2821392 | 565920 | 2760624 | 588240 | 2696976 | 612000 | 3600 | 7200 | 18000 | 183600
| 6 | 0 | 7200 | 7200 | 7200 | 7200 | 7200 | 7200 | 7200 | 7200 | 7200 | 7200
| 7 | 0 | 3025152 | 574560 | 2961864 | 596520 | 2898576 | 619560 | 3600 | 3600 | 183600 | 342000
| 8 | 0 | 3600 | 3600 | 3600 | 3600 | 3600 | 3600 | 3600 | 3600 | 3600 | 3600
| 9 | 0 | 3237804 | 584280 | 3171996 | 605880 | 3106188 | 628560 | 183600 | 18000 | 21600 | 18000
EER
| 5 | 0 | 4.9855 |  | 4.693 |  | 4.4068 |  | 0.5 |  | 0.098039
| 6 | 0 | 1 |  | 1 |  | 1 |  | 1 |  | 1
| 7 | 0 | 5.2652 |  | 4.9652 |  | 4.6784 |  | 1 |  | 0.53684
| 8 | 0 | 1 |  | 1 |  | 1 |  | 1 |  | 1
| 9 | 0 | 5.5415 |  | 5.2354 |  | 4.9418 |  | 10.2 |  | 1.2
|  |  | capacity ratio | COP ratio | capacity ratio | COP ratio | capacity ratio | COP ratio | capacity ratio | COP ratio | capacity ratio | COP ratio
| 5 | 0 | 0.93264 | 0.94781 | 0.91256 | 0.89221 | 0.89152 | 0.8378 | 0.00119 | 0.095057 | 0.0059501 | 0.018639
| 6 | 0 | 0.00238 | 0.19011 | 0.00238 | 0.19011 | 0.00238 | 0.19011 | 0.00238 | 0.19011 | 0.00238 | 0.19011
| 7 | 0 | 1 | 1.001 | 0.97908 | 0.94396 | 0.95816 | 0.88944 | 0.00119 | 0.19011 | 0.060691 | 0.10206
| 8 | 0 | 0.00119 | 0.19011 | 0.00119 | 0.19011 | 0.00119 | 0.19011 | 0.00119 | 0.19011 | 0.00119 | 0.19011
| 9 | 0 | 1.0703 | 1.0535 | 1.0485 | 0.99531 | 1.0268 | 0.9395 | 0.060691 | 1.9392 | 0.0071401 | 0.22814
Datei für Type 666
| 5 | 6 | 7 | 8 | 9 |  |  | !Chilled water leaving temperature (C)
| 30 | 32 | 34 | 36 | 38 |  |  | !Cooling water inlet temperature (C)
| 0.9326 | 0.9478 | [5 empty] | !Capacity ratio and COP ratio at | 5 | C oulet CHWT and | 30 | C inlet CWT
| 0.9125 | 0.8922 | [5 empty] | !Capacity ratio and COP ratio at | 5 | C oulet CHWT and | 32 | C inlet CWT
| 0.8915 | 0.8377 | [5 empty] | !Capacity ratio and COP ratio at | 5 | C oulet CHWT and | 34 | C inlet CWT
| 0.0011 | 0.095 | [5 empty] | !Capacity ratio and COP ratio at | 5 | C oulet CHWT and | 36 | C inlet CWT
| 0.0059 | 0.0186 | [5 empty] | !Capacity ratio and COP ratio at | 5 | C oulet CHWT and | 38 | C inlet CWT
| 0.0023 | 0.1901 | [5 empty] | !Capacity ratio and COP ratio at | 6 | C oulet CHWT and | 30 | C inlet CWT
| 0.0023 | 0.1901 | [5 empty] | !Capacity ratio and COP ratio at | 6 | C oulet CHWT and | 32 | C inlet CWT
| 0.0023 | 0.1901 | [5 empty] | !Capacity ratio and COP ratio at | 6 | C oulet CHWT and | 34 | C inlet CWT
| 0.0023 | 0.1901 | [5 empty] | !Capacity ratio and COP ratio at | 6 | C oulet CHWT and | 36 | C inlet CWT
| 0.0023 | 0.1901 | [5 empty] | !Capacity ratio and COP ratio at | 6 | C oulet CHWT and | 38 | C inlet CWT
| 1 | 1.0009 | [5 empty] | !Capacity ratio and COP ratio at | 7 | C oulet CHWT and | 30 | C inlet CWT
| 0.979 | 0.9439 | [5 empty] | !Capacity ratio and COP ratio at | 7 | C oulet CHWT and | 32 | C inlet CWT
| 0.9581 | 0.8894 | [5 empty] | !Capacity ratio and COP ratio at | 7 | C oulet CHWT and | 34 | C inlet CWT
| 0.0011 | 0.1901 | [5 empty] | !Capacity ratio and COP ratio at | 7 | C oulet CHWT and | 36 | C inlet CWT
| 0.0606 | 0.102 | [5 empty] | !Capacity ratio and COP ratio at | 7 | C oulet CHWT and | 38 | C inlet CWT
| 0.0011 | 0.1901 | [5 empty] | !Capacity ratio and COP ratio at | 8 | C oulet CHWT and | 30 | C inlet CWT
| 0.0011 | 0.1901 | [5 empty] | !Capacity ratio and COP ratio at | 8 | C oulet CHWT and | 32 | C inlet CWT
| 0.0011 | 0.1901 | [5 empty] | !Capacity ratio and COP ratio at | 8 | C oulet CHWT and | 34 | C inlet CWT
| 0.0011 | 0.1901 | [5 empty] | !Capacity ratio and COP ratio at | 8 | C oulet CHWT and | 36 | C inlet CWT
| 0.0011 | 0.1901 | [5 empty] | !Capacity ratio and COP ratio at | 8 | C oulet CHWT and | 38 | C inlet CWT
| 1.0702 | 1.0535 | [5 empty] | !Capacity ratio and COP ratio at | 9 | C oulet CHWT and | 30 | C inlet CWT
| 1.0485 | 0.9953 | [5 empty] | !Capacity ratio and COP ratio at | 9 | C oulet CHWT and | 32 | C inlet CWT
| 1.0267 | 0.9394 | [5 empty] | !Capacity ratio and COP ratio at | 9 | C oulet CHWT and | 34 | C inlet CWT
| 0.0606 | 1.9391 | [5 empty] | !Capacity ratio and COP ratio at | 9 | C oulet CHWT and | 36 | C inlet CWT
| 0.0071 | 0.2281 | [5 empty] | !Capacity ratio and COP ratio at | 9 | C oulet CHWT and | 38 | C inlet CWT
Format: mit Punkt
| 5 | 6 | 7 | 8 | 9 |  |  | !Chilled water leaving temperature (C)
| 30 | 32 | 34 | 36 | 38 |  |  | !Cooling water inlet temperature (C)
| 0.9326 | 0.9478 | [5 empty] | !Capacity ratio and COP ratio at | 5 | C oulet CHWT and | 30 | C inlet CWT
| 0.9125 | 0.8922 | [5 empty] | !Capacity ratio and COP ratio at | 5 | C oulet CHWT and | 32 | C inlet CWT
| 0.8915 | 0.8377 | [5 empty] | !Capacity ratio and COP ratio at | 5 | C oulet CHWT and | 34 | C inlet CWT
| 0.0011 | 0.095 | [5 empty] | !Capacity ratio and COP ratio at | 5 | C oulet CHWT and | 36 | C inlet CWT
| 0.0059 | 0.0186 | [5 empty] | !Capacity ratio and COP ratio at | 5 | C oulet CHWT and | 38 | C inlet CWT
| 0.0023 | 0.1901 | [5 empty] | !Capacity ratio and COP ratio at | 6 | C oulet CHWT and | 30 | C inlet CWT
| 0.0023 | 0.1901 | [5 empty] | !Capacity ratio and COP ratio at | 6 | C oulet CHWT and | 32 | C inlet CWT
| 0.0023 | 0.1901 | [5 empty] | !Capacity ratio and COP ratio at | 6 | C oulet CHWT and | 34 | C inlet CWT
| 0.0023 | 0.1901 | [5 empty] | !Capacity ratio and COP ratio at | 6 | C oulet CHWT and | 36 | C inlet CWT
| 0.0023 | 0.1901 | [5 empty] | !Capacity ratio and COP ratio at | 6 | C oulet CHWT and | 38 | C inlet CWT
| 1 | 1.0009 | [5 empty] | !Capacity ratio and COP ratio at | 7 | C oulet CHWT and | 30 | C inlet CWT
| 0.979 | 0.9439 | [5 empty] | !Capacity ratio and COP ratio at | 7 | C oulet CHWT and | 32 | C inlet CWT
| 0.9581 | 0.8894 | [5 empty] | !Capacity ratio and COP ratio at | 7 | C oulet CHWT and | 34 | C inlet CWT
| 0.0011 | 0.1901 | [5 empty] | !Capacity ratio and COP ratio at | 7 | C oulet CHWT and | 36 | C inlet CWT
| 0.0606 | 0.102 | [5 empty] | !Capacity ratio and COP ratio at | 7 | C oulet CHWT and | 38 | C inlet CWT
| 0.0011 | 0.1901 | [5 empty] | !Capacity ratio and COP ratio at | 8 | C oulet CHWT and | 30 | C inlet CWT
| 0.0011 | 0.1901 | [5 empty] | !Capacity ratio and COP ratio at | 8 | C oulet CHWT and | 32 | C inlet CWT
| 0.0011 | 0.1901 | [5 empty] | !Capacity ratio and COP ratio at | 8 | C oulet CHWT and | 34 | C inlet CWT
| 0.0011 | 0.1901 | [5 empty] | !Capacity ratio and COP ratio at | 8 | C oulet CHWT and | 36 | C inlet CWT
| 0.0011 | 0.1901 | [5 empty] | !Capacity ratio and COP ratio at | 8 | C oulet CHWT and | 38 | C inlet CWT
| 1.0702 | 1.0535 | [5 empty] | !Capacity ratio and COP ratio at | 9 | C oulet CHWT and | 30 | C inlet CWT
| 1.0485 | 0.9953 | [5 empty] | !Capacity ratio and COP ratio at | 9 | C oulet CHWT and | 32 | C inlet CWT
| 1.0267 | 0.9394 | [5 empty] | !Capacity ratio and COP ratio at | 9 | C oulet CHWT and | 34 | C inlet CWT
| 0.0606 | 1.9391 | [5 empty] | !Capacity ratio and COP ratio at | 9 | C oulet CHWT and | 36 | C inlet CWT
| 0.0071 | 0.2281 | [5 empty] | !Capacity ratio and COP ratio at | 9 | C oulet CHWT and | 38 | C inlet CWT

## Chiller Performance5_6 (hidden)
| Anlagenname |  | Temp. Kühlwasser VL
| Anlagentyp |  | 30 | 30 | 32 | 32 | 34 | 34 | 36 | 36 | 38 | 38 | 40 | 40
| Temp. KW VL | Temp. KW RL | Kältekap. [KW] | Leistungsaufn. [kW] | Kältekap. [KW] | Leistungsaufn. [kW] | Kältekap. [KW] | Leistungsaufn. [kW] | Kältekap. [KW] | Leistungsaufn. [kW] | Kältekap. [KW] | Leistungsaufn. [kW] | Kältekap. [KW] | Leistungsaufn. [kW]
| 5 | 0 | 783.72 | 157.2 | 766.84 | 163.4 | 749.16 | 170 | 1 | 2 | 5 | 51 | 2 | 2
| 6 | 0 | 780 | 150 | 756 | 125 | 789 | 178 | 1 | 2 | 2 | 2 | 2 | 2
| 7 | 0 | 840.32 | 159.6 | 822.74 | 165.7 | 805.16 | 172.1 | 1 | 1 | 51 | 95 | 23 | 26
| 8 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| 9 | 0 | 899.39 | 162.3 | 881.11 | 168.3 | 862.83 | 174.6 | 51 | 5 | 6 | 5 | 62 | 6
| Nenndaten: | Temp. Kühlwasser VL: |  | 30 |  | Kältekap. [KW] | 840.32 | Kältekap. [kJ/hr] | 3025152 |  | COP: | 5.26
|  | Temp. KW VL: |  | 7 |  | Leistungsaufn. [kW] | 159.6 | Leistungsaufn. [kJ/hr] | 574560
| in kJ/hr |  | Capacity | Pel | Capacity | Pel | Capacity | Pel | Capacity | Pel | Capacity | Pel | Capacity | Pel
| Temp. KW VL | Temp. KW RL | Kältekap. [kJ/hr] | Leistungsaufn. [kJ/hr] | Kältekap. [kJ/hr] | Leistungsaufn. [kJ/hr] | Kältekap. [kJ/hr] | Leistungsaufn. [kJ/hr] | Kältekap. [kJ/hr] | Leistungsaufn. [kJ/hr] | Kältekap. [kJ/hr] | Leistungsaufn. [kJ/hr] | Kältekap. [kJ/hr] | Leistungsaufn. [kJ/hr]
| 5 | 0 | 2821392 | 565920 | 2760624 | 588240 | 2696976 | 612000 | 3600 | 7200 | 18000 | 183600 | 7200 | 7200
| 6 | 0 | 2808000 | 540000 | 2721600 | 450000 | 2840400 | 640800 | 3600 | 7200 | 7200 | 7200 | 7200 | 7200
| 7 | 0 | 3025152 | 574560 | 2961864 | 596520 | 2898576 | 619560 | 3600 | 3600 | 183600 | 342000 | 82800 | 93600
| 8 | 0 | 3600 | 3600 | 3600 | 3600 | 3600 | 3600 | 3600 | 3600 | 3600 | 3600 | 3600 | 3600
| 9 | 0 | 3237804 | 584280 | 3171996 | 605880 | 3106188 | 628560 | 183600 | 18000 | 21600 | 18000 | 223200 | 21600
EER
| 5 | 0 | 4.9855 |  | 4.693 |  | 4.4068 |  | 0.5 |  | 0.098039 |  | 1
| 6 | 0 | 5.2 |  | 6.048 |  | 4.4326 |  | 0.5 |  | 1 |  | 1
| 7 | 0 | 5.2652 |  | 4.9652 |  | 4.6784 |  | 1 |  | 0.53684 |  | 0.88462
| 8 | 0 | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1
| 9 | 0 | 5.5415 |  | 5.2354 |  | 4.9418 |  | 10.2 |  | 1.2 |  | 10.3333
|  |  | capacity ratio | COP ratio | capacity ratio | COP ratio | capacity ratio | COP ratio | capacity ratio | COP ratio | capacity ratio | COP ratio | capacity ratio | COP ratio
| 5 | 0 | 0.93264 | 0.94781 | 0.91256 | 0.89221 | 0.89152 | 0.8378 | 0.00119 | 0.095057 | 0.0059501 | 0.018639 | 0.00238 | 0.19011
| 6 | 0 | 0.92822 | 0.98859 | 0.89966 | 1.1498 | 0.93893 | 0.8427 | 0.00119 | 0.095057 | 0.00238 | 0.19011 | 0.00238 | 0.19011
| 7 | 0 | 1 | 1.001 | 0.97908 | 0.94396 | 0.95816 | 0.88944 | 0.00119 | 0.19011 | 0.060691 | 0.10206 | 0.027371 | 0.16818
| 8 | 0 | 0.00119 | 0.19011 | 0.00119 | 0.19011 | 0.00119 | 0.19011 | 0.00119 | 0.19011 | 0.00119 | 0.19011 | 0.00119 | 0.19011
| 9 | 0 | 1.0703 | 1.0535 | 1.0485 | 0.99531 | 1.0268 | 0.9395 | 0.060691 | 1.9392 | 0.0071401 | 0.22814 | 0.073781 | 1.9645
Datei für Type 666
| 5 | 6 | 7 | 8 | 9 |  |  | !Chilled water leaving temperature (C)
| 30 | 32 | 34 | 36 | 38 | 40 |  | !Cooling water inlet temperature (C)
| 0.9326 | 0.9478 | [5 empty] | !Capacity ratio and COP ratio at | 5 | C oulet CHWT and | 30 | C inlet CWT
| 0.9125 | 0.8922 | [5 empty] | !Capacity ratio and COP ratio at | 5 | C oulet CHWT and | 32 | C inlet CWT
| 0.8915 | 0.8377 | [5 empty] | !Capacity ratio and COP ratio at | 5 | C oulet CHWT and | 34 | C inlet CWT
| 0.0011 | 0.095 | [5 empty] | !Capacity ratio and COP ratio at | 5 | C oulet CHWT and | 36 | C inlet CWT
| 0.0059 | 0.0186 | [5 empty] | !Capacity ratio and COP ratio at | 5 | C oulet CHWT and | 38 | C inlet CWT
| 0.0023 | 0.1901 | [5 empty] | !Capacity ratio and COP ratio at | 5 | C oulet CHWT and | 40 | C inlet CWT
| 0.9282 | 0.9885 | [5 empty] | !Capacity ratio and COP ratio at | 6 | C oulet CHWT and | 30 | C inlet CWT
| 0.8996 | 1.1498 | [5 empty] | !Capacity ratio and COP ratio at | 6 | C oulet CHWT and | 32 | C inlet CWT
| 0.9389 | 0.8426 | [5 empty] | !Capacity ratio and COP ratio at | 6 | C oulet CHWT and | 34 | C inlet CWT
| 0.0011 | 0.095 | [5 empty] | !Capacity ratio and COP ratio at | 6 | C oulet CHWT and | 36 | C inlet CWT
| 0.0023 | 0.1901 | [5 empty] | !Capacity ratio and COP ratio at | 6 | C oulet CHWT and | 38 | C inlet CWT
| 0.0023 | 0.1901 | [5 empty] | !Capacity ratio and COP ratio at | 6 | C oulet CHWT and | 40 | C inlet CWT
| 1 | 1.0009 | [5 empty] | !Capacity ratio and COP ratio at | 7 | C oulet CHWT and | 30 | C inlet CWT
| 0.979 | 0.9439 | [5 empty] | !Capacity ratio and COP ratio at | 7 | C oulet CHWT and | 32 | C inlet CWT
| 0.9581 | 0.8894 | [5 empty] | !Capacity ratio and COP ratio at | 7 | C oulet CHWT and | 34 | C inlet CWT
| 0.0011 | 0.1901 | [5 empty] | !Capacity ratio and COP ratio at | 7 | C oulet CHWT and | 36 | C inlet CWT
| 0.0606 | 0.102 | [5 empty] | !Capacity ratio and COP ratio at | 7 | C oulet CHWT and | 38 | C inlet CWT
| 0.0273 | 0.1681 | [5 empty] | !Capacity ratio and COP ratio at | 7 | C oulet CHWT and | 40 | C inlet CWT
| 0.0011 | 0.1901 | [5 empty] | !Capacity ratio and COP ratio at | 8 | C oulet CHWT and | 30 | C inlet CWT
| 0.0011 | 0.1901 | [5 empty] | !Capacity ratio and COP ratio at | 8 | C oulet CHWT and | 32 | C inlet CWT
| 0.0011 | 0.1901 | [5 empty] | !Capacity ratio and COP ratio at | 8 | C oulet CHWT and | 34 | C inlet CWT
| 0.0011 | 0.1901 | [5 empty] | !Capacity ratio and COP ratio at | 8 | C oulet CHWT and | 36 | C inlet CWT
| 0.0011 | 0.1901 | [5 empty] | !Capacity ratio and COP ratio at | 8 | C oulet CHWT and | 38 | C inlet CWT
| 0.0011 | 0.1901 | [5 empty] | !Capacity ratio and COP ratio at | 8 | C oulet CHWT and | 40 | C inlet CWT
| 1.0702 | 1.0535 | [5 empty] | !Capacity ratio and COP ratio at | 9 | C oulet CHWT and | 30 | C inlet CWT
| 1.0485 | 0.9953 | [5 empty] | !Capacity ratio and COP ratio at | 9 | C oulet CHWT and | 32 | C inlet CWT
| 1.0267 | 0.9394 | [5 empty] | !Capacity ratio and COP ratio at | 9 | C oulet CHWT and | 34 | C inlet CWT
| 0.0606 | 1.9391 | [5 empty] | !Capacity ratio and COP ratio at | 9 | C oulet CHWT and | 36 | C inlet CWT
| 0.0071 | 0.2281 | [5 empty] | !Capacity ratio and COP ratio at | 9 | C oulet CHWT and | 38 | C inlet CWT
| 0.0737 | 1.9645 | [5 empty] | !Capacity ratio and COP ratio at | 9 | C oulet CHWT and | 40 | C inlet CWT
Format: mit Punkt
| 5 | 6 | 7 | 8 | 9 |  |  | !Chilled water leaving temperature (C)
| 30 | 32 | 34 | 36 | 38 | 40 |  | !Cooling water inlet temperature (C)
| 0.9326 | 0.9478 | [5 empty] | !Capacity ratio and COP ratio at | 5 | C oulet CHWT and | 30 | C inlet CWT
| 0.9125 | 0.8922 | [5 empty] | !Capacity ratio and COP ratio at | 5 | C oulet CHWT and | 32 | C inlet CWT
| 0.8915 | 0.8377 | [5 empty] | !Capacity ratio and COP ratio at | 5 | C oulet CHWT and | 34 | C inlet CWT
| 0.0011 | 0.095 | [5 empty] | !Capacity ratio and COP ratio at | 5 | C oulet CHWT and | 36 | C inlet CWT
| 0.0059 | 0.0186 | [5 empty] | !Capacity ratio and COP ratio at | 5 | C oulet CHWT and | 38 | C inlet CWT
| 0.0023 | 0.1901 | [5 empty] | !Capacity ratio and COP ratio at | 5 | C oulet CHWT and | 40 | C inlet CWT
| 0.9282 | 0.9885 | [5 empty] | !Capacity ratio and COP ratio at | 6 | C oulet CHWT and | 30 | C inlet CWT
| 0.8996 | 1.1498 | [5 empty] | !Capacity ratio and COP ratio at | 6 | C oulet CHWT and | 32 | C inlet CWT
| 0.9389 | 0.8426 | [5 empty] | !Capacity ratio and COP ratio at | 6 | C oulet CHWT and | 34 | C inlet CWT
| 0.0011 | 0.095 | [5 empty] | !Capacity ratio and COP ratio at | 6 | C oulet CHWT and | 36 | C inlet CWT
| 0.0023 | 0.1901 | [5 empty] | !Capacity ratio and COP ratio at | 6 | C oulet CHWT and | 38 | C inlet CWT
| 0.0023 | 0.1901 | [5 empty] | !Capacity ratio and COP ratio at | 6 | C oulet CHWT and | 40 | C inlet CWT
| 1 | 1.0009 | [5 empty] | !Capacity ratio and COP ratio at | 7 | C oulet CHWT and | 30 | C inlet CWT
| 0.979 | 0.9439 | [5 empty] | !Capacity ratio and COP ratio at | 7 | C oulet CHWT and | 32 | C inlet CWT
| 0.9581 | 0.8894 | [5 empty] | !Capacity ratio and COP ratio at | 7 | C oulet CHWT and | 34 | C inlet CWT
| 0.0011 | 0.1901 | [5 empty] | !Capacity ratio and COP ratio at | 7 | C oulet CHWT and | 36 | C inlet CWT
| 0.0606 | 0.102 | [5 empty] | !Capacity ratio and COP ratio at | 7 | C oulet CHWT and | 38 | C inlet CWT
| 0.0273 | 0.1681 | [5 empty] | !Capacity ratio and COP ratio at | 7 | C oulet CHWT and | 40 | C inlet CWT
| 0.0011 | 0.1901 | [5 empty] | !Capacity ratio and COP ratio at | 8 | C oulet CHWT and | 30 | C inlet CWT
| 0.0011 | 0.1901 | [5 empty] | !Capacity ratio and COP ratio at | 8 | C oulet CHWT and | 32 | C inlet CWT
| 0.0011 | 0.1901 | [5 empty] | !Capacity ratio and COP ratio at | 8 | C oulet CHWT and | 34 | C inlet CWT
| 0.0011 | 0.1901 | [5 empty] | !Capacity ratio and COP ratio at | 8 | C oulet CHWT and | 36 | C inlet CWT
| 0.0011 | 0.1901 | [5 empty] | !Capacity ratio and COP ratio at | 8 | C oulet CHWT and | 38 | C inlet CWT
| 0.0011 | 0.1901 | [5 empty] | !Capacity ratio and COP ratio at | 8 | C oulet CHWT and | 40 | C inlet CWT
| 1.0702 | 1.0535 | [5 empty] | !Capacity ratio and COP ratio at | 9 | C oulet CHWT and | 30 | C inlet CWT
| 1.0485 | 0.9953 | [5 empty] | !Capacity ratio and COP ratio at | 9 | C oulet CHWT and | 32 | C inlet CWT
| 1.0267 | 0.9394 | [5 empty] | !Capacity ratio and COP ratio at | 9 | C oulet CHWT and | 34 | C inlet CWT
| 0.0606 | 1.9391 | [5 empty] | !Capacity ratio and COP ratio at | 9 | C oulet CHWT and | 36 | C inlet CWT
| 0.0071 | 0.2281 | [5 empty] | !Capacity ratio and COP ratio at | 9 | C oulet CHWT and | 38 | C inlet CWT
| 0.0737 | 1.9645 | [5 empty] | !Capacity ratio and COP ratio at | 9 | C oulet CHWT and | 40 | C inlet CWT

## PLR
0 | 0.25 | 0.5 | 0.75 | 1 | ! | Part | Load | Ratio
0 | ! | Fraction | of | Full | Load | Power | at | PLR= | 0
0.2497 | ! | Fraction | of | Full | Load | Power | at | PLR= | 0.25
0.4956 | ! | Fraction | of | Full | Load | Power | at | PLR= | 0.5
0.6902 | ! | Fraction | of | Full | Load | Power | at | PLR= | 0.75
1 | ! | Fraction | of | Full | Load | Power | at | PLR= | 1
0 | 0.25 | 0.5 | 0.75 | 1 | ! | Part | Load | Ratio
0 | ! | Fraction | of | Full | Load | Power | at | PLR= | 0
0.2497 | ! | Fraction | of | Full | Load | Power | at | PLR= | 0.25
0.4956 | ! | Fraction | of | Full | Load | Power | at | PLR= | 0.5
0.6902 | ! | Fraction | of | Full | Load | Power | at | PLR= | 0.75
1 | ! | Fraction | of | Full | Load | Power | at | PLR= | 1